## Sheet1
Requirement |  | Resource Registration Glossary | [10 empty] | Data Validation Rules
Groups that use data element | Purpose of data element | RARF Tab | Wind | Conventional Generation (Gen) | Combined Cycle (CC) | Load Resources | Notes | Field Name | Definition / Detailed Description | Screening Study (SS) (R, C, O, A) | Full Interconnect Study (FIS) (R, C, O, A) | Full Registration (R, C, O, A) | RARF DATA FIELD | Business Rules/Basic UI validations | Field/ Tab Type | Data type | Validation Type | Source | Destination Application | Required for Screening Study (SS) | Required for Full Interconnect Study (FIS) | Required for Planning
|  | Private Network - Unit | X | X | X |  | List | Unit Name | Unit Code as provided on the Unit Info tab. | R | R | R | Unit Name | 1. This field is not null. Data type: Character. | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS | Y | Y
|  | Private Network - Unit | X | X | X |  | Automatic | Site Code | Site Code as provided on the General and Site Information tab. |  |  | A | SITE_CODE | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | [5 empty] | N | N
|  | Private Network - Unit | X | X | X |  | Automatic | Resource Name (Unit Code/Mnemonic) | Resource name as provided on the General and Site Information tab. |  |  | A | Resource Name (Unit Code/Mnemonic) | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS | Y | Y
|  | Private Network - Unit | X | X | X |  | MW | Average Amount of Self-Serve private Load | Amount of the total site generation MW output used for self serve and not available for the grid. If multiple generators are registered, proportion the total site load equally against each generator | C | C | C | Average Amount Of Self-serve Private Load | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 | EMS | Y | Y
|  | Private Network - Unit | X | X | X |  | MVAr | Average Amount of Self-Serve private reactive Load | Amount of the total site generation MVAr output used for self serve and not available for the grid. If multiple generators are registered, proportion the total site load against each generator | C | C | C | Average Amount Of Self-serve Private Reactive Load | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 |  | Y | Y
|  | Private Network - Unit | X | X | X |  | MW | Expected Typical Private Network Net Interchange | MW Net Interchange with ERCOT grid (typical Net=Gen-Load). If multiple generators are registered, proportion the total site load against each generator | C | C | C | Expected Typical Private Network Net Interchange | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 | EMS | Y | Y
|  | Private Network - Unit | X | X | X |  | MVAr | Expected Typical Private Network Net Reactive Interchange | MVAr Net Interchange with ERCOT grid (typical Net=Gen-Load). If multiple generators are registered, proportion the total site load against each generator | C | C | C | Expected Typical Private Network Net Reactive Interchange | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 |  | Y | Y
|  | Private Network - Unit | X | X | X |  | MW | Private Network Gross Unit Capability | MW Gross Generation Capability for the generator | C | C | C | Private Network Gross Unit Capability | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 | EMS | Y | Y
|  | Private Network - Unit | X | X | X |  | MVAr | Private Network Gross Unit Reactive Capability | MVAr Gross Generation Capability for the generator | C | C | C | Private Network Gross Unit Reactive Capability | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 |  | Y | Y
|  | Private Network - Unit | X | X | X |  | Y/N | If Unit trips, does Load trip? | This is necessary to determine how much Load will appear on the ERCOT grid if the unit trips. |  |  | C | If Unit trips, Does Load trip? | Select from Y or N. | C | Dropdown List | B,DVB | RARF Glossary Version 4.0/RARF Guide Version 4.0 |  | N | N
|  | Private Network - Unit | X | X | X |  | % | If yes, approximate percentage of Load that will trip? | If unit trips what percentage of Load associated with this unit is tripped? Enter % (ex. 70% is entered as 70.0) |  |  | C | If yes, Approximate Percentage of Load That Will Trip? | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 |  | N | N
|  | Reactive Capability | X | X | X |  | List | Unit Name | Unit Code as provided on the Unit Info tab. | R | R | R | Unit Name | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS | Y | Y
|  | Reactive Capability | X | X | X |  | Automatic | Resource Name (Unit Code/Mnemonic) | Concatenated mnemonic of Resource Site Code and Unit name (e.g. CBY_CBYG1). |  |  | A | Resource Name (Unit Code/Mnemonic) | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS | Y | Y
|  | Reactive Capability | X | X | X |  | List | Reactive Capability Provided is Gross value? | Select Gross | R | R | R | Reactive Capability Data Provided Below Is Gross Values? | Select from the list: GROSS |  | Dropdown List |  |  |  | Y | Y
|  | Reactive Capability | X | X | X |  | List | Reactive Capability Data Provided is from NDCRC Test Data | Indicate (Y/N) if the reactive capability data is from test data |  |  | R | Reactive Capability Data Provided Below Is From NDCRC Test Data? | Select from the list: Y or N |  | Dropdown List |  |  |  | N | N
|  | Reactive Capability | X | X | X |  | Date | Reactive Test Date | Include the Reactive Test Date, if the Reactive Capability Data Provided is from NDCRC test data |  |  | C | If Reactive Capability Data Provided Below Is From NDCRC Test Data Then Enter The Date On Which The Test Was Performed. | This field is Conditional. Format should be: MM/DD/YYYY | O | Date |  |  |  | N | N
|  | Reactive Capability | X | X | X |  | MW | MW1 | For non-IRR generators, the gross MW value associated with the units' lowest "Seasonal Net Minimum Sustainable Rating" as registered on the RARF, (Net to Gross conversion). For IRRs, record the Gross MW value representing 10% of registered nameplate capacity. |  | R | R | Mw1 | 1. MW1 >=0 .1 2. MW1<MW2. 3. X(1) <= WMN(Unit Minimal output) where X(1) represents MW1( Generate a Warning Only when Business Rule#2 fails) | R | Numeric | B,DVB | Lin Xu/ WeiHui | EMS,NMMS | N | Y
|  | Reactive Capability | X | X | X |  | MVAr | Lagging MVAr limit associated with MW1 output | The Lagging Reactive Power capability associated with the MW1 curve point, in MVAR. |  | R | R | Lagging MVAR limit associated with Mw1 output | 1. Lagging MVAR limit associated with MW1 output >=0. 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R | Numeric | B,DVB | Lin Xu/ WeiHui | EMS,NMMS | N | Y
|  | Reactive Capability | X | X | X |  | MVAr | Leading MVAr limit associated with MW1 output | The Leading Reactive Power capability associated with the MW1 curve point, in MVAR, input as negative number |  | R | R | Leading MVAR limit associated with Mw1 output | 1. Leading MVAR limit associated with MW1 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | R | Numeric | B,DVB | Lin Xu/ WeiHui | EMS,NMMS | N | Y
|  | Reactive Capability | X | X | X |  | MW | MW2 | Select MW 2 breakpoint which provides the best straight line fit between MW points 1 and 4. |  | R | R | Mw2 | 1. MW2>0 2. MW2<MW3 | R | Numeric | B,DVB | Lin Xu/ WeiHui | EMS,NMMS | N | Y
|  | Reactive Capability | X | X | X |  | MVAr | Lagging MVAr limit associated with MW2 output | The Lagging Reactive Power capability associated with the MW2 curve point, in MVAR. |  | R | R | Lagging MVAR limit associated with Mw2 output | 1.Lagging MVAR limit associated with MW2 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R | Numeric | B,DVB | Lin Xu/ WeiHui | EMS,NMMS | N | Y
|  | Reactive Capability | X | X | X |  | MVAr | Leading MVAr limit associated with MW2 output | The Leading Reactive Power capability associated with the MW2 curve point, in MVAR,input as negative number |  | R | R | Leading MVAR limit associated with Mw2 output | 1. Leading MVAR limit associated with MW2 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | R | Numeric | B,DVB | Lin Xu/ WeiHui | EMS,NMMS | N | Y
|  | Reactive Capability | X | X | X |  | MW | MW3 | Select MW 3 breakpoint which provides the best straight line fit between MW points 1 and 4. |  | R | R | Mw3 | 1. MW3 >0 2. MW3<MW4 | R | Numeric | B,DVB | Lin Xu/ WeiHui | EMS,NMMS | N | Y
|  | Reactive Capability | X | X | X |  | MVAr | Lagging MVAr limit associated with MW3 output | The Lagging Reactive Power capability associated with the MW3 curve point, in MVAR. |  | R | R | Lagging MVAR limit associated with Mw3 output | 1. Lagging MVAR limit associated with MW3 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R | Numeric | B,DVB | Lin Xu/ WeiHui | EMS,NMMS | N | Y
|  | Reactive Capability | X | X | X |  | MVAr | Leading MVAr limit associated with MW3 output | The Leading Reactive Power capability associated with the MW3 curve point, in MVAR. |  | R | R | Leading MVAR limit associated with Mw3 output | 1.Leading MVAR limit associated with MW3 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | R | Numeric | B,DVB | Lin Xu/ WeiHui | EMS,NMMS | N | Y
|  | Reactive Capability | X | X | X |  | MW | MW4 | The gross MW value which is associated with the highest "Seasonal Net Maximum Sustainable Rating" as registered on the RARF, (Net to gross conversion) |  | R | R | Mw4 | 1. MW4 >0 2. MW4<MW5 3. X(n) > = WMX (Unit Max output) where n is the last MW value in the curve. If the curve has 4 points, X(n) is X(4) [ Generate a Warning Only When Business Rule#2 Fails] | R | Numeric | B,DVB | Lin Xu/ WeiHui | EMS,NMMS | N | Y
|  | Reactive Capability | X | X | X |  | MVAr | Lagging MVAr limit associated with MW4 output | The Lagging Reactive Power capability associated with the MW4 curve point, in MVAR. |  | R | R | Lagging MVAR limit associated with Mw4 output | 1. Lagging MVAR limit associated with MW4 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R | Numeric | B,DVB | Lin Xu | EMS,MMS,NMMS | N | Y
|  | Reactive Capability | X | X | X |  | MVAr | Leading MVAr limit associated with MW4 output | The Leading Reactive Power capability associated with the MW4 curve point, in MVAR, input as negative number. |  | R | R | Leading MVAR limit associated with Mw4 output | 1.Leading MVAR limit associated with MW4 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | R | Numeric | B,DVB | Lin Xu | EMS,MMS,NMMS | N | Y
|  | Reactive Capability |  | X | X |  | MW | MW5 - Unity Power Factor | The MW output at Unity power factor (zero MVAr) |  | R | R | Mw5 - Unity Power Factor | 1. MW5 >0 2. MW5 >MW4 | R | Numeric | B,DVB | Lin Xu | MMS,NMMS | N | Y
|  | Reactive Capability |  | X | X |  | PSI | If hydrogen cooled, indicate hydrogen pressure (psi) associated with your Reactive Curve submitted for ERCOT studies | From manufacturer Reactive Capability Curve or data sheet. |  |  | C | If Hydrogen Cooled, Indicate Hydrogen Pressure (PSI) Associated With Your Reactive Curve Submitted For ERCOT Studies | Data type is Numeric | O | Numeric | B | Angela Moy\RARF Guide Version 4.0/RARF Glossary Version 4.0 |  | N | N
|  | Reactive Capability | X | X | X |  | MVAr | Maximum Leading Operating Capability (MVAr) | Enter the maximum lagging MVArs that can be produced. Input as negative number | R | R | R | Maximum Lagging Operating Capability | 1.Net Maximum Lagging Operating Capability >=0 2. Lagging MVAR must always be greater than the Leading MVAR | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,MMS | Y | Y
|  | Reactive Capability | X | X | X |  | MVAr | Maximum Lagging Operating Capability (MVAr) | Enter the maximum leading MVArs that can be produced. Input as positive number | R | R | R | Maximum Leading Operating Capability | 1.Net Maximum Leading Operating Capability <=0 | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,MMS | Y | Y
|  | Reactive Capability | X | X | X |  | Y/N | Manufacturer's Capability Curve submitted? | Has the most recent curve been submitted to ERCOT? If not, please attach. |  | R | R | Manufacturer's Capability Curve submitted? | Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 |  | N | Y
|  | Planning |  | X | X |  | List | Unit Name | Unit Code as provided on the Unit Info tab. |  | R | R | Resource Name (Unit Code/Mnemonic) | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS | N | Y
|  | Planning | X | X | X |  | Automatic | Resource Name (Unit Code/Mnemonic) | Concatenated mnemonic of Resource Site Code and Unit name (e.g. CBY_CBYG1). |  |  | A | What Is The Mva Base That The Following Data Is Based On? | 1) This field is required 2) Value must be Float 3) Generate a Warning if MVABASE > 2500 4)[ If MVABASE value is within +/- 25% range of Unit Name Plate Rating] OR [MVABASE value = 100, then it is OK.If MVABASE value is outside the +/- 25% range of Unit Name Plate Rating, then Generate a Warning that the MVABSE is outside the typical +/- 25% variation of unit name plate rating | R | Float | B | Planning Team |  | N | Y
|  | Planning |  | X | X |  | MVA | What is the MVA base that the following data is based on? | The MVA Base for stated impedances. |  | R | R | What Is The Kv Base That The Following Data Is Based On? | 1) This field is required 2) Value must be >0 and <1000 3) Generate a Warning if KVBASE > 40 4) If KVBASE value is within +/- 25% range of Unit KV value in the unit-information tab then it is OK.If If KVBASE value is outside the typical +/- 25% variation of Unit KV value in the unit-information tab then Generate a Warning that the KVBASE is outside the typical +/- 25% variation of Unit KV value | R | Float | B,DVB | Planning Team |  | N | Y
|  | Planning |  | X | X |  | KV | What is the kV base that the following data is based on? | The KV Base for stated impedances. |  | R | R | Direct Axis Subtransient Reactance, X"di (unsaturated) | 1) This field is required and Data type is float 2) Value must be between 0.0 and 1.0 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) 4) Generate a Warning if X"di (unsaturated) < X"dv (saturated) | R | Float | B | Planning Team |  | N | Y
|  | Planning |  | X | X |  | p.u. | Direct Axis Subtransient reactance, X"di (unsaturated) | Enter the direct axis subtransient reactance (unsaturated) for the fault. |  | R | R | Direct Axis Transient Reactance, X'di (unsaturated) | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) 4) Generate a Warning if X’di (unsaturated) < X’dv (saturated) | R | Float | B | Planning Team |  | N | Y
|  | Planning |  | X | X |  | p.u. | Direct Axis Transient reactance, X'di (unsaturated) | Enter the direct axis transient reactance (unsaturated) for the first 2-3 cycles of the fault. |  | R | R | Positive Sequence Z (unsaturated) | 1) This field is required and Data type is float 2) Value must be between 0 and 1 |  |  |  | Planning Team |  | N | Y
|  | Planning |  | X | X |  | R in p.u. | Positive Sequence Z (unsaturated) | Enter the positive sequence resistance (unsaturated) for system models. |  | R | R | Positive Sequence Z (unsaturated) | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) |  |  |  | Planning Team |  | N | Y
|  | Planning |  | X | X |  | X in p.u. | Positive Sequence Z (unsaturated) | Enter the positive sequence reactance (unsaturated) for system models. |  | R | R | Negative Sequence Z (unsaturated) | 1) This field is required and Data type is float 2) Value must be between 0 and 1 |  |  |  | Planning Team |  | N | Y
|  | Planning |  | X | X |  | R in p.u. | Negative Sequence Z (unsaturated) | Enter the negative sequence resistance (unsaturated) for system models. |  | R | R | Negative Sequence Z (unsaturated) | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] |  |  |  | Planning Team |  | N | Y
|  | Planning |  | X | X |  | X in p.u. | Negative Sequence Z (unsaturated) | Enter the negative sequence reactance (unsaturated) for system models. |  | R | R | Does Zero Sequence Z exist? | Drop down list select Y/N | R | Dropdown List |  | Planning Team |  | N | Y
|  | Planning |  | X | X |  | Y/N | Does Zero Sequence Z exist? | Select whether the generator has Zero Sequence Z data. If no, then the zero sequence data fields will not be required. |  | R | R | Zero Sequence Z (unsaturated) | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning ONLY when value is > 1.0 P.U |  |  |  | Planning Team |  | N | Y
|  | Planning |  | X | X |  | R in p.u. | Zero Sequence Z (unsaturated) | Enter the zero sequence resistance (unsaturated) for system models. |  | R | R | Zero Sequence Z (unsaturated) | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] |  |  |  | Planning Team |  | N | Y
|  | Planning |  | X | X |  | X in p.u. | Zero Sequence Z (unsaturated) | Enter the zero sequence reactance (unsaturated) for system models. |  | R | R | Direct Axis Subtransient Reactance, X"dv (saturated) | 1) This field is required and Data type is float 2) Value must be between -1 and 1 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value.(* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team |  | N | Y
|  | Planning |  | X | X |  | p.u. | Direct Axis Subtransient reactance, X"di (saturated) | Enter the direct axis subtransient reactance (saturated) for the fault. |  | R | R | Direct Axis Transient Reactance, X'dv (saturated) | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team |  | N | Y
|  | Planning |  | X | X |  | p.u. | Direct Axis Transient reactance, X"di (saturated) | Enter the direct axis transient reactance (saturated) for the first 2-3 cycles of the fault. |  | R | R | Positive Sequence Z (saturated) | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | R | Float | B | Planning Team | NMMS | N | Y
|  | Planning |  | X | X |  | R in p.u. | Positive Sequence Z (saturated) | Enter the positive sequence resistance (saturated) for system models. |  | R | R | Positive Sequence Z (saturated) | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | R | Float | B | Planning Team | NMMS | N | Y
|  | Planning |  | X | X |  | X in p.u. | Positive Sequence Z (saturated) | Enter the positive sequence reactance (saturated) for system models. |  | R | R | Negative Sequence Z (saturated) | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | R | Float | B | Planning Team |  | N | Y
|  | Planning |  | X | X |  | R in p.u. | Negative Sequence Z (saturated) | Enter the negative sequence resistance (saturated) for system models. |  | R | R | Negative Sequence Z (saturated) | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team |  | N | Y
|  | Planning |  | X | X |  | X in p.u. | Negative Sequence Z (saturated) | Enter the negative sequence reactance (saturated) for system models. |  | R | R | Zero Sequence Z (saturated) | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning ONLY when value is > 1.0 P.U | R | Float | B | Planning Team | NMMS | N | Y
|  | Planning |  | X | X |  | R in p.u. | Zero Sequence Z (saturated) | Enter the zero sequence resistance (saturated) for system models. |  | R | R | Zero Sequence Z (saturated) | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team | NMMS | N | Y
|  | Planning |  | X | X |  | X in p.u. | Zero Sequence Z (saturated) | Enter the zero sequence reactance (saturated) for system models. |  | R | R | Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 Value must be greater than or equal to 0.0 and less than or equal to 99999.0 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Model Adminstration |  | N | Y
|  | Planning |  | X | X |  | p.u. | Zero Sequence Grounding Resistance For An Impedance Grounded Generator in p.u. (100 MVA Base) | Zero Sequence Grounding Resistance value of the Generator Grounding Inpedance is required. The value must be specified on a 100 MVA base. |  | R | R | Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 Value must be greater than or equal to 0.0 and less than or equal to 99999.0 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Model Adminstration |  | N | Y
|  | Planning |  | X | X |  | p.u. | Zero Sequence Grounding Reactance For An Impedance Grounded Generator in p.u. (100 MVA Base) | Zero Sequence Grounding Reactance value of the Generator Grounding Inpedance is required. The value must be specified on a 100 MVA base. |  | R | R | Average Amount of Auxiliary Real Power | 1) This field is required 2) Data type is float 3) Value must be < Parameters - GEN - High Reasonability Limit 4) Warn if value > (High Reasonability Limit) * .20 5) Error if value > (High Reasonability Limit) * .50 | R | Float | B | Planning Team |  | Y | Y
|  | Planning | X | X | X |  | MW | Average Amount of Auxiliary Real Power | Enter average MW for auxiliary Load | R | R | R | Average Amount of Auxiliary Reactive Power | 1) This field is conditionally required (see below) 2) Data type is Float 3) Value must be <= Reactive Capability - GEN - Maximum Lagging Operating Capability (MVAR) 4) Warn if value > ( Maximum Lagging Operating Capability) * .20 5) Error if value > ( Maximum Lagging Operating Capability) * .50 Either Auxiliary Reactive Power or Power Factor is required | C | Float | B | Planning Team |  | Y | Y
|  | Planning | X | X | X |  | MVAr | Average Amount of Auxiliary Reactive Power | Enter average MVAr for auxiliary Load | C | C | C | Auxiliary Load Power Factor | Between .6 and 1.0 conditionally required (see below) Either Auxiliary Reactive Power or Power Factor is required | C |  |  | Planning Team |  | Y | Y
|  | Planning | X | X | X |  |  | Auxiliary Load Power Factor | Enter power factor for auxiliary Load | C | C | C | Large Motor, Percent Of Total Mw Load | 1)This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at >= 2400V / 4160V are large motors | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS | N | N
|  | Planning | X | X | X |  | % | Large Motor, percent of total MW Load | Enter % of total MW Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  | C | Small Motor, Percent Of Total Mw Load | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at < 2400V / 4160V are small motors | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS | N | N
|  | Planning | X | X | X |  | % | Small Motor, percent of total MW Load | Enter % of total MW Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  | C | Resistive (heating) Load, Percent Of Total Mw Load | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS | N | N
|  | Planning | X | X | X |  | % | Resistive (Heating) Load, percent of total MW Load | Enter % of total MW Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  | C | Discharge Lighting, Percent Of Total Mw Load | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS | N | N
|  | Planning | X | X | X |  | % | Discharge Lighting, percent of total MW Load | Enter % of total MW Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  | C | Other, Percent Of Total Mw Load | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS | N | N
|  | Planning | X | X | X |  | % | Other, percent of total MW Load | Enter % of total MW Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  | C | Large Motor, Percent Of Total Mvar Load | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% 4) Motors connected at >= 2400V / 4160V are large motors | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS | N | N
|  | Planning | X | X | X |  | % | Large Motor, percent of total MVAr Load | Enter % of total MVAr Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  | C | Small Motor, Percent Of Total Mvar Load | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at < 2400V / 4160V are small motors | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS | N | N
|  | Planning | X | X | X |  | % | Small Motor, percent of total MVAr Load | Enter % of total MVAr Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  | C | Discharge Lighting, Percent Of Total Mvar Load | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS | N | N
|  | Planning | X | X | X |  | % | Discharge Lighting, percent of total MVAr Load | Enter % of total MVAr Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  | C | Other, Percent Of Total Mvar Load | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS | N | N
|  | Planning | X | X | X |  | % | Other, percent of total MVAr Load | Enter % of total MVAr Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  | C