## Slide 1: Voltage Reduction Task Force Update
September 25, 2014
Presentation to ERCOT TAC

## Slide 2: VOLTAGE REDUCTION OVERVIEW
  VR is one technique used to reduce end-use loads during peak conditions
  In ERCOT, VR is initiated voluntarily as a final back-stop prior to initiating firm load shed (ERCOT EEA2 Level Event)
ERCOT Nodal Protocols - Section 6: Adjustment Period and Real-Time Operations - 6.5.9.4.2 page 77
  “Instruct TSPs and DSPs or their agents to reduce Customers’ Load by using distribution voltage reduction measures, if deemed beneficial by the TSP, DSP, or their agents”
  VR relies on Transformer (XFMR) Load Tap Changers (LTCs) / Regulators
Installed on load serving substation XFMRs
Regulates voltage by raising and lowering tap position
Many legacy control circuits “trick” LTC into lowering bus voltage
    Customers’ lights and air conditioners stay on

## Slide 3: VOLTAGE REDUCTION OVERVIEW PUCT PRESENT VOLTAGE REQUIREMENT
PUCT Substantive Rule 25.51 references ANSI C84.1 voltage requirements
Range B necessarily results from the practical design and operating conditions on supply and/or user systems, which are part of practical operations. However, such conditions should be limited in extent, duration and frequency. Corrective measures shall be undertaken within a reasonable time to bring back voltages within Range A limits, in cases of Range B values occurrence.
110 Volts
Where Utilities typically operate
Where utilities operate during VR events
Notes: 3

## Slide 4: ERCOT VOLTAGE REDUCTION TASK FORCE OVERVIEW
The effectiveness and use of VR is on the rise;
More effectively harvesting the benefits of VR is improved due to:
      Improvements in load tap-changer (LTC) control systems
      Ability to inexpensively monitor voltage along the distribution circuit
      Ability to flatten the voltage along the distribution feeder

## Slide 5: ERCOT VOLTAGE REDUCTION TASK FORCE OVERVIEW
  Voltage Reduction Task Force (VRTF)
    Created in December 2012 to test/evaluate VR
    Scope of work includes:
      Develop testing methods to validate the effectiveness of voltage reduction in multiple areas and share testing result
      Analyze the findings of the test and comparing them to industry experience;
      Provide control system and operational options
      Estimate the potential seasonal MW reduction that ERCOT could recognize based on the different operational options;
      Preparing a report of its findings to ERCOT - ROS
  Four companies participated in the testing (Summer and Winter testing)

## Slide 6: ERCOT VOLTAGE REDUCTION QUANTIFYING VOLTAGE REDUCTION BENEFIT

## Slide 7: VOLTAGE REDUCTION TEST EXAMPLE SUMMER TESTING
Total % = 3% for a 5% voltage reduction. CVR factor >0.6

## Slide 8: VOLTAGE REDUCTION TEST EXAMPLE WINTER TESTING
Total % = 3.05% for a 5% voltage reduction. CVR factor >0.6

## Slide 9: ERCOT VOLTAGE REDUCTION TASK FORCE
  Findings
A 1% to 2% average demand reduction was observed during the test periods
Tests indicated that for every 1% drop in substation bus voltage an average of 0.6-1.0% drop in demand was observed. Results were similar to what has been observed in areas outside of ERCOT
Advancements in substation regulation controls and the installation of Advanced Metering Systems have the potential to improve voltage reduction programs
The availability of a deployed control system enables the remote implementation of voltage reduction schemes on a large scale within 5 to 15 minutes
Notes: For the designated areas, independently chosen by each utility, included in voltage reduction testing, a 1% to 2% average demand reduction was observed during the test periods.
Tests indicated that for every 1% drop in substation bus voltage an average of 0.6-1.0% drop in demand was observed.
Results were similar to what has been observed in areas outside of ERCOT (e.g. New York ISO, New England ISO, Midwest ISO, PJM RTO, and Independent Electricity System Operator “Ontario”).
Advancements in substation regulation controls and the installation of Advanced Metering Systems have the potential to improve voltage reduction programs.
The availability of a deployed control system enables the remote implementation of voltage reduction schemes on a large scale within 5 to 15 minutes.
The efficiency of voltage reduction is dependent upon circuit topography, load characteristics and system design.
No adverse customer impact was reported as a result of the voltage reduction testing (circuits deemed to have adverse customer impacts were excluded from testing).

## Slide 10: ERCOT VOLTAGE REDUCTION TASK FORCE
Findings
The efficiency of voltage reduction is dependent upon circuit topography, load characteristics and system design
No adverse customer impact was reported (some circuits deemed to have adverse customer impacts were excluded from testing)
Typical voltage reductions are limited to 5%;
Longer-term varying levels of VR benefit can be obtained depending on the system investment made

## Slide 11: Questions?