## Slide 1
Future Ancillary Services Team
Update
September 25, 2014 TAC meeting

## Slide 2: Options for Determining and Providing PFRS and FFRS Requirements
OPTIONS | DA | MA | YA
Option 2 (Based on projected DA system condition) | √ | Advisory | Advisory
Option 3 (Based on median system condition for last 2 years) | ∆ | √ | 
Option 4 (Based on median system condition for last 2 years) | ∆ | ∆ | √
Option 5(Based on median system condition for last 2 years) | ∆ |  | √
Option 6 (Based on monthly worst condition) | ∆ | √ | 
DA: Day-Ahead, MA: Month-Ahead, YA: Year Ahead
√: Determine the needs for the entire period
∆: Determine the “incremental” needs based on the system condition

## Slide 3: Preliminary FFR and PFR Study Results
 | Case1 | Case2 | Case3 | Case4 | Case5 | Case6 | Case7 | Case8 | Case9 | Case10 | Case11 | Case12
FFR/PFR | 2.2:1 | 2.0:1 | 1.5:1 | 1.4:1 | 1.3:1 | 1.25:1 | 1.13 :1 | 1.08:1 | 1:1 | 1.0:1 | 1:1 | 1:1
Net load Level(GW) | 15-20 | 15-20 | 20-25 | 25-30 | 30-35 | 35-40 | 40-45 | 45-50 | 50-55 | 55-60 | 60-65 | 60-65
Inertia (GW∙s) | 239 | 271 | 304 | 354 | 403 | 459 | 511 | 556 | 593 | 631 | 664 | 700
PFR needed (no FFR) | 5200 | 4700 | 3750 | 3370 | 3100 | 3040 | 2640 | 2640 | 2240 | 2280 | 2140 | 2140
 | Case1 | Case2 | Case3 | Case4 | Case5 | Case6 | Case7 | Case8 | Case9 | Case10 | Case11 | Case12
FFR/PFR | 2.2:1 | 2.0:1 | 1.5:1 | 1.4:1 | 1.3:1 | 1.25:1 | 1.13 :1 | 1.08:1 | 1:1 | 1:1 | 1:1 | 1:1
PFR Min | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240
FFR needed with PFR Min | 1800 | 1696 | 1641 | 1511 | 1431 | 1440 | 1239 | 1296 | 1000 | 1040 | 900 | 900
Combined Total | 3040 | 2936 | 2881 | 2751 | 2671 | 2680 | 2479 | 2536 | 2240 | 2280 | 2140 | 2140

## Slide 4: An Example of Case Study
Minimum amount of FFR and PFR is determined by preventing frequency from dropping below 59.4Hz for loss of 2 largest units (2750MW)

## Slide 5: Determination of FFRS to PFRS Equivalency Ratio
Criteria : Frequency nadir shall be equal to or above 59.4 Hz for loss of two largest units. (0.1 Hz margin for the first stage of UFLS at 59.3 Hz)
  Assuming no FFRS, what was the minimum PFRS needed to meet the above criteria; for Case1 the answer was 5200 MW of PFRS
  Then we keep the minimum PFRS constant at 1240 MW and re-run the study adding incremental MW of FFRS until the reliability criteria is met.
  For Case1, the reliability criteria above was met at 1800 MW of FFRS
  Which means the combined PFRS and FFRS for case1 is 3040 MW
  So by getting 1800 MW of FFRS we need not buy 3960 MW (5200 MW -1240 MW) of PFRS, therefore 1 MW of FFRS was equivalent to which is equal to 2.2 MW of PFRS

## Slide 6: Proposed ERCOT Option (Option #7)
  The ERCOT option simplifies the procurement process and reduces uncertainty.
  Annually, ERCOT will post the 90th percentile of PFR and the 50th percentile of PFR that would need to be procured for each 4 hour block of the next year.
  These two numbers represent a maximum and minimum amount of procurement, in other words, the two “bookends”.
  Note that we do not publish an amount of FFR needed but, rather, we publish the equivalency ratio between FFR and PFR.
  Knowing these two numbers, in combination with the minimum amount of PFR which will be the same in all hours, a market participant can develop a reasonable hedging strategy.
  ERCOT has set the bookends such that it would not expect to need to purchase more than the 90th percentile, nor less than the 50th percentile, in any 4 hour block.

## Slide 7
Chart: Equivalent Ratio (FFR/PFR) -Jan 2015 (50th Percentile)
| H01 | H02 | H03 | H04 | H05 | H06 | H07 | H08 | H09 | H10 | H11 | H12 | H13 | H14 | H15 | H16 | H17 | H18 | H19 | H20 | H21 | H22 | H23 | H24
Equivalent Ratio (FFR/PFR) -Jan 2015 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.4 | 1.4
Equivalent Ratio by Hour – Examples

## Slide 8
Chart: Equivalent Ratio (FFR/PFR) -April 2015 (50th Percentile)
| H01 | H02 | H03 | H04 | H05 | H06 | H07 | H08 | H09 | H10 | H11 | H12 | H13 | H14 | H15 | H16 | H17 | H18 | H19 | H20 | H21 | H22 | H23 | H24
Equivalent Ratio (FFR/PFR) -April 2015 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.4 | 1.4 | 1.4 | 1.4 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.5 | 1.5
Equivalent Ratio by Hour

## Slide 9
Chart: Equivalent Ratio (FFR/PFR) -Aug 2015 (50th Percentile)
| H01 | H02 | H03 | H04 | H05 | H06 | H07 | H08 | H09 | H10 | H11 | H12 | H13 | H14 | H15 | H16 | H17 | H18 | H19 | H20 | H21 | H22 | H23 | H24
Equivalent Ratio (FFR/PFR) -Aug 2015 | 1.13 | 1.13 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.13 | 1.13
Equivalent Ratio by Hour

## Slide 10
Chart: Equivalent Ratio (FFR/PFR) -Oct 2015 (50th Percentile)
| H01 | H02 | H03 | H04 | H05 | H06 | H07 | H08 | H09 | H10 | H11 | H12 | H13 | H14 | H15 | H16 | H17 | H18 | H19 | H20 | H21 | H22 | H23 | H24
Equivalent Ratio (FFR/PFR) -Aug 2015 | 1.4 | 1.4 | 1.5 | 1.5 | 1.5 | 1.5 | 1.4 | 1.4 | 1.4 | 1.4 | 1.3 | 1.3 | 1.3 | 1.3 | 1.25 | 1.25 | 1.25 | 1.25 | 1.3 | 1.3 | 1.3 | 1.3 | 1.4 | 1.4
Equivalent Ratio by Hour

## Slide 11
Description of Pricing Proposals

## Slide 12: Introduction
There is consensus that the proposed AS procurement constraints are appropriate
All three proposals consider the exact same constraints and hence:
  The MW awards under all proposals are exactly the same and
  All three proposals allow for substitutability and thereby promote market liquidity
The only difference in the proposals are:
  Prices (MCPCs) for the different AS
  Replacement costs, if a need arises
The following slides describe the pricing and replacement costs associated with:
  the FAST proposal,
  Alternate Proposal #1,
  Alternate Proposal #2

## Slide 13: FAST Proposal
Stays with the current approach of pricing equivalent AS MW awards the same for equivalent AS types
For example, FRRS-Up, FRRS-Down, FFR1, FFR2, CR2, SR2 awards are valued the same as the corresponding equivalent Reg-Up, Reg-Down, PFRS, CR1, SR1 awards respectively
In the case of FFR, the ratio (R) determines the equivalence of R MW of PFR to 1 MW of FFR
If the Reg-Up, Reg-Down, PFR, CR1, SR1 MCPCs reflect opportunity costs, then the corresponding equivalent FRRS-Up, FRRS-Down, FFR1, FFR2, CR2, SR2 MCPCs will also reflect opportunity costs

## Slide 14: FAST Proposal
Replacement
If a need arises to replace FRRS-Up, FRRS-Down, FFR1, FFR2, CR2 or SR2 MW responsibility with an equivalent Reg-Up, Reg-Down, PFR, CR1 or SR1 MW responsibility, the cost to replace will be the same, i.e. is consistent, as replacing 1 MW of PFR with 1 MW of PFR, or 1 MW of CR1 with 1 MW of CR1, etc.
There is an exception to this consistency when the MCPC for FFR1 or FFR2 is capped at VOLL. The probability of this occurring is much lower than the probability of this inconsistency occurring in Alternate Proposal 1

## Slide 15: Alternate Proposal 1
Same as FAST’s Proposal except in the calculation of MCPC for FFR1 and FFR2
    The MCPCs for FRRS-Up, FRRS-Down, CR2, and SR2 are the same as the FAST Proposal
FFR1 MCPC Price Formation Process:
  Execute FAST Proposal MCPC formula for FFR1,
  Subtract from the FAST MCPC formula for FFR1:
    Shadow price of the constraint that limits FFR1 quantities to be procured and
    Shadow price of the constraint that limits the total FFR (FFR1+FFR2) quantities to be procured,
  If this computed result is less than MCPC for PFR, then, set the MCPC for FFR1 to be equal to the MCPC for PFR
FFR2 MCPC Price Formation Process:
  Execute FAST Proposal MCPC formula for FFR2,
  Subtract from the FAST Proposal MCPC formula for FFR2:
    Shadow price of the constraint that limits the total FFR (FFR1+FFR2) quantities to be procured,
  If this computed result is less than MCPC for PFR, then, set the MCPC for FFR2 to be equal to the MCPC for PFR

## Slide 16: Alternate Proposal 1
Replacement
Replacing costs for FRRS-Up, FRRS-Down, CR2 or SR2 MW responsibility are the same as the FAST proposal
Difference with FAST proposal can arise in the replacement cost for FFR1 and FFR2 MW responsibility with an equivalent PFR MW responsibility
  If a need arises to replace FFR1 or FFR2 MW responsibility with PFR, the cost of equivalent PFR MW responsibility would be inconsistent if:
    the Ratio (R) is greater than 1 and,
    the shadow price that limits the FFR1 or total FFR quantities to be procured is non-zero and if the FFR offers submitted do not include an estimate of this replacement cost
  The probability of this occurring is higher in this proposal than the FAST proposal

## Slide 17: Alternate Proposal 2
Moves away from the current approach of pricing equivalent AS MW awards the same for equivalent AS types
MCPC Price Formation Process:
  Execute FAST Proposal MCPC formula for FRRS-Up, FRRS-Down, FFR1, FFR2, CR2, SR2
  Subtract from this the shadow price of the constraint that limits quantities to be procured of each service (it includes any opportunity costs), and then…
  STOP – Computed MCPCs for FRRS-Up, FRRS-Down, FFR1, FFR2, CR2, SR2 are final
  The end result is that even though substitutability is maintained, the resulting MCPCs for FRRS-Up, FRRS-Down, FFR1, FFR2 CR2, SR2 are as if they had been cleared on their own offer stacks

## Slide 18: Alternate Proposal 2
If a need arises to replace FRRS-Up, FRRS-Down, FFR1, FFR2, CR2 or SR2 MW responsibility with an equivalent Reg-Up, Reg-Down, PFR, CR1 or SR1 MW responsibility, the cost to replace would be inconsistent with the cost to replace 1 MW of PFR with 1 MW of PFR, or 1 MW of CR1 with 1 MW of CR1, etc. if:
      The shadow price that limits the quantities to be procured is non-zero, and
      The AS offers submitted do not include an estimate of this replacement cost

## Slide 19: MCPC Formulas for Each Proposal
AS | FAST | Alternate #1 | Alternate #2
FRRS-Up | RegUp MCPC | RegUp MCPC | RegUp MCPC – SP of FRRS-Upmax constraint1
FRRS-Dn | RegDn MCPC | RegDn MCPC | RegDn MCPC – SP of FRRS-Downmax constraint*
FFR1 | Min( Ratio * PFR MCPC, VOLL) | Max( PFR MCPC, Ratio * PFR MCPC – SP of FFRmax constraint1 – SP of FFR1max constraint1) | Ratio * PFR MCPC – SP of FFRmax constraint1 – SP of FFR1max constraint1
FFR2 | Min( Ratio * PFR MCPC, VOLL) | Max( PFR MCPC, Ratio * PFR MCPC – SP of FFRmax constraint1 ) | Ratio * PFR MCPC – SP of FFRmax constraint1
CR2 | CR1 MCPC | CR1 MCPC | CR1 MCPC – SP of CR1min constraint1
SR2 | SR1 MCPC | SR1 MCPC | SR1 MCPC – SP of SR1min constraint1
1 Opportunity costs, if present, will be included in the shadow prices
SP = Shadow Price of Constraint

## Slide 20: Pricing Results (Scenario 1)
AS TYPE | FAST | Alternate #1 | Alternate #2
PFR | 15 | 15 | 15
FFR1 | 30 | 15 | 3
FFR2 | 30 | 15 | 6
CR1 | 14 | 14 | 14
CR2 | 14 | 14 | 4

## Slide 21: Pricing Results (Scenario 2)
AS TYPE | FAST | Alternate #1 | Alternate #2
PFR | 20 | 20 | 20
FFR1 | 40 | 20 | 3
FFR2 | 40 | 20 | 6
CR1 | 19 | 19 | 19
CR2 | 19 | 19 | 4

## Slide 22: Pricing Results (Scenario 3a)
AS TYPE | FAST | Alternate #1 | Alternate #2
PFR | 2,020 | 2,020 | 2,020
FFR1 | 2,020 | 2,020 | 3
FFR2 | 2,020 | 2,020 | 6
CR1 | 2,019 | 2,019 | 2,019
CR2 | 2,019 | 2,019 | 4

## Slide 23: Pricing Results (Scenario 3b)
AS TYPE | FAST | Alternate #1 | Alternate #2
PFR | 2,020 | 2,020 | 2,020
FFR1 | 4,040 | 2,020 | 3
FFR2 | 4,040 | 2,020 | 6
CR1 | 2,019 | 2,019 | 2,019
CR2 | 2,019 | 2,019 | 4

## Slide 24: Pricing Results (Scenario 4a)
AS TYPE | FAST | Alternate #1 | Alternate #2
PFR | 8,920 | 8,920 | 8,920
FFR1 | 8,920 | 8,920 | 3
FFR2 | 8,920 | 8,920 | 6
CR1 | 8,919 | 8,919 | 8,919
CR2 | 8,919 | 8,919 | 4

## Slide 25: Pricing Results (Scenario 4b)
AS TYPE | FAST | Alternate #1 | Alternate #2
PFR | 8,920 | 8,920 | 8,920
FFR1 | 9,000 | 8,920 | 3
FFR2 | 9,000 | 8,920 | 6
CR1 | 8,919 | 8,919 | 8,919
CR2 | 8,919 | 8,919 | 4

## Slide 26: Pricing Results (Scenario 5)
AS TYPE | FAST | Alternate #1 | Alternate #2
PFR | 15 | 15 | 15
FFR1 | 30 | 15 | 3
FFR2 | 30 | 15 | 6
CR1 | 13 | 13 | 13
CR2 | 13 | 13 | 4
RegUp | 15 | 15 | 15
FRRSUp | 15 | 15 | 15
RegDn | 8 | 8 | 8
FRRSDn | 8 | 8 | 8
SR1 | 10 | 10 | 10
SR2 | 10 | 10 | 2