## Slide 1: ERS Summer Performance Update
Mark Patterson, ERCOT
Technical Advisory Committee
September 25, 2014

## Slide 2: Weather Sensitive ERS Performance
Overview
21.6 MWs obligated in both BH2 (1 – 4 p.m.) and BH3 (4 – 8 pm) for June through September SCT
3 Resources (residential aggregations)
Test Requirements (minimum 1 and maximum of 2 per month)
5 tests performed during current SCT
  1 in June
  2 in July
  1 in August
  1 to-date in September (data not yet available for analysis)
September 25, 2014
<number>

## Slide 3
VDI Start: 15:24:15 Average MW Reduction: 21.2 MW
VDI Stop: 17:02:00 Average PM Dry Bulb: 92.8⁰
Weather Sensitive ERS Performance
September 25, 2014
<number>

## Slide 4
VDI Start: 16:42:39 Average MW Reduction: 16.2 MW
VDI Stop: 18:17:56 Average PM Dry Bulb: 94.0⁰
Weather Sensitive ERS Performance
September 25, 2014
<number>

## Slide 5
VDI Start: 16:03:26 Average MW Reduction: 16.2 MW
VDI Stop: 18:31:06 Average PM Dry Bulb: 96.3⁰
Weather Sensitive ERS Performance
September 25, 2014
<number>

## Slide 6
VDI Start: 15:26:43 Average MW Reduction: 21.8 MW
VDI Stop: 17:48:22 Average PM Dry Bulb: 99.3⁰
Weather Sensitive ERS Performance
September 25, 2014
<number>

## Slide 7
Weather Sensitive ERS Performance
September 25, 2014
<number>

## Slide 8: Non-Weather Sensitive ERS Performance
Non-Weather Sensitive ERS Resources are subject to deployment test every 365 days
Successful deployment during deployment event will meet the annual testing requirement
Most obligated non-weather sensitive ERS Resources (both 10 and 30-Minute) successfully deployed during the January 6th event but new resources or reconstituted resources will have a testing requirement throughout the year
With no deployment event during the summer 2014 (to-date) there is no fleet wide event performance available to report
September 25, 2014
<number>

## Slide 9: January 6, 2014 ERS Deployment Timeline
Non-Weather Sensitive ERS Performance
September 25, 2014
<number>

## Slide 10: ERS-30 Performance (Jan, 6, 2014 Event)
Graph is based on 15-minute interval data.
Performance is based on a prorated obligation for the 1st partial interval
only (11.57 minutes) therefore prorated obligation for 1st partial interval was 86.11 MWs
Fleet response = 94.831 MWs
September 25, 2014
<number>

## Slide 11: ERS-10 Performance (Jan 6, 2014 Event)
Graph is based on 15-minute interval data.
Performance is based on a prorated obligation for the 1st partial interval and one full interval.
1 Resource had prescheduled unavailability from HE0900 - 1600 on the day of the event (14.6 MWs)
Fleet wide obligation less scheduled unavailability = 495.72 MWs
Fleet Response = 594.86 MWs
September 25, 2014
<number>