August 2014 ERCOT Monthly Operations Report

Reliability and Operations Subcommittee Meeting

October 2, 2014

Table of Contents

1.	Report Highlights	1

2.	Frequency Control	2

2.1.	Frequency Events	2

2.2.	Responsive Reserve Events	3

2.3.	Load Resource Events	3

3.	Reliability Unit Commitment	3

4.	Wind Generation as a Percent of Load	4

5.	Congestion Analysis	4

5.1.	Notable Constraints for August	4

5.2.	Generic Transmission Constraint Congestion	5

5.3.	Congestion Costs for Calendar Year 2014	6

6.	System Events	7

6.1.	ERCOT Peak Load	7

6.2.	Load Shed Events	7

6.3.	Stability Events	7

6.4.	Notable PMU Events	7

6.5.	TRE/DOE Reportable Events	7

6.6.	New/Updated Constraint Management Plans	8

6.7.	New/Modified/Removed SPS	8

6.8.	New Procedures/Forms/Operating Bulletins	8

7.	Emergency Conditions	8

7.1.	OCNs	8

7.2.	Advisories	8

7.3.	Watches	8

7.4.	Emergency Notices	8

8.	Application Performance	8

8.1.	TSAT/VSAT Performance Issues	9

8.2.	Communication Issues	9

9.	Net-Forecast Bias Applied to NSRS Procurement for September 2014	9

10.	Appendix A: Real-Time Constraints	10

# Report Highlights

August was the warmest month of the summer in the ERCOT region. Despite the high temperatures, the ERCOT system performed well. Operations continued to note a low level of frequency events and RRS deployments. The amount of SCED congestion remained consistent with what was seen in July, and was due mainly to high system loads. There was a single reportable system event this month. ERCOT applications performed well in August, with the exception of one missed VSAT run.

Highlights of this report:

- The unofficial ERCOT peak for August was 66,427 MW.

- There were three frequency events in August. The ERCOT system transitioned well in each case.

- There were two instances where Responsive Reserves were deployed. Both of them were the result of frequency events.

- There were three RUC Commitments in August, all for local congestion.

- The level of SCED congestion held steady in August and was mainly due to high system loads resulting from the hot summer weather.

- There was one system even event this month that was reported as the result of a loss of generation in excess of 1000 MW. System reliability was not impacted.

- ERCOT Applications performed well through the month. However, VSAT experienced an issue following an EMS site failover.

# Frequency Control

## Frequency Events

The ERCOT Interconnection experienced three frequency events in August, all of which resulted from Resource trips. The average event duration was approximately 108 seconds.

When analyzing frequency events, ERCOT evaluates PMU data according to industry standards. Events with an oscillating frequency of less than 1 Hz are considered to be inter-area, while higher frequencies indicate local events. Industry standards specify that damping ratio for inter-area oscillations should be 3.0% or greater. All events listed below indicate the ERCOT system met these standards and transitioned well after each disturbance. Further details on the Resource trip events can be seen in the Performance Disturbance Compliance Working Group report.

A summary of the frequency events is provided below:

| Date and Time | Max/Min Frequency (Hz) | Duration of Event (seconds) | PMU Data |  | Comments |
| --- | --- | --- | --- | --- | --- |
|  |  |  | Oscillation Mode | Damping Ratio |  |
| 8/4/2014 14:23 | 59.798 | 166 | No significant oscillation modes captured |  | Unit trip with approximately 839 MW |
| 8/4/2014 14:27 | 59.82 | 136 | No significant oscillation modes captured |  | Unit trip with approximately 781 MW |
| 8/30/2014 22:17 | 59.871 | 23 | No significant oscillation modes captured |  | Unit trip with approximately 583 MW |

(Note: the duration of the frequency events is defined to be the time at which the frequency was outside the range of 60±0.1 Hz)

## Responsive Reserve Events

There were two events where Responsive Reserve MWs were released to SCED in August.  The events highlighted in blue were related to frequency events reported in section 2.1 above.

| Date and Time Released to SCED | Date and Time Recalled | Duration of Event | Maximum MWs Released | Comments |
| --- | --- | --- | --- | --- |
| 8/4/14 14:23:30 | 8/4/14 14:32:54 | 0:09:24 | 911.47 |  |
| 8/30/14 22:17:46 | 8/30/14 22:20:06 | 0:02:20 | 318.21 |  |

## Load Resource Events

There were no load resource deployment events in August.

# Reliability Unit Commitment

ERCOT reports on Reliability Unit Commitments (RUC) on a monthly basis. Commitments are reported grouped by operating day and weather zone. The total number of hours committed is the sum of the hours for all the units in the specified region. Additional information on RUC commitments can be found on the MIS secure site at Grid  Generation  Reliability Unit Commitment.

There were no DRUC commitments in August.

| HRUC Commitments |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Resource Location | # of Resources | Operating Day | Total # of Hours Committed | Total MWhs | Reason for commitment | Unit(s) |
| N. Central | 1 | 8/23/2014 | 8 | 944 | Local Congestion |  |
| Southern | 2 | 8/23/2014 | 10 | 304 | Local Congestion |  |

# Wind Generation as a Percent of Load

# Congestion Analysis

The number of congestion events experienced by the ERCOT system remained steady in August as temperatures remained high throughout the region. There was no activity on any of the Generic Transmission Constraints (GTCs) in August.

## Notable Constraints for August

Nodal protocol section 3.20 specifies that ERCOT shall identify transmission constraints that are active or binding three or more times within a calendar month. As part of this process, ERCOT reports congestion that meets this criterion to ROS. In addition ERCOT also highlights notable constraints that have an estimated congestion rent exceeding $1,000,000 for a calendar month. These constraints are detailed in the table below. Rows highlighted in blue indicate the congestion was affected by one or more outages. For a list of all constraints activated in SCED for the month of August, please see Appendix A at the end of this report.

| Contingency | Overload | # of Days Constraint Active | Estimated Congestion Rent | Transmission Project |
| --- | --- | --- | --- | --- |
| Salt Flat Road - Skywest 138 kV | Midland East - Buffalo 138 kV | 6 | $8,656,987 | 14TPIT0052 |
| Hutto Switch Axfmr 1 (3) 345/138 kV | Gilleland - Pflugerville 138 kV | 3 | $5,072,055 | 16TPIT0062 |
| Skywest - Spraberry Switch 138 kV | Midland East - Buffalo 138 kV | 4 | $4,001,618 | 14TPIT0052 |
| DCKT Flewellen - Obrien and Mason Road 138 kV | Hockley - Betka 138 kV | 4 | $3,103,561 | TPIT Project 3682A, 3682B |
| Roanoke Switch Axfmr 1 (3) 345/138 kV | Euless - Grapevine Highway 360 138 kV (1065_L) | 1 | $2,367,095 | 11TPIT0012 |
| DCKT Singleton - Tomball 345 kV | Singleton - Zenith 345 kV (SNGZEN99) | 8 | $2,318,819 | TPIT Project 3937 |
| DCKT Gibbons Creek - Singleton 345 kV | Jewett - Singleton 345 kV (260_A) | 22 | $2,244,342 | TPIT Project 3937 |
| DCKT Lon Hill - North Edinburg 345 kv and Orange Grove Switching Station 138 kV | Lon Hill - Smith 69 kV | 13 | $1,690,306 | 16TPIT0026 |
| Los Fresnos - Loma Alta Substation 138 kV | La Palma - Villa Cavazos 138 kV | 1 | $1,337,710 | 16TPIT0029, 16TPIT0030 |
| Lake Wichita Switch - Bowman Switch 138 kV | Certain Teed - Wichita Falls Cogen Switch 138 kV | 1 | $1,207,918 |  |
| Fairview - Bulldog 138 kV | Midland East - Buffalo 138 kV | 5 | $1,075,270 | 14TPIT0052 |
| Orange Grove Switching Station - Lon Hill 138 kV | Lon Hill - Smith 69 kV | 5 | $875,501 | 16TPIT0026 |
| Laquinta - Lobo 138 kV | Bruni 138_69_1 138/69 kV | 22 | $870,694 | 13TPIT0158 |
| Lobo - San Miguel 345_138 kV Switchyards 345 kV | Laquinta - Lobo 138 kV | 12 | $667,089 | 2013-R90, 2013-R100 |
| Salem LCRA AT4 345/138kV | Fayetteville 26AT2 345/138kV | 12 | $608,063 |  |
| Koch Up River - Gila 138 kV | Gila - Hiway 9 138 kV (GILA_HIWAY_2) | 19 | $529,438 |  |
| DCKT Ferguson - Granite Mountain and Wirtz - Starcke - Paleface 138 kV | Wirtz - Flat Rock Lcra 138 kV | 6 | $225,862 |  |
| Forney - Forney Switch 345 kV (Line 199) | Forney - Forney Switch 345 kV (Line 198) | 4 | $163,332 | 12TPIT0080 |
| DCKT Twin Oak Switch - Gibbons Creek and Btu_Jack_Creek 345 kV | Jewett - Singleton 345 kV (260_A) | 5 | $109,806 | TPIT Project 3937 |
| DCKT Jewett - Singleton 345 kV | Twin Oak Switch - Btu_Jack_Creek 345 kV | 8 | $72,845 | TPIT Project 3937 |
| DCKT Austrop - Sandow Switch 345 kV | Hutto Switch - Round Rock Northeast 138 kV (1661_B) | 4 | $64,385 | 15TPIT0062, 08TPIT0033 |
| Lobo 2_345_138 345/138 kV | Pearsall Switching Station - Paloduro Sub 138 kV | 4 | $51,435 | TPIT Project 3821 |
| Yellow Jacket - Fort Mason 138 kV | Fort Mason - Mason 69 kV | 3 | $40,981 | TPIT Project 3673 |
| Ennis Switch - Desoto Switch 138 kV | Ennis West Switch - Waxahachie 138 kV | 3 | $31,658 | 06TPIT0036 |
| Victoria - Coleto Creek 138 kV (COLETO_VICTOR1) | Victoria - Coleto Creek 138 kV (COLETO_VICTOR2) | 6 | $18,414 | 16TPIT0034 |
| DCKT Gibbons Creek - Singleton 345 kV | Jewett - Singleton 345 kV (240_A) | 3 | $2,635 | TPIT Project 3937 |

## Generic Transmission Constraint Congestion

There was no activity on any ERCOT GTCs in August.

## Congestion Costs for Calendar Year 2014

The following table represents the top twenty active constraints for the calendar year to date based on the estimated congestion rent attributed to the congestion. ERCOT updates this list on a monthly basis.

| Contingency | Binding Element | # of 5-min SCED Intervals | Estimated Congestion Rent | Transmission Project |
| --- | --- | --- | --- | --- |
| Lytton Springs LY_AT1 345/138 kV | Lytton Springs LY_AT1 345/138 kV | 1,997 | $55,956,002 |  |
| Skywest - Spraberry Switch 138 kV, Skywest - Salt Flat Road 138 kV, and Salt Mine - Barber Lake Switch 138 kV | Midland East - Pecan Grove 138 kV | 3,738 | $46,790,259 | 14TPIT0052 |
| Midland East Axfmr 1 (3) 345/138 kV, Moss Switch Axfmr 1 345/138 kV, and Midland East - Moss Switch - Odessa Ehv Switch 345 kV | Odessa North Sd3 138 kV | 5,310 | $23,944,433 | 2012-R3, 2012-R4 |
| Orange Grove Switching Station - Lon Hill 138 kV, DCKT Lon Hill - North Edinburg 345 kv and Orange Grove Switching Station 138 kV, and Lon Hill 345_138_2 (3) 345/138 kV | Lon Hill - Smith 69 kV | 7,663 | $13,480,141 | 16TPIT0026, 2012-R18 |
| Basecase | Valley Import | 495 | $11,577,259 |  |
| DCKT Jewett - Singleton 345 kV | Twin Oak Switch - Gibbons Creek 345 kV | 273 | $10,912,808 |  |
| DCKT Gabriel - Glasscock LCRA and Rivery 138 kV, Glasscock LCRA - Gabriel 138 kV, and DCKT Gabriel - Bell County - Hutto Switch 138 kV | Marshall Ford - Lago Vista 138 kV | 209 | $9,871,526 | 15TPIT0061 |
| DCKT Flewellen - Obrien and Maso Road 138 kV, DCKT Singleton - Zenith 345 kV | Hockley - Betka 138 kV | 462 | $9,500,744 | TPIT Project 3682A, 3682B |
| DCKT Paris Switch - Valley Ses and Valley South 345 kV | Paris Switch AXFMR1 (3) 345/138 kV | 1,442 | $9,291,357 | 14TPIT0093 |
| DCKT Wa Parish - Jeanetta 345 kV | Smithers - Bellaire 345 kV | 1,058 | $7,870,155 |  |
| Alice - Kingsville 138 kV, Kingsville - Lon Hill 138 kV, Nelson Sharpe - Lon Hill 345 kV | Lon Hill - Calallen Sub 69 kV | 912 | $7,699,219 | 12TPIT0181, 2012-R13 |
| Laquinta - Lobo 138 kV | Bruni 138_69_1 138/69 kV | 10,547 | $6,999,791 | 13TPIT0148 |
| DCKT Gibbons Creek - Singleton 345 kV and DCKT Twin Oak Switch - Gibbons Creek and Btu_Jack_Creek 345 kV | Jewett - Singleton 345 kV (260_A) | 6,910 | $6,766,444 | TPIT Project 3937 |
| Sun Switch - Morgan Creek Ses 138 kV and Bluff Creek Switch - Ennis Creek Switch 138 kV | Snyder - Sacroc 138 kV | 509 | $6,283,276 | 09TPIT0120 |
| Stadium Aep - Alice 69 kV, Pawnee Switching Station - Lon Hill 345 kV, and Alice - Kingsville 138 kV | Lon Hill - Robstown Tap 69 kV | 904 | $6,091,279 | 12TPIT0180 |
| DCKT Singleton - Tomball 345 kV | Singleton - Zenith 345 kV (SNGZEN99) | 4,142 | $5,741,600 | TPIT Project 3937 |
| Koch Up River - Gila 138 kV | Gila - Hiway 9 138 kV (GILA_HIWAY_2) | 20,546 | $5,578,500 |  |
| McNeil Lcra - Gilleland 138 kV, Hutto Switch Axfmr 1 (3) 345/138 kV, and DCKT Austrop - Sandow Switch 345 kV | Hutto Switch - Round Rock Northeast 138 kV (1661_B) | 207 | $4,844,211 | 16TPIT0062 |
| Falcon Seaboard - Midland East 345 kV and Moss Switch - Odessa Ehv Switch 345 kV | Odessa - Odessa North 138 kV | 346 | $4,650,914 | 14TPIT0054 |
| Coleto Creek - Pawnee Switching Station 345 kV, Pawnee Switching Station - Calaveras 345 kV | Coleto Creek - Kenedy Switch 138 kV | 405 | $4,490,198 | 16TPIT0034 |

# System Events

## ERCOT Peak Load

The unofficial ERCOT peak load for the month was 66,427 MW and occurred on August 25 during the hour ending 17:00.

## Load Shed Events

None

## Stability Events

None

## Notable PMU Events

ERCOT analyzes PMU data for any significant system disturbances that do not fall into the Frequency Events category reported in section 2.1. The results are summarized in this section once the analysis has been completed.

| Date and Time | PMU Data |  | Event Description |
| --- | --- | --- | --- |
|  | Oscillation Mode | Damping Ratio |  |
| 8/13/2014 10:45 | 0.647 Hz | 12.46% | System event was caused by a single unit trip with approximately 489 MW. Since system frequency did not decline below 59.9 Hz and no RRS was deployed, this event was not included in section 2 above. |

## TRE/DOE Reportable Events

ERCOT experienced one system event that was reported this month. On August 4, two units at a single plant tripped with a total generation loss of 1,620 MW. The time interval between first and second generator trips was more than one minute and system reliability was not impacted.

## New/Updated Constraint Management Plans

There were two new RAPs in August: Gabriel LCRA – Bell County Brazos/Round Rock Double Circuit 138 kV line and McNeil – Gilleland 138 kV Single Circuit line. Both RAPs were implemented on 8/6/2014.

## New/Modified/Removed SPS

Benbrook Switch SPS was retired on 8/6/2014.

## New Procedures/Forms/Operating Bulletins

| Date | Document | Description |
| --- | --- | --- |
| 8/1/2014 | Power Operations Bulletin 678 | DC Tie Desk V1 Rev29 |
| 8/1/2014 | Power Operations Bulletin 679 | Real Time Desk V1 Rev31 |
| 8/1/2014 | Power Operations Bulletin 680 | Resource Desk V1 Rev29 |
| 8/1/2014 | Power Operations Bulletin 681 | Shift Supervisor Desk V1 Rev28 |
| 8/1/2014 | Power Operations Bulletin 682 | Transmission and Security Desk V1 Rev33 |

# Emergency Conditions

## OCNs

| Date and Time | Description |
| --- | --- |
| 8/5/2014 01:05 | ERCOT issued an OCN for a projected reserve capacity shortage for hours ending 14:00 through 22:00. |
| 8/7/2014 17:09 | ERCOT issued an OCN for a projected reserve capacity shortage for hours ending 14:00 through 22:00. |
| 8/17/2014 18:30 | ERCOT issued an OCN for an EMMS Site Failover. |

## Advisories

| Date and Time | Description |
| --- | --- |
| 8/17/2014 18:59 | Advisory issued due to ERCOT's Voltage Security Assessment Tool is currently unavailable. |
| 8/18/2014 09:58 | ERCOT issued an Advisory for the deadline for DAM submissions for Operating Day 08/19/2014 being extended due to internal server connection issue that has been resolved. |

## Watches

None

## Emergency Notices

None

# Application Performance

ERCOT system applications performed well in August. There was one issue with the VSAT application.

## TSAT/VSAT Performance Issues

There was one issue in August related to the Voltage Security Assessment Tool.

| Date and Time | Description |
| --- | --- |
| 8/17/2014 18:59 | Advisory issued due to ERCOT's Voltage Security Assessment Tool is currently unavailable. |

## Communication Issues

None

# Net-Forecast Bias Applied to NSRS Procurement for September 2014

Each month, ERCOT calculates a net Forecast Bias pursuant to the ERCOT Ancillary Services Methodology for procurement of Non-Spinning Reserve Service (NSRS).  The table below indicates the amount of net Forecast Bias that was applied to the NSRS procurement for specified blocks of time for the month of September, 2014.

| Blocks | Negative Net Load Forecast Average Error - By Weather Zone for the 5 Largest Zones |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Coast | East | North Central | South Central | Southern |
| 1-2 | 0 | 0 | 0 | 0 | 0 |
| 3-6 | 0 | 0 | 0 | 0 | 0 |
| 7-10 | 0 | 0 | 0 | 0 | 0 |
| 11-14 | 0 | 0 | 0 | 0 | 0 |
| 15-18 | 0 | 0 | 0 | 0 | 0 |
| 19-22 | 0 | 0 | 0 | 0 | 0 |
| 23-24 | 0 | 0 | 0 | 0 | 0 |

# Appendix A: Real-Time Constraints

The following is a complete list of constraints activated in SCED for the month of August. Full contingency descriptions can be found in the Standard Contingencies List located on the MIS secure site at Grid  Generation  Reliability Unit Commitment.

| Contingency | Constrained Element | From Station | To Station | # of Days Constraint Active |
| --- | --- | --- | --- | --- |
| DGIBSNG5 | 260_A_1 | JEWET | SNG | 22 |
| SLAQLOB8 | BRUNI_69_1 | BRUNI | BRUNI | 22 |
| SKOCNU28 | GILA_HIWAY_2_1 | GILA | HIWAY_9 | 19 |
| DLONOR58 | LON_HI_SMITH1_1 | LON_HILL | SMITH | 13 |
| SLOBSAN5 | LAQUIN_LOBO1_1 | LAQUINTA | LOBO | 12 |
| XSAL258 | FAYETT_6AT2 | FAYETT | FAYETT | 12 |
| DJEWSNG5 | JK_TOKSW_1 | TOKSW | JK_CK | 8 |
| DTB_SNG5 | SNGZEN99_A | SNG | ZEN | 8 |
| DFERPAL8 | 38T365_1 | WIRTZ | FLATRO | 6 |
| SSALSK28 | 6146__A | MDLNE | BUFFALO | 6 |
| SVICCO28 | COLETO_VICTOR2_1 | COLETO | VICTORIA | 6 |
| DGIBJK_5 | 260_A_1 | JEWET | SNG | 5 |
| SFAIBUL8 | 6146__A | MDLNE | BUFFALO | 5 |
| SORNLON8 | LON_HI_SMITH1_1 | LON_HILL | SMITH | 5 |
| DAUSSND5 | 1661__B | HUTTO | RRNES | 4 |
| DFL_MAR8 | BETHK_66_A | HK | BET | 4 |
| SFRNFO25 | 198__A | FRNYPP | FORSW | 4 |
| SSKYSBY8 | 6146__A | MDLNE | BUFFALO | 4 |
| XLOB58 | PALDRO_PEARSAL_1 | PEARSALL | PALODURO | 4 |
| DGIBSNG5 | 240__A | JEWET | SNG | 3 |
| SFORYEL8 | FORTMA_MASN1_1 | FORTMA | MASN | 3 |
| SRDODES8 | 940__C | ENWSW | WXHCH | 3 |
| XHUT58 | 1666__B | GILLCR | PFLGV | 3 |
| DCHBJOR5 | BRNLAN86_A | LAN | BRN | 2 |
| DLYTTUN8 | GARFIELD_AT1 | GARFIELD | GARFIELD | 2 |
| SFLCMDL5 | 6510__A | GLNHV | CRM8T | 2 |
| SGIBSNG5 | SNGXGC99_1 | GIBCRK | SNG | 2 |
| SJNSWNT8 | OLSEN_NAT1 | OLSEN | OLSEN | 2 |
| SLOBSAN5 | PALDRO_PEARSAL_1 | PEARSALL | PALODURO | 2 |
| XSBY89 | 6620__A | STASW | MRCAP | 2 |
| XWL2V58 | 3130__B | INDST | CMPST | 2 |
| DAUSDUN8 | 1661__B | HUTTO | RRNES | 1 |
| DAUSDUN8 | GARFIELD_AT1 | GARFIELD | GARFIELD | 1 |
| DAUSSND5 | 1661__A | RRNES | RNDRK | 1 |
| DCALHOT8 | N4_X3_1 | CALAVERS | X3 | 1 |
| DELMMAR5 | 293T304_1 | CIBOLO | SCHERT | 1 |
| DELMSAN5 | POT_OAKS_1 | OAKS9 | POTEETS | 1 |
| DENTSCS5 | 1170__A | NCDSE | HNRSW | 1 |
| DEULLIG8 | 745__A | DFWAW | GRPVN | 1 |
| DHCKRNK5 | 1065__L | EULES | GRHWY | 1 |
| DLOCDA89 | 101T158_1 | ZORN | POOLRO | 1 |
| DLYTHIC8 | GARFIELD_AT1 | GARFIELD | GARFIELD | 1 |
| DNB_JOR5 | DPWLYD70_A | LYD | DPW | 1 |
| DVLYANA5 | 562__D | PAYSW | MEMWT | 1 |
| DWTRTRC5 | 1750__B | SGOVL | KLBTP | 1 |
| SAJORI25 | RAYMND_RAYMON1_1 | RAYMND2 | RAYMOND1 | 1 |
| SALAN_28 | AIRLIN_CABANI1_1 | AIRLINE | CABANISS | 1 |
| SALIKIN8 | FALFUR_69A1 | FALFUR | FALFUR | 1 |
| SARMRA38 | HARLNS_RAYMON1_1 | HARLNSW | RAYMOND1 | 1 |
| SBIGDIL8 | ASHERT_W_BATE1_1 | W_BATESV | ASHERTON | 1 |
| SBRAUVA8 | HAMILT_MAVERI1_1 | HAMILTON | MAVERICK | 1 |
| SCOLBRB8 | 6146__A | MDLNE | BUFFALO | 1 |
| SEILPCT8 | 6146__A | MDLNE | BUFFALO | 1 |
| SENSEN28 | 940__C | ENWSW | WXHCH | 1 |
| SHIWCIT8 | MORRIS_NUECES1_1 | NUECES_B | MORRIS | 1 |
| SL_FLA_8 | LA_PAL_VCAVAZ1_1 | LA_PALMA | VCAVAZOS | 1 |
| SLEABAN9 | UVALDE_69A1 | UVALDE | UVALDE | 1 |
| SLKWBOM8 | 6170__D | CNTED | WFCOG | 1 |
| SLOBSAN5 | BRUNI4_LAQUIN1_1 | BRUNI4 | LAQUINTA | 1 |
| SLOBSAN5 | FREER_SAN_DI1_1 | SAN_DIEG | FREER | 1 |
| SLOCMEN8 | 101T158_1 | ZORN | POOLRO | 1 |
| SMCNGIL8 | 1661__A | RRNES | RNDRK | 1 |
| SREDMCC8 | 102T375_1 | MCCALA | RNRD12 | 1 |
| SSCLWF28 | 6840__B | NVKSW | ANARN | 1 |
| SSCLWF28 | NVKSW_FMR1 | NVKSW | NVKSW | 1 |
| SSTABSP8 | SBYSW_FMR1 | SBYSW | SBYSW | 1 |
| SVCAMIL8 | RIOHND_ERIOHND_1 | RIOHONDO | MV_RIOHO | 1 |
| XLOB58 | DIL_COTU_1 | DILLEYSW | COTULAS | 1 |
| XLOB58 | DILLEY_JARDIN1_1 | DILLEYSW | JARDIN | 1 |
| XMOS258 | 6475__C | ODEHV | ODESA | 1 |
| XRN2K58 | 1065__L | EULES | GRHWY | 1 |
| XSTA89 | SBYSW_FMR1 | SBYSW | SBYSW | 1 |