| NOGRR Number | 139 | NOGRR Title | Under/Over-Frequency Relaying Requirements |
| --- | --- | --- | --- |
| Date Posted |  | September 30, 2014 |  |

| Requested Resolution | Normal |
| --- | --- |
| Nodal Operating Guide Section(s) Requiring Revision | 2.6, Requirements for Under-Frequency Relaying 2.6.2, Generators |
| Other Binding Documents Requiring Revision or Related Revision Requests | None. |
| Revision Description | This Nodal Operating Guide Revision Request (NOGRR) adds over-frequency relaying requirements and clarifies under-frequency and over-frequency relay set-points so that Generation Resources know what is expected. Over-frequency relay set points criteria was approved by NERC in March 2014 under Standard PRC-024, Generator Frequency and Voltage Protective Relay Settings. |
| Reason for Revision | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |

| Business Case |  |
| --- | --- |
| Qualitative Benefits | - This NOGRR aligns the ERCOT Operating Guides with a recently approved NERC requirement; all generators in the ERCOT region are impacted. |
| Quantitative Benefits |  |
| Impact to Market Segments |  |
| Credit Implications |  |
| Other |  |

| Sponsor |  |
| --- | --- |
| Name | Ajay Pappu / Isabel Flores |
| E-mail Address | vpappu@ercot.com / iflores@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-3168 / 512-248-6531 |
| Cell Number |  |
| Market Segment | Not applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Brian Manning |
| E-Mail Address | Brian.manning@ercot.com |
| Phone Number | 512-248-3937 |

Proposed Guide Language Revision

2.6	Requirements for Under-Frequency and Over-Frequency Relaying

2.6.2	Generators

(1)	Under-frequency relays  shall be set such that the automatic removal of individual Generation Resources from the ERCOT System meets the following requirements:

| Frequency Range | Delay to Trip |
| --- | --- |
| Above 59.4 Hz | No automatic tripping (Continuous operation) |
| Above 58.4 Hz up to And including 59.4 Hz | Not less than 9 minutes |
| Above 58.0 Hz up to And including 58.4 Hz | Not less than 30 seconds |
| Above 57.5 Hz up to And including 58.0 Hz | Not less than 2 seconds |
| 57.5 Hz or below | No time delay required |

(2)	Over-frequency relays shall be set such that the automatic removal of individual Generation Resources from the ERCOT System meets the following requirements:

| Frequency Range | Delay to Trip |
| --- | --- |
| Below 60.6 Hz down to and including 60 Hz | No automatic tripping (Continuous operation) |
| Below 61.6 Hz down to and including 60.6 Hz | Not less than 9 minutes |
| Below 61.8 Hz down to and including 61.6 Hz | Not less than 30 seconds |
| 61.8 Hz or above | No time delay required |

(3)	A Resource Entity that owns Generation Resources that do not currently comply with (1) and (2) above shall submit a schedule for compliance as requested by ERCOT.

(4)	The Resource Entity that owns Generation Resources that are unable to comply shall provide an explanation of the process used by the Generation Resource to manage under-frequency and over-frequency events.  The Generation Resource shall provide the details on the limitations of the unit to comply with the frequency set points if necessary.