## Slide 1
Constraint Management During EEA
NPRR642 & NOGRR135
ERCOT
Joint ROS/WMS Meeting
October 6 2014

## Slide 2: Background
NPRR480 removed language associated with “relaxing” transmission constraints during emergency operations
  Rationale was the language was inconsistent with Attachment 1-EOP-002-2.1
Binding constraints in SCED have limited some generation during the EEA events during the 2013/2014 winter
A mechanism is needed to allow generation capacity to be available to serve load during emergency operations in a manner that preserves transmission reliability

## Slide 3: Background
ERCOT reassessed the requirements of Attachment 1-EOP-002 Energy Emergency Alerts
  The Reliability Standard has provisions during EEA2 for the Reliability Coordinator (RC) to review its SOLs/IROLs with impacted Balancing Authorities (BA) and Transmission Providers
  Provisions also in place during EEA3 to revise SOLs/IROLs, subject to considerations
  There is not a provision that allows the RC to stop managing congestion on the grid during EEA

## Slide 4: NPRR642 Proposal
6.5.9.3.3 (7)
  During a Watch, ERCOT will investigate binding constraints and determine, during EEA2 or EEA3
    If a 15-minute rating can be used
    If recalling outages or other transmission switching/changes can be implemented
    The risk of a double-circuit failure
  Beginning during a Watch allows time for coordination with Transmission Operators in anticipation of an EEA2 or EEA3

## Slide 5: NPRR642 Proposal
6.5.9.4
  (3) Management of IROLs will not change
  (10) In EEA2 or EEA3, control to the 15-minute rating if available
  (11) Constrain to single-circuit contingencies if risk of double-circuit outage is low
Note that the changes in (10) and (11) only apply to constraints that limit generation output
This NPRR does not propose changes to the treatment of double-circuit contingencies under normal conditions
  only during EEA 2 or EEA 3 for capacity shortage to avoid load shed if transmission risk is low

## Slide 6: NPRR642 Implementation
6.5.9.3.3 (7)
  Procedure changes to review active constraints and identify
    those which have resources with high positive shift factors
    whether a 15-minute rating exists for the constrained element
    the restoration time for any planned transmission outages in the area that are contributing to the congestion
    time permitting, the risk of a double-circuit failure

## Slide 7: NPRR642 Implementation
Procedure Language
  Review all active constraints’ shift factors
  Time permitting, for DCKTs, call impacted TSP(s) and discuss risk of a DCKT outage
  For any constraint where there are one or more generators with a + 65% shift factor or greater
    review the constrained element to determine if a 15-minute rating exists
    review the restoration times for any associated outages

## Slide 8: NPRR642 Implementation
6.5.9.4
  Procedure changes to manage transition into/out of utilization of the 15-minute rating for post-contingency congestion management as well as double-circuit considerations during EEA2 and EEA3
  No changes needed for IROL management

## Slide 9: NPRR642 Implementation
Procedure Language
  When entering EEA2
    if DCKT risk is low, deactivate DCKT constraint, activate the SCKT constraint
    change constrained limit to 15-minute rating if available
    recall transmission outages if possible
  When exiting EEA2 into EEA1
    activate DCKT constraint, deactivate SCKT constraint
    change constrained limit to 2-hour rating
    evaluate re-implementation of transmission outages