## Slide 1: Ancillary Services Methodology Changes for 2015
October 6, 2014 ROS/WMS Joint Meeting
ERCOT Staff

## Slide 2: Schedule for discussion with Stakeholders
23-Sept | QMWG (Concept/Policy)
6-Oct | ROS/WMS (Concept/Policy)
9-Oct | Post AS Methodology document based on ROS/WMS input
23-Oct | TAC
08-Dec | BOD
Notes: 3.16 Standards for Determining Ancillary Service Quantities
The ERCOT Board shall review and approve ERCOT's methodology for determining the minimum Ancillary Service requirements, the monthly percentage of Load Resources, Controllable Load Resources and DC Ties allowed to provide RRS, and the maximum amount of Reg-Up and Reg-Down that can be provided by Resources providing FRRS-Up and FRRS-Down.
Last done by BOD Dec 2013.

## Slide 3: What is to be discussed?
Responsive Reserve Service (RRS)
  Overview of recent frequency response studies
  2 Options for changes to address needs illustrated by studies
  Other issues affecting RRS requirements
Regulation Service
  Removal of the RRS schedule release as an input to the Reg-Up procurement analysis
  Routine update of factors for installed wind capacity
Non-Spin Reserve Service (NSRS)
  Based on the option selected for RRS, we may need to change the requirement to transfer 500 MW of NSRS to RRS and lower maximum cap on NSRS
Seeking input on concepts/policy options; Will develop specific AS Methodology document based on that input

## Slide 4: 09-23-2014 QMWG Discussion
There was general consensus on proposed Option 2 as a preferred option.
Members suggested that ERCOT include RRS requirement quantity with and without any adjustment for 24% RRS threshold and post the numbers for 2015 prior to joint ROS-WMS meeting.
It was suggested that ERCOT ask DWG to perform studies/evaluation to see whether or not 50% limitation on Load Resources providing RRS needs to be revised.
It was suggested to not transfer 500 MW from NSRS to RRS
Suggestions were also made to remove load forecast bias from methodology to determine minimum NSRS quantity
  No consensus to change this current practice
There was some discussions on whether or not the use of 59.40 Hz criteria for determining the RRS requirement.
  No consensus to change this criteria from current practice

## Slide 5: What is driving the need for RRS changes for 2015?
Protocol section 3.16 Standards for Determining Ancillary Service Quantities
  ERCOT shall, at least annually, review the quantity and requirements for each Ancillary Service needed for reliability.
ERCOT has identified issues during periods of low inertia which need to be addressed
  ERCOT has historically studied reserve requirements to protect against the loss of two largest Resources without tripping UFLS (UFLS trips at 59.3 Hz);
  ERCOT identified additional areas of concern during the Future Ancillary Services Taskforce (FAST) process; and
  NERC-BAL-003 - will require ERCOT to plan for the loss of 2750 MW (based on two largest generators) without tripping UFLS. The standard will go into effect in 2016.

## Slide 6: Background on proposed RRS changes
ERCOT as a single BA Interconnection has historically been concerned with low frequency events and has procured RRS to protect against those events
  Original ERCOT requirement was the sum of the two largest units in ERCOT plus 200 MW (requirement was 1600 to 1800 MW)
  When first nuclear unit came on line in late 1980s it increased to 2300 MW
  Has not changed since 1988.
  Two separate studies were performed in 2014.
    In preparation for the NERC BAL-003-1 requirements, ERCOT performed studies to determine minimum RRS needed to protect the grid against simultaneous loss of two largest units (2750 MW).
    ERCOT performed several studies considering the need for frequency responsive reserves for the FAST

## Slide 7
2014 Dynamic Simulation
Examples of low Inertia impact to UFLS for loss of 2750 MW

## Slide 8: An Example of Case Study
Minimum amount of FFR and PFR is determined by preventing frequency from dropping below 59.4Hz for loss of 2 largest units (2750MW)

## Slide 9: FAST Study Case Selection
case1
case2
case3
case4
case5
case6
case7
case8
case9
case10
case11
case12
Inertia=2*Kinetic Energy=2*H*MVA
Notes: Upper portion of the box represents 75% lower is 25% line in the box is 50%
Line at the top and bottom is 3 standard deviations and outside those lines are outliers

## Slide 10: FAST Case results Load Resource (FFR) and PFR Requirement
 | Case1 | Case2 | Case3 | Case4 | Case5 | Case6 | Case7 | Case8 | Case9 | Case10 | Case11 | Case12
FFR/PFR | 2.2:1 | 2.0:1 | 1.5:1 | 1.4:1 | 1.3:1 | 1.25:1 | 1.13 :1 | 1.08:1 | 1.0:1 | 1.0:1 | 1.0:1 | 1.0:1
Netload Level(GW) | 15-20 | 15-20 | 20-25 | 25-30 | 30-35 | 35-40 | 40-45 | 45-50 | 50-55 | 55-60 | 60-65 | 60-65
Inertia (GW∙s) | 239 | 271 | 304 | 354 | 403 | 459 | 511 | 556 | 593 | 631 | 664 | 700
PFR Requirement (no FFR) | 5200 | 4700 | 3750 | 3370 | 3100 | 3040 | 2640 | 2640 | 2240 | 2280 | 2140 | 2140
 | Case1 | Case2 | Case3 | Case4 | Case5 | Case6 | Case7 | Case8 | Case9 | Case10 | Case11 | Case12
FFR/PFR | 2.2:1 | 2.0:1 | 1.5:1 | 1.4:1 | 1.3:1 | 1.25:1 | 1.13 :1 | 1.08:1 | 1.0:1 | 1.0:1 | 1.0:1 | 1.0:1
PFR Requirement | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240
FFR Requirement | 1800 | 1696 | 1641 | 1511 | 1431 | 1440 | 1239 | 1296 | 1000 | 1040 | 900 | 900
Combined Total | 3040 | 2936 | 2881 | 2751 | 2671 | 2680 | 2479 | 2536 | 2240 | 2280 | 2140 | 2140
Inertia=2*Kinetic Energy=2*H*MVA
“Equivalency Ratio” between RRS from LRs and Gen

## Slide 11: What do these studies mean?
All studies from 1988 to present indicate there will be UFLS during loss of two largest units in low inertia periods without sufficient reserves.
The amount of reserves that are needed to avoid UFLS changes depending on the amount of synchronous generation (inertia) that is committed
  The amount of RRS needed during low inertia periods is higher than the amount currently procured
During low inertia periods, RRS from LRs are more effective per MW than from generation
  “Equivalency Ratio” is 1:1 for higher inertia periods
ERCOT expects that there will be more periods of low net load, with correspondingly low system inertia during periods of 2015.
  This will increase the number of hours per year that the low inertia will present risks of UFLS.

## Slide 12
Current AS methodology methods
Limitations to our current approach, in light of new studies:
  ERCOT buys one RRS amount for all hours of the year.
    Currently 2800 MWs RRS.
  ERCOT values all RRS the same, whether from Load or Generation, even though our studies indicate that, at low load inertia levels, Load Resources are more effective
  Load is restricted to providing no more than 50% of RRS
  ERCOT does not know how much RRS is being provided by LRs until the DAM
  Some of the generation RRS may not be fully delivered until after UFLS due to the 24%
  NPRR 524 has been approved to allow non-frequency responsive generation to provide RRS (when ERCOT was buying 2800 MW of RRS and only required 2300 MWs)
Notes: Note the NPRR524 has not yet been implemented.

## Slide 13
What changes are needed?
If amount of RRS was updated as indicated by new studies, and the historic practice of procuring the same amount of RRS for the entire year, based on the most critical conditions, were followed:
  the current 2800MW RRS amount would increase to over 5,000 MW for all hours
However, the other aspects of the recent studies should also be considered:
  Recognizing the reduced need for RRS during high load periods is probably warranted; and
  Recognizing the higher effectiveness of Load Resources in some periods is probably warranted
The question is “how to do it appropriately?”
  Recognizing that ERCOT system changes are not feasible by 1/2015

## Slide 14
ERCOT recognizes there is a tradeoff for different options in addressing Ancillary Services quantity requirements.
  More certain options are:
    Simpler to hedge
    Simpler to plan
  More variable options are:
    More efficient
    May offer more flexibility
ERCOT offers two options that attempt to address this tradeoff, based on feedback from 9/15 TAC/FAST meeting
Certainty vs Efficiency

## Slide 15: Option 1 – Assumption of No LR Participation in RRS
Once annually, ERCOT will post amounts of RRS (six 4-hour blocks) for each month.
  These amounts will be based on expected diurnal load and wind patterns for the month and covering for 70% of historic system inertia conditions (see slide 8).
These annually published amounts are the values that will be procured in in the DAM for each hour of the year.
The posted RRS amounts will be based on a 1:1 equivalency ratio between LRs and generation providing RRS.

## Slide 16: Option 1 – Assumption of No LR Participation in RRS – Example Values
January- 2015 |  | 
HE | Total RRS MW | Equivalency Ratio (FYI – Not Used)
22-02 | 3370 | 1.40
03-06 | 3750 | 1.50
07-10 | 3370 | 1.40
11-14 | 3370 | 1.40
15-18 | 3370 | 1.40
19-22 | 3370 | 1.40
April- 2015 |  | 
HE | Total RRS MW | Equivalency Ratio (FYI – Not Used)
22-02 | 3750 | 1.50
03-06 | 4700 | 2.00
07-10 | 3370 | 1.40
11-14 | 3370 | 1.40
15-18 | 3370 | 1.40
19-22 | 3370 | 1.40
August- 2015 |  | 
HE | Total RRS MW | Equivalency Ratio (FYI – Not Used)
22-02 | 3040 | 1.25
03-06 | 3040 | 1.25
07-10 | 3040 | 1.25
11-14 | 2640 | 1.08
15-18 | 2496 | 1.00
19-22 | 2640 | 1.08
October- 2015 |  | 
HE | Total RRS MW | Equivalency Ratio (FYI – Not Used)
22-02 | 3750 | 1.50
03-06 | 3750 | 1.50
07-10 | 3370 | 1.40
11-14 | 3100 | 1.30
15-18 | 3100 | 1.30
19-22 | 3100 | 1.30

## Slide 17: Option 1 – Assumption of No LR Participation in RRS
Pros:
  Hedgeable
  Hourly values improve efficiency of procurement
  Little risk of under procurement
Cons:
  The assumption of no LRS amounts leads to (significant) over procurement in those hours where LRS is more effective than Generation

## Slide 18: Option 2 – Assume 50% LRs with Equivalency Ratio
Once annually, ERCOT will post amounts of RRS (six 4-hour blocks) for each month.
  These amounts will be based on expected diurnal load and wind patterns for the month and covering for 70% of historic system inertia conditions (see slide 8).
These annually published amounts are the values that will be procured in in the DAM for each hour of the year.
The posted RRS amounts will be based on an assumption that 50% of RRS requirement is met by LRs and the appropriate Equivalency Ratio for the expected conditions for that hour will be used.

## Slide 19: Option 2 – Assume 50% LRs with Equivalency Ratio – Example Values
August - 2015 |  |  |  |  | 
HE | Total RRS MW (Without 24% adjustment) | Total RRS MW (With 24% adjustment) | PFRS | LRs | Equivalency Ratio
22-02 | 2702 | 2906 | 1453 | 1453 | 1.25
03-06 | 2702 | 2906 | 1453 | 1453 | 1.25
07-10 | 2702 | 2906 | 1453 | 1453 | 1.25
11-14 | 2538 | 2788 | 1394 | 1394 | 1.08
15-18 | 2300 | 2496 | 1248 | 1248 | 1.00
19-22 | 2538 | 2788 | 1394 | 1394 | 1.08
October - 2015 |  |  |  |  | 
HE | Total RRS MW (Without 24% adjustment) | Total RRS MW (With 24% adjustment) | PFRS | LRs | Equivalency Ratio
22-02 | 3002 | 3204 | 1602 | 1602 | 1.50
03-06 | 3002 | 3204 | 1602 | 1602 | 1.50
07-10 | 2808 | 3006 | 1503 | 1503 | 1.40
11-14 | 2696 | 2894 | 1447 | 1447 | 1.30
15-18 | 2696 | 2894 | 1447 | 1447 | 1.30
19-22 | 2696 | 2894 | 1447 | 1447 | 1.30
April- 2015 |  |  |  |  | 
HE | Total RRS MW (Without 24% adjustment) | Total RRS MW (With 24% adjustment) | PFRS | LRs | Equivalency Ratio
22-02 | 3002 | 3204 | 1602 | 1602 | 1.50
03-06 | 3132 | 3310 | 1655 | 1655 | 2.00
07-10 | 2808 | 3006 | 1503 | 1503 | 1.40
11-14 | 2808 | 3006 | 1503 | 1503 | 1.40
15-18 | 2808 | 3006 | 1503 | 1503 | 1.40
19-22 | 2808 | 3006 | 1503 | 1503 | 1.40
January- 2015 |  |  |  |  | 
HE | Total RRS MW (Without 24% adjustment) | Total RRS MW (With 24% adjustment) | PFRS | LRs | Equivalency Ratio
22-02 | 2808 | 3006 | 1503 | 1503 | 1.40
03-06 | 3002 | 3204 | 1602 | 1602 | 1.50
07-10 | 2808 | 3006 | 1503 | 1503 | 1.40
11-14 | 2808 | 3006 | 1503 | 1503 | 1.40
15-18 | 2808 | 3006 | 1503 | 1503 | 1.40
19-22 | 2808 | 3006 | 1503 | 1503 | 1.40

## Slide 20: Option 2 – Assume 50% LRs with Equivalency Ratio
Pros:
  Hedgeable
  Hourly values improve efficiency of procurement
  Lower quantities to be procured take advantage of likely procurement and effectiveness of LRs
Cons:
  Risk of under procurement if less than 50% of RRS is supplied by LRs in hours with Equivalency Ratio greater than 1.0.

## Slide 21: Policy issues that could affect RRS quantities
50% limitation for Load Resources
  Examples assume 50% limit
  Change would require Protocol and Systems change
Limit on maximum capacity of a unit providing RRS of 24%
  Examples assume higher overall amounts of RRS need to be procured in order to provide sufficient frequency-responsive RRS
  Change the limit from 24% to 20% will provide lower RRS quantity to be procured
  Change would require Protocol but not Systems change
500 MW of NSRS requirement moved to RRS
  Example quantities do not include 500MW moved from NSRS
  This decision is to be determined for the 2015 AS Methodology
Percentile of Inertia to be used
  Example quantities based on covering 70% of historic on-line inertia at a given net load level
  This decision is to be determined for 2015 AS Methodology
Changes that would require NPRRs/System Changes would be done in time for 2016 AS Methodology

## Slide 22
Proposed AS Methodology changes summary
Regulation Service

## Slide 23: Why change the Regulation procurement methodology
Remove RRS schedule release as an input to the Reg-Up procurement analysis
  Carried over from Zonal, where RRS deployment was energy deployment
  In Nodal, RRS deployment is only release of schedule not an energy deployment
  RRS was very frequently used in Zonal to replace regulation-up
Update the factors used to adjust the Regulation Service quantities for additional installed wind generation since June 2013
  Added approximately 988 MW of Wind since last analyses
Notes: We can also explore the idea of removing exhaustion rate from the methodology

## Slide 24: Impact of RRS Deployment on Feb 2014 HE 0700

## Slide 25: Non Spin
If the decision on RRS is that we would NOT move 500 MW of NSRS requirement to RRS, then a change would be needed in the NSRS section of the AS Methodology
ERCOT also proposes to reduce the NSRS quantities by the amount of the 24% adjustment for each hour (generally, about 200MW).

## Slide 26
Discussion

## Slide 27: References
History of RRS background: http://www.ercot.com/content/meetings/board/keydocs/2007/0220/Item_04a_-_Recent_EECP_Events_&_Responsive_Reserve_Adequacy.pdf
2008 UFLS:
http://www.ercot.com/content/meetings/ros/keydocs/2002/1210/ROS12102002-11.doc
2014 NERC BAL-003-1 -Study :
http://www.ercot.com/content/meetings/other/keydocs/2014/0619-EEAWorkshop/EEA_Workshop_2_Presentation.ppt
NERC BAL-003:
http://www.nerc.com/FilingsOrders/us/NERC%20Filings%20to%20FERC%20DL/FR%20Annual%20Report%2012-27-13%20Final.pdf
2014 FAST -Study :
http://www.ercot.com/content/meetings/fast/keydocs/2014/0825/FAST-TAC%208-25-14%20Workshop.ppt