## Slide 1: PDCWG Report to ROS
Sydney Niemeyer Chair
NRG Energy
Don Blackburn Vice Chair
Luminant Energy
October 6, 2014

## Slide 2: PDCWG Meeting September 10
Reviewed frequency control performance. The PDCWG wants to review the frequency profile of days that do not include a Time Error Correction to see if TECs are impacting the profile. Graphs included in this report.
Reviewed Regulation Service Deployment Bias during June, July and August.
  Startup and Shutdown of Resources continue to consume Regulation Service.
  Intervals with Reg Up and Reg Down deployed continued improvement in summer 2014 over 2013 and 2012.
  Regulation Exhaustion rate improved for June 2014 but had a small increase for July and August 2014 over same month 2013. All three months of 2013 and 2014 were significantly better than same months in 2012.
  Suggested improvement:
    Continue to investigate the use of an Integral term.
    The use of shorter SCED intervals, especially during startup and shutdown periods would improve Regulation use.

## Slide 3: PDCWG Meeting continued
Reviewed the August 4th, 30th and September 3rd frequency events.
  Reviewed RRS provider performance.
  Reviewed non-RRS provider performance.

## Slide 4: Future Meeting Dates
November 11, 2014
December 2, 2014
  All meetings at the Met Center.

## Slide 5: ERCOT Frequency Control Report September 2014
Sydney Niemeyer NRG Energy
October 3, 2014

## Slide 6: Ercot frequency control
BAL-001 CPS 1 & 2 Performance, RMS 1 and Frequency Profile

## Slide 10
CPS1 12 Month Rolling Average = 162.50

## Slide 15
60.010 <= HZ < 60.015

## Slide 19: ERCOT Time error and time correction
Time Error History

## Slide 20: Notes
Time error values from NRG True Time device can be slightly different from ERCOT’s Time Error but the daily delta times should be accurate.

## Slide 21: Time Error Corrections
Five slow Time Error Corrections were executed in August.
Other than the days with the TECs, three days had positive time error.

## Slide 24
Time Correction History

## Slide 27: Ercot primary frequency response performance
BAL-003-1 Interconnection Frequency Response and Bias Measure.

## Slide 28
ERCOT Primary Frequency Response – BAL-003-1
2015 Bias and Frequency Response Measure

## Slide 29
BAL-003-1 Performance to R1
R1 Present Interconnection Minimum Frequency Response Requirement: -413 MW/0.1 Hz
Using the Median Measure

## Slide 30: Ercot total energy and wind production
Total ERCOT Energy and Total Energy Production from Wind Resources.