## Slide 1
2015 Ancillary Services Methodology
Dan Woodfin
Director, System Operations
TAC
October 23, 2014

## Slide 2: Annual AS Methodology Update
Protocol Section 3.16 - Standards for Determining Ancillary Service Quantities
  ERCOT shall, at least annually, review the quantity and requirements for each Ancillary Service needed for reliability.

## Slide 3: Schedule for Review/Approval

## Slide 4: Overview
Responsive Reserve Service (RRS)
  Review of findings from recent frequency response studies related to FAST and upcoming NERC BAL-003-1 standard implementation
  Proposed changes, based on ROS/WMS input
Non-Spin Reserve Service (NSRS)
  Corresponding NSRS changes based on the proposed RRS changes, based on ROS/WMS input
  Remove Load Forecast bias adjustment
Regulation Service
  Removal of the RRS schedule release as an input to the Reg-Up procurement analysis
  Routine update of factors for installed wind capacity

## Slide 5: Background on RRS Requirements
ERCOT, as a single BA Interconnection, has historically been concerned with low frequency events and has procured RRS to protect against those events
The quantity of RRS procured has been 2300 MW since the nuclear units came on line in the late 1980’s
To meet new NERC BAL-003-1 requirements that are effective in early 2016, ERCOT will need to protect against UFLS for the simultaneous loss of two largest units (currently 2750 MW).
  While ERCOT has historically studied the impact of the simultaneous loss of the two largest units in ERCOT, the quantity of RRS procured has not always been enough to protect against the activation of the under-frequency load shed (UFLS) for a simultaneous trip of these units
  ERCOT would like to modify the A/S Methodology meet this standard in 2015 in order to get operating experience and resolve any issues before the standard becomes effective

## Slide 6: Example of Frequency Response Study Result
Minimum amount of FFR and PFR is determined by preventing frequency from dropping below 59.4Hz for loss of 2 largest units (2750MW)

## Slide 7: FAST Study Case Selection
case1
case2
case3
case4
case5
case6
case7
case8
case9
case10
case11
case12
Inertia=2*Kinetic Energy=2*H*MVA
Notes: Upper portion of the box represents 75% lower is 25% line in the box is 50%
Line at the top and bottom is 3 standard deviations and outside those lines are outliers

## Slide 8: FAST Case results Load Resource (FFR) and PFR Requirement
 | Case1 | Case2 | Case3 | Case4 | Case5 | Case6 | Case7 | Case8 | Case9 | Case10 | Case11 | Case12
FFR/PFR | 2.2:1 | 2.0:1 | 1.5:1 | 1.4:1 | 1.3:1 | 1.25:1 | 1.13 :1 | 1.08:1 | 1.0:1 | 1.0:1 | 1.0:1 | 1.0:1
Netload Level(GW) | 15-20 | 15-20 | 20-25 | 25-30 | 30-35 | 35-40 | 40-45 | 45-50 | 50-55 | 55-60 | 60-65 | 60-65
Inertia (GW∙s) | 239 | 271 | 304 | 354 | 403 | 459 | 511 | 556 | 593 | 631 | 664 | 700
PFR Requirement (no FFR) | 5200 | 4700 | 3750 | 3370 | 3100 | 3040 | 2640 | 2640 | 2240 | 2280 | 2140 | 2140
 | Case1 | Case2 | Case3 | Case4 | Case5 | Case6 | Case7 | Case8 | Case9 | Case10 | Case11 | Case12
FFR/PFR | 2.2:1 | 2.0:1 | 1.5:1 | 1.4:1 | 1.3:1 | 1.25:1 | 1.13 :1 | 1.08:1 | 1.0:1 | 1.0:1 | 1.0:1 | 1.0:1
PFR Requirement | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240
FFR Requirement | 1800 | 1696 | 1641 | 1511 | 1431 | 1440 | 1239 | 1296 | 1000 | 1040 | 900 | 900
Combined Total | 3040 | 2936 | 2881 | 2751 | 2671 | 2680 | 2479 | 2536 | 2240 | 2280 | 2140 | 2140
Inertia=2*Kinetic Energy=2*H*MVA
“Equivalency Ratio” between RRS from LRs and Gen

## Slide 9: What do these studies mean?
The amount of reserves that are needed changes depending on the amount of synchronous generation (inertia) that is committed
  The amount of RRS needed during low inertia periods is higher than the amount currently procured
During low inertia periods, RRS from LRs are more effective per MW than from generation
  “Equivalency Ratio” is 1:1 for higher inertia periods

## Slide 10: Why changes are needed?
If amount of RRS was updated as indicated by new studies, and the historic practice of procuring the same amount of RRS for the entire year, based on the most critical conditions, were followed:
  The current 2800MW RRS amount would increase to over 5,000 MW for all hours
However, the other aspects of the recent studies should also be considered:
  Recognizing the reduced need for RRS during high load periods is probably warranted; and
  Recognizing the higher effectiveness of Load Resources in some periods is probably warranted
The question is “how to do it appropriately?”
  Recognizing that ERCOT system changes are not feasible by 1/2015
In addition, the tradeoff between certainty and efficiency needs to be considered

## Slide 11: “Option 2” from ROS/WMS Meeting
Once annually, ERCOT will post amounts of RRS (six 4-hour blocks) for each month.
  These amounts will be based on expected diurnal load and wind patterns for the month and covering for 70% of historic system inertia conditions (see slide 8).
These annually published amounts are the values that will be procured in in the DAM for each hour of the year.
The posted RRS amounts will be based on an assumption that 50% of RRS requirement is met by LRs and the appropriate Equivalency Ratio for the expected conditions for that hour will be used.

## Slide 12: ROS/WMS Recommendation
  1. Option 2 (as presented by ERCOT at the 10/6/14 Joint ROS/WMS meeting),
  2. Using 20% adjustment factor*,
  3. Do not transfer any of calculated NSRS amount to RRS,
  4. Revisit the NSRS procurement methodology;
  5. Amounts published annually are fixed amounts, not advisory,
  6. Amounts are calculated using 70th percentile of cases in each particular bin,
  7. Load Resources remain limited to providing a maximum of 50% of RRS,
  8. Make changes to Regulation as recommended by ERCOT,
  9. Effective date of RRS and Non-Spin changes to be effective June 1, 2015:
  Regulation change to be effective January 1, 2015 but remainder of 2014 AS Methodology remains in effect until June 1, 2015.
  * Will require Protocol change; ERCOT will submit NPRR

## Slide 13: WMS/ROS Recommendation – Example Quantities
August - 2015 |  |  |  | 
HE | Total RRS MW (Based on 20% Limit) | PFRS | LRs | Equivalency Ratio
22-02 | 2702 | 1453 | 1453 | 1.25
03-06 | 2702 | 1453 | 1453 | 1.25
07-10 | 2702 | 1453 | 1453 | 1.25
11-14 | 2538 | 1394 | 1394 | 1.08
15-18 | 2300 | 1248 | 1248 | 1.00
19-22 | 2538 | 1394 | 1394 | 1.08
October - 2015 |  |  |  | 
HE | Total RRS MW (Based on 20% Limit) | PFRS | LRs | Equivalency Ratio
22-02 | 3002 | 1602 | 1602 | 1.50
03-06 | 3002 | 1602 | 1602 | 1.50
07-10 | 2808 | 1503 | 1503 | 1.40
11-14 | 2696 | 1447 | 1447 | 1.30
15-18 | 2696 | 1447 | 1447 | 1.30
19-22 | 2696 | 1447 | 1447 | 1.30
April- 2015 |  |  |  | 
HE | Total RRS MW (Based on 20% Limit) | PFRS | LRs | Equivalency Ratio
22-02 | 3002 | 1602 | 1602 | 1.50
03-06 | 3132 | 1655 | 1655 | 2.00
07-10 | 2808 | 1503 | 1503 | 1.40
11-14 | 2808 | 1503 | 1503 | 1.40
15-18 | 2808 | 1503 | 1503 | 1.40
19-22 | 2808 | 1503 | 1503 | 1.40
January- 2015 |  |  |  | 
HE | Total RRS MW (Based on 20% Limit) | PFRS | LRs | Equivalency Ratio
22-02 | 2808 | 1503 | 1503 | 1.40
03-06 | 3002 | 1602 | 1602 | 1.50
07-10 | 2808 | 1503 | 1503 | 1.40
11-14 | 2808 | 1503 | 1503 | 1.40
15-18 | 2808 | 1503 | 1503 | 1.40
19-22 | 2808 | 1503 | 1503 | 1.40

## Slide 14: Proposed Changes for Non Spin Service
Remove transfer of 500 MW from Non-Spin to RRS
Remove one-sided bias adjustment, so that NSRS quantity is based solely on 6 hour ahead Net Load Forecast uncertainty, less the Reg Up requirement, capped at 2000 MW

## Slide 15: Proposed Changes for Regulation
Update the factors used to adjust the Regulation Service quantities for additional installed wind generation since June 2013
  Added approximately 988 MW of Wind since last analyses
Remove RRS schedule release as an input to the Reg-Up procurement analysis
  Carried over from Zonal, where RRS deployment was energy deployment
  In Nodal, RRS deployment is only release of schedule not an energy deployment
  RRS was very frequently used in Zonal to replace regulation-up

## Slide 16: Impact of RRS Deployment on Feb 2014 HE 0700

## Slide 17
Discussion