| NOGRR Number | 135 | NOGRR Title | Constraint Management During Energy Emergency Alerts |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Tabled |
| Date of Decision |  | October 22, 2014 |  |  |
| Proposed Effective Date |  | To be determined. |  |  |
| Priority and Rank Assigned |  | To be determined. |  |  |
| Nodal Operating Guide Sections Requiring Revision |  | 4.2.3, Watch 4.5.2, Operating Procedures 4.5.3, Implementation 4.5.3.1, General Procedures Prior to EEA Operations |  |  |
| Other Binding Documents Requiring Revision or Related Revision Requests |  | Nodal Protocol Revision Request (NPRR) 642, Constraint Management During Energy Emergency Alerts |  |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) seeks to improve management of congestion during an Energy Emergency Alert (EEA) by proposing: - Language that provides a mechanism for ERCOT Operations to manage constraints in EEA 2 or 3 to higher Facility ratings when applicable for those constraints identified as limiting generation output; and - Language that reconsiders use of double-circuit contingencies during emergency operations based on Grid conditions. |  |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) |  |  |
| Procedural History |  | - On 7/23/14, NOGRR135 and an associated Impact Analysis were posted. - On 8/19/14, the Operations Working Group (OWG) considered NOGRR135. - On 10/7/14, ROS comments were posted. - On 10/21/14, Luminant comments were posted. - On 10/22/14, OWG again considered NOGRR135. |  |  |
| OWG Decision |  | On 8/19/14, OWG was in consensus to table NOGRR135 for one month. On 10/22/14, OWG was in consensus to table NOGRR135. |  |  |
| Summary of OWG Discussion |  | On 8/19/14, participants discussed the benefits of tabling NOGRR135 in an effort to receive additional input from the upcoming joint WMS/ROS meeting to discuss NOGRR135 and NPRR642. On 10/22/14, participants agreed to table NOGRR135 to allow for additional comments to be submitted. |  |  |

| Business Case |  |
| --- | --- |
| Qualitative Benefits | Improved transparency with regards to transmission constraint management during an EEA |
| Quantitative Benefits | Improved efficiency in the Real-Time Market (RTM) during an EEA due to an increase in available capacity for Dispatch by Security-Constrained Economic Dispatch (SCED) |
| Impact to Market Segments |  |
| Other |  |

| Sponsor |  |
| --- | --- |
| Name | Chad Thompson |
| E-mail Address | Chad.Thompson@ercot.com |
| Company | ERCOT |
| Phone Number | 512-255-6508 |
| Cell Number | 512-750-3476 |
| Market Segment | Not applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Brian Manning |
| E-Mail Address | Brian.manning@ercot.com |
| Phone Number | 512-248-3937 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| ROS 100714 | Requested OWG table to allow for additional time for Market Participants to file comments to align this NOGRR with NPRR642. |
| Luminant 102114 | Proposed revisions to align with comments submitted on NPRR642. |

Proposed Guide Language Revision

4.2.3	Watch

(1)	A Watch may be issued by ERCOT in accordance with Protocol Section 6.5.9.3.3, Watch, when it recognizes that conditions have developed such that an Emergency Condition exists or is imminent.

(2)	ERCOT may require information from QSEs and TOs.  Typical information requested may include, but is not limited to:

(a)	Resource fuel capabilities;

(b)	Resource condition details; and

(c)	Actual weather conditions.

(3)	When a post-contingency overload of an element cannot be rectified, including through the use of Constraint Management Plans (CMPs), ERCOT shall issue a Watch.

(4)	When a Watch is issued for Physical Responsive Capability (PRC) below 2,500 MW, ERCOT shall begin to identify constraints active in Security-Constrained Economic Dispatch (SCED) and determine which constraints have the potential to limit generation output.  Those identified constraints may be evaluated with the TOs that own or operate the overloaded Transmission Facilities associated with those constraints and the Resource Entity whose generation output would be limited to determine if:

(a)	A 15-Minute Rating is available that allows for additional transmission capacity for use in congestion management in the event an EEA Level 2 or 3 is declared;

(b)	Post-contingency actions can be taken within 15 minutes to return the flow to within the Normal Rating.  Such actions may include but are not limited to reducing the generation that increased its output as a result of enforcing the 15-Minute Rating rather than the Emergency Rating; or

(c)       Restoring Transmission Elements that are out of service, reconfiguring the transmission system, or adjusting of phase angle regulator tap positions would allow for additional transmission capacity to allow for additional output from the limited Resource Entity.

ERCOT shall coordinate, time permitting, with TOs who own and operate the Transmission Facilities associated with the double-circuit contingencies for the constraints identified above to determine whether the double-circuit failures are at risk of occurring due to system conditions or whether those double-circuit contingencies identified are at low risk of double-circuit failure.

(5)	ERCOT shall provide verbal notice of the Watch to all TOs and QSEs and shall post the message electronically to the MIS Public Area.  QSEs shall notify appropriate Resources, REPs, and LSEs.  TOs shall notify their represented TSPs.

4.5.2	Operating Procedures

(1)	The ERCOT System Operators have the authority to make and carry through decisions that are required to operate the ERCOT System during emergency or adverse conditions.  ERCOT will have sufficiently detailed operating procedures for emergency or short supply situations and for restoration of service in the event of a Partial Blackout or Blackout.  These procedures will be distributed to the personnel responsible for performing specified tasks to handle emergencies, remedy short supply situations, or restore service.  Transmission Service Providers (TSPs) will develop procedures to be filed with ERCOT describing implementation of ERCOT requests in emergency and short supply situations, including interrupting Load, notifying others and restoration of service.

(2)	ERCOT and each TSP will endeavor to maintain transmission ties intact if at all possible.  This will:

(a) 	Permit rendering the maximum assistance to an area experiencing a deficiency in generation;

(b) 	Minimize the possibility of cascading loss to other parts of the system; and

(c) 	Assist in restoring operation to normal.

(3)	ERCOT's operating procedures will meet the following goals while continuing to respect the confidentiality of market sensitive data.  If all goals cannot be respected simultaneously then the priority order listed below shall be respected:

(a)	Maintain station service for nuclear generating facilities;

(b)	Securing startup power for power generating plants;

(c)	Operating generating plants isolated from ERCOT without communication;

(d)	Restoration of service to critical Loads such as:

(i)	Military facilities;

(ii)	Facilities necessary to restore the electric utility system;

(iii)	Law enforcement organizations and facilities affecting public health; and

(iv)	Communication facilities.

(e)	Maximum utilization of ERCOT System capability;

(f)	Utilization of Responsive Reserve (RRS) services and other Ancillary Services to the extent permitted by ERCOT System conditions;

(g)	Utilization of the market to the fullest extent practicable without jeopardizing the reliability of the ERCOT System;

(h)	Restoration of service to all Customers following major system disturbances, giving priority to the larger group of Customers; and

(i) 	Management of Interconnection Reliability Operating Limits (IROLs) shall not change.

4.5.3	Implementation

(1)	ERCOT shall be responsible for monitoring system conditions, initiating the EEA levels below, notifying all Qualified Scheduling Entities (QSEs) and Transmission Operators (TOs), and coordinating the implementation of the EEA conditions while maintaining transmission security limits.  QSEs and TOs will notify all the Market Participants they represent of each declared EEA level.

(2)	During the EEA, ERCOT has the authority to obtain energy from non-ERCOT Control Areas using Direct Current Tie(s) (DC Tie(s)) or by using Block Load Transfers (BLTs) to move load to non-ERCOT Control Areas.  ERCOT maintains the authority to curtail energy schedules flowing into or out of the ERCOT System across the DC Ties in accordance with North American Electric Reliability Corporation (NERC) scheduling guidelines.

(3) 	ERCOT, at management’s discretion, may at any time issue an ERCOT-wide appeal through the public news media for voluntary energy conservation.

(4)	There may be insufficient time to implement all levels in sequence.  ERCOT may immediately implement Level 3 of the EEA any time the steady-state system frequency is below 59.8 Hz and shall immediately implement Level 3 any time the steady-state frequency is below 59.5 Hz.

(5)	Percentages for Level 3 Load shedding will be based on the previous year’s TSP peak Loads, as reported to ERCOT, and will be reviewed by ERCOT and modified annually.

(6)	The ERCOT System Operator shall declare the EEA levels to be taken by QSEs and TSPs.  QSEs and TSPs shall implement actions under that level (and all above if not previously accomplished) and if ordered by the ERCOT shift supervisor or his designate, shall report back to the ERCOT System Operator when the requested level has been completed.

(7)	During EEA Level 3, ERCOT must be capable of shedding sufficient firm Load to arrest frequency decay and to prevent generator tripping.  The amount of firm Load to be shed may vary depending on ERCOT Transmission Grid conditions during the event.  Each TSP will be capable of shedding its allocation of firm Load, without delay.  The maximum time for the TSP to interrupt firm Load will depend on how much Load is to be shed and whether the Load is to be interrupted by Supervisory Control and Data Acquisition (SCADA) or by the dispatch of personnel to substations.  Since the need for firm Load shed is immediate, interruption by SCADA is preferred.  The following requirements apply for an ERCOT instruction to shed firm Load:

(a)	Load interrupted by SCADA will be shed without delay and in a time period not to exceed 30 minutes;

(b)	Load interrupted by dispatch of personnel to substations to manually shed Load will be implemented within a time period not to exceed one hour;

(c)	The initial clock on the firm Load shed shall apply only to Load shed amounts up to 1000 MW total.  Load shed amount requests exceeding 1000 MW on the initial clock may take longer to implement; and

(d)	If, after the first Load shed instruction, ERCOT determines that an additional amount of firm Load should be shed, another clock will begin anew.  The time frames mentioned above will apply.

(8)	Each TSP, or its designated agent, will provide ERCOT a status report of Load shed progress within 30 minutes of the time of ERCOT’s instruction or upon ERCOT’s request.

(9)	During EEA Level 2 or 3, for those constraints that meet the criteria identified in paragraph (4) of Section 4.2.3, Watch, ERCOT may control the post-contingency flow to within the 15-Minute Rating in Security-Constrained Economic Dispatch (SCED).   After the EEA Level 2 or 3 condition has ended, ERCOT shall restore control of the post -ontingency flow to within the Emergency Rating for these constraints that utilized the 15-Minute Rating in SCED during the EEA.

(10)	For those constraints that meet the criteria identified in paragraph (4) of Section 4.2.3, Watch, ERCOT shall continue to enforce constraints associated with double-circuit contingencies throughout the EEA, including EEA Level 2 or 3, if the double-circuit failures are determined to be at risk of occurring due to system conditions.  For those double-circuit contingencies identified in paragraph (4) of Section 4.2.3, Watch, to be at low risk of double-circuit failure, ERCOT may elect to enforce only the associated single-circuit contingencies during EEA Level 2 or 3.  For constraints related to stability limits that are not IROLs, ERCOT may elect not to enforce double-circuit contingencies during EEA Level 3 only.

4.5.3.1 	General Procedures Prior to EEA Operations

Prior to declaring EEA Level 1 detailed in Section 4.5.3.3, EEA Levels, ERCOT may perform the following operations consistent with Good Utility Practice:

(a)	Provide Dispatch Instructions to QSEs for specific Resources to operate at an Emergency Base Point to maximize Resource deployment so as to increase Responsive Reserve levels on other Resources;

(b)	Commit specific available Resources as necessary that can respond in the timeframe of the emergency.  Such commitments will be settled using the Hourly Reliability Unit Commitment (HRUC) process;

(c)	Start Reliability Must-Run (RMR) Units available in the time frame of the emergency.  RMR Units should be loaded to full capability;

(d)	Utilize available Resources providing Non-Spinning Reserve (Non-Spin) services as required; and

(e)	ERCOT shall use the Physical Responsive Capability (PRC) to determine the appropriate Emergency Notice and EEA levels.