## Resource Registration Glossary
PROTOCOL DISCLAIMER
This Resource Registration Glossary describes ERCOT processes and is not intended to be a substitute for the ERCOT Nodal Protocols (available at http://www.ercot.com/mktrules/nprotocols/), as amended from time to time. If any conflict exists between this document and the ERCOT Nodal Protocols, the ERCOT Nodal Protocols shall control in all respects.
SECTION 2: RESOURCE REGISTRATION GLOSSARY - Effective November 1, 2014
RARF Tab | Wind | Conventional Generation (Gen) | Combined Cycle (CC) | Load Resources | Notes | Field Name | Definition / Detailed Description | Screening Study (SS) (R, C, O, A) | Full Interconnect Study (FIS) (R, C, O, A) | Full Registration (R, C, O, A) | Effective Date
GENERAL_SITE_ESIID_Information - General and Site Information
General and Site | X | X | X |  | List | This submittal is for | Select from drop down: New Site, Revision, Addition of unit(s), or Deletion of unit(s). |  |  | R
General and Site | X | X | X |  | Date | Date Form Completed | Enter date in the format MM/DD/YYYY. |  |  | R
General and Site | X | X | X |  | Text | Resource Entity Submitting Form | Enter the name of the Resource Entity. This must be the same entity name that filed as a Resource Entity on the Standard Form Agreement. The Protocols require that a Load Resource must also complete and submit an Application. | R | R | R
General and Site | X | X | X |  | Number | Resource Entity DUNS # | Enter the Market Participant unique identifier as registered with ERCOT for the Resource Entity (DUNS number plus 4 as assigned by ERCOT). |  |  | R
General and Site | X | X | X |  | Text | Resource Site Name | Resource site or main Facility name (i.e. Cedar Bayou Plant). Determined jointly with ERCOT. | R | R | R
General and Site | X | X | X |  | Text | Resource Site Code | Code for Resource site (i.e. Cedar Bayou Plant it is CBY). Determined jointly with ERCOT. |  |  | R
General and Site | X | X | X |  |  | Street Address | Physical Street Address of the plant site |  |  | R
General and Site | X | X | X |  |  | City | City of the site |  |  | R
General and Site | X | X | X |  |  | State | State of the site |  |  | R
General and Site | X | X | X |  |  | Zipcode | Zipcode of the site |  |  | R
General and Site | X | X | X |  |  | County | County of the site | R | R | R
General and Site | X | X | X |  | Date | Site In-Service Date | Date is the date when site was (or is planned to be) commissioned. | R | R | R
General and Site | X | X | X |  | Date | Site Stop Service Date | Date is the date when site will be decommissioned. Blank if not known. |  |  | O
General and Site | X | X | X |  | List | Congestion Management Zone for 2003: | This information can be found in the ERCOT Data Dictionary on the Planning and Operations Information website. For newer units, please contact ERCOT. |  |  | O
General and Site | X | X | X |  | Y/N | Resource owned by NOIE? (Y/N) | Indicate NOIE Ownership of Resource | R | R | R
General and Site | X | X | X |  | Y/N | Is Resource behind a NOIE Settlement Meter Point? (Y,N) | For Resources that are connected to the grid behind NOIE Settlement Meter Points |  |  | R
General and Site | X | X | X |  |  | Number of EPS Primary meters | Enter the total number of primary ERCOT-Polled Settlement (EPS) Meters associated with this site. |  |  | R
General and Site | X | X | X |  | Y/N | Is Resource claiming status as a Non-Modeled Generator as defined in ERCOT Protocol Section 2. | Refer to Protocol Section 2, Definitions and Acronyms, for the definition of a Non-Modeled Generator. Required if Resource is claiming Non-Modeled Generator status. |  |  | C
General and Site | X | X | X |  | Y/N | Is Resource >10 MW? | Indicate if the Resource is greater than 10 MW. Required if Resource is claiming Non-Modeled Generator status. |  |  | C
General and Site | X | X | X |  | Text | Primary Contact | Enter the Primary Contact person who can address ERCOT questions regarding Resource Registration submittal. Enter the contact's name, title, phone number, email address, and fax number. | R | R | R
General and Site | X | X | X |  | Text | Title: | Enter the Title of the Primary Contact |  |  | R
General and Site | X | X | X |  |  | Phone Number: | Enter the Phone Number for the Primary Contact |  |  | R
General and Site | X | X | X |  |  | E-mail Address: | Enter the E-mail Address for the Primary Contact |  |  | R
General and Site | X | X | X |  |  | Fax Number: | Enter the Fax Number for the Primary Contact |  |  | O
General and Site | X | X | X |  | Text | Secondary Contact | Enter the Secondary Contact person who can address ERCOT questions regarding Resource Registration submittal. Enter the contact's name, title, phone number, email address, and fax number. | O | O | O
General and Site | X | X | X |  | Text | Title: | Enter the Title of the Secondary Contact |  |  | O
General and Site | X | X | X |  |  | Phone Number: | Enter the Phone Number for the Secondary Contact |  |  | O
General and Site | X | X | X |  |  | E-mail Address: | Enter the E-mail Address for the Secondary Contact |  |  | O
General and Site | X | X | X |  |  | Fax Number: | Enter the Fax Number for the Secondary Contact |  |  | O
GENERAL_SITE_ESI ID_Information - Gen Load Split - ESI ID
Gen Load Split - ESIID | X | X | X |  | Y/N | Gen. Load Splitting (Y or N) | Indicate if unit(s) represent Split Generation Resources behind the EPS Meter or if Load is split across multiple TDSPs. |  |  | R
Gen Load Split - ESIID | X | X | X |  | Y/N | ERCOT Read (Y or N) | Indicate if the meter is an EPS Meter. |  |  | R
Gen Load Split - ESIID | X | X | X |  | Number | ESI ID | Enter the ESI ID. Required unless behind a NOIE Settlement Point. |  |  | C
Gen Load Split - ESIID | X | X | X |  | List | TDSP Providing Service To Resource | From the drop-down menu, select the name of the TDSP that provides transmission or distribution service to the site for the ESI ID. Required unless behind a NOIE Settlement Point. |  |  | C
Gen Load Split - ESIID | X | X | X |  | Automatic | TDSP DUNS Number | The TDSP DUNS number is automatically populated based on TDSP selection. |  |  | A
Gen Load Split - ESIID | X | X | X |  | % | Fixed Load Splitting % | Enter the fixed percentage of Load associated with each ESI ID. |  |  | C
Gen Load Split - ESIID | X | X | X |  | List | Load Serving Entity | Enter the Load Serving Entity (LSE) associated with that ESI ID. |  |  | C
Gen Load Split - ESIID | X | X | X |  | Automatic | Load Serving Entity DUNS # | The LSE DUNS number is automatically populated based on LSE selection. |  |  | A
GENERAL_SITE_ESIID_Information - Private Network - Site
Private Network - Site | X | X | X |  | Y/N | Private Network? | Indicate if the site is a Private Use Network as defined in the Protocol Section 2. | R | R | R
Private Network - Site | X | X | X |  | MW | Average Amount of Self-Serve private Load | If the site is a Private Use Network, then enter the amount of the total site generation MW output used for self serve and not available for the grid. | C | C | C
Private Network - Site | X | X | X |  | MVAr | Average Amount of Self-Serve private reactive Load | If the site is a Private Use Network, then enter the amount of the total site generation MVAr output used for self serve and not available for the grid. | C | C | C
Private Network - Site | X | X | X |  | MW | Expected Typical Private Network Net Interchange | If the site is a Private Use Network, then enter the MW Net Interchange with ERCOT grid (typically Net=Gen-Load). | C | C | C
Private Network - Site | X | X | X |  | MVAr | Expected Typical Private Network Net Reactive Interchange | If the site is a Private Use Network, then enter the MVAr Net Interchange with ERCOT grid (typically Net=Gen-Load). | C | C | C
Private Network - Site | X | X | X |  | MW | Private Network Gross Unit Capability | If the site is a Private Use Network, then enter the MW Gross Generation Capability for the Site | C | C | C
Private Network - Site | X | X | X |  | MVAr | Private Network Gross Unit Reactive Capability | If the site is a Private Use Network, then enter the MVAr Gross Generation Capability for the Site | C | C | C
Private Network - Site | X | X | X |  | % | Large Motor, percent of total MW Load | Enter % of total MW Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  | C
Private Network - Site | X | X | X |  | % | Small Motor, percent of total MW Load | Enter % of total MW Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  | C
Private Network - Site | X | X | X |  | % | Resistive (Heating) Load, percent of total MW Load | Enter % of total MW Load per Load type. |  |  | C
Private Network - Site | X | X | X |  | % | Discharge Lighting, percent of total MW Load | Enter % of total MW Load per Load type. |  |  | C
Private Network - Site | X | X | X |  | % | Other, percent of total MW Load | Enter % of total MW Load per Load type. |  |  | C
Private Network - Site | X | X | X |  | % | Large Motor, percent of total MVAr Load | Enter % of total MVAr Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  | C
Private Network - Site | X | X | X |  | % | Small Motor, percent of total MVAr Load | Enter % of total MVAr Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  | C
Private Network - Site | X | X | X |  | % | Discharge Lighting, percent of total MVAr Load | Enter % of total MVAr Load per Load type. |  |  | C
Private Network - Site | X | X | X |  | % | Other, percent of total MVAr Load | Enter % of total MVAr Load per Load type. |  |  | C
Unit Information
Unit Information | X | X | X |  | Text | Resource Site Code | Enter the Site Code established in the General and Site Information tab of the GENERAL_SITE_ESIID_Information workbook. | R | R | R
Unit Information | X | X | X |  | Text | Unit Name | Enter Unit Code for the generator unit (e.g.. Cedar Bayou Plant Gen 1 is "CBYG1"). | R | R | R
Unit Information | X | X | X |  | Automatic | Resource Name (Unit Code/Mnemonic) | Concatenated mnemonic of Resource Site Code and Unit name (e.g. CBY_CBYG1). |  |  | A
Unit Information | X | X | X |  | Y/N | Non Modeled Generator | Refer to ERCOT Protocol Section 2 for the definition of a Non-Modeled Generator. |  |  | R
Unit Information | X | X | X |  | Number | PUC Registration Number | Enter the PUCT registration number. |  |  | O
Unit Information | X | X | X |  | Number | ERCOT Interconnection Project Number | Enter the ERCOT INR number. Required for new or upgraded units. |  | C | C
Unit Information | X | X | X |  | Number | NERC Number | Enter NERC NCR number. |  |  | O
Unit Information | X | X | X |  | Y/N | Qualifying Facility | Refer to ERCOT Protocol Section 2 for the definition of Qualifying Facility. |  |  | R
Unit Information | X | X | X |  | Date | Transmission Only MRD | Planned Point of Interconnection (POI) substation energization (backfeed) date for new Resources used to plan Resource integration schedule. |  |  | O
Unit Information | X | X | X |  | Date | Standard Generation Interconnect Agreement (SGIA) Signature Date | Enter the date the Resource signed SGIA. For NOIEs, use MOU date. |  |  | R
Unit Information | X | X | X |  | Date | Unit Start Date (Model Ready Date) | Planned initial energy production (synchronization) date for a new unit used to plan the resouce integration schedule. |  |  | O
Unit Information | X | X | X |  | Date | Unit Commercial Date | Enter the unit's planned commercial operations date. (used in accordance with paragraph (b) of Protocol Section 4.4.9.4.1 , Mitigated Offer Cap. After commercial operations is declared, this field should be updated with the actual commercial operations date. | R | R | R
Unit Information | X | X | X |  | Date | Unit Retirement Date | Enter the date of expected or actual retirement. Leave blank if unknown. |  |  | O
Unit Information | X | X | X |  | All Caps | SubStation Code/SubStation Mnemonic (POI) | Enter the interconnecting transmission station code. If you need assistance in determining the corresponding ERCOT Substation Code\Substation Mnemonic, please work with your TDSP or ERCOT. | R | R | R
Unit Information | X | X | X |  | kV | Voltage Level (POI) | Enter the nominal voltage level at the Point of Interconnection. If you need assistance in determining the corresponding Voltage Level, please work with your TDSP or ERCOT. | R | R | R
Unit Information | X | X | X |  | Number | PTI Bus Number (POI) | Enter the PTI Bus Number at the Point of Interconnection in the planning model. If you need assistance in determining the corresponding PTI Bus Number, please work with your TDSP or ERCOT. | R | R | R
Unit Information | X | X | X |  | List | Primary Fuel Type | AB -- Agriculture Byproducts (bagasse, straw, energy crops) BFG -- Blast-Furnace Gas BIT -- Bituminous Coal BL -- Black liquor DFO -- Distillate Fuel Oil (diesel, No1 fuel oil, No 2 fuel oil, No 4 fuel oil) GEO -- Geothermal JF -- Jet Fuel KER -- Kerosene LFG -- Landfill Gas LIG -- Lignite MSW -- Municipal Solid Waste (refuse) NA -- Not Applicable NG -- Natural Gas NUC -- Nuclear (uranium, plutonium, thorium) OBG -- Other - Biomass Gas (methane, digester gas) OBL -- Other - Biomass Liquids (ethanol, fish oil, waste alcohol, other gases) OBS -- Other - Biomass Solids (animal manure/waster, medical waste, paper pellets, paper derived fuel) OG -- Other - Gas (butane, coal processes, coke-oven coal, methanol, refinery gas) OO -- Other - Oil (butane, crude, liquid byproducts, oil waste, propane) OTH -- Other (batteries, chemicals, hydrogen pitch sulfur, misc technologies) PC -- Petroleum Coke PG -- Propane RFO -- Residual Fuel Oil (No 5 and No 6 fuel oil) STM -- Steam from other units SLW -- Sludge Waste SUB -- Sub-bituminous Coal SUN -- Solar (photovoltaic, thermal) TDF -- Tires T -- Tidal WAT -- Water (conventional, pumped storage) WDL -- Wood/Wood Waste - Liquids (red liquor, sludge wood spent sulfite liquor, other liquors) WDS -- Wood/Wood Waste - Solids (peat, railroad ties, utility poles, wood chips, other solids) WH -- Waste heat WND -- Wind WOC -- Waste / Other Coal | R | R | R
Unit Information | X | X | X |  | List | Secondary Fuel Type | Same data entry elements as primary fuel type, but for secondary or start-up fuel. | R | R | R
Unit Information | X | X | X |  | List | Fuel Transportation Type | CV -- Conveyor PL -- Pipeline RR -- Railroad TK -- Truck NA -- Not Applicable |  |  | R
Unit Information | X | X | X |  | List | Resource Category | Nuclear Hydro Coal and Lignite Combined Cycle ≤ 90 MW* Combined Cycle > 90 MW* Gas Steam - Supercritical Boiler Gas Steam - Reheat Boiler Gas Steam - Non-reheat or Boiler without air-preheater Simple Cycle ≤ 90 MW Simple Cycle > 90 MW Diesel Renewable |  |  | R
Unit Information | X | X | X |  | Y/N | Renewable | Indicate if the unit is a Renewable Energy Credit (REC) generator, as certified with the PUCT. |  |  | R
Unit Information | X | X | X |  | Y/N | Renewable/Offset | REC offset generators that produce generation to cover offsets they have been approved to provide, as certified with the PUCT. |  |  | R
Unit Information | X | X | X |  | List | Physical Unit Type | CA -- Combined cycle steam turbine part (includes steam part of integrated coal gasification combined cycle) CC -- Combined cycle total unit (use only for plants/generators that are in planning stage, for which specific generator details cannot be provided) CE -- Compressed air energy storage CS -- Combined cycle single shaft (combustion turbine and steam turbine share a single generator) CT -- Combined cycle combustion/gas turbine part (includes comb. turbine part of integrated coal gasification combined cycle) FC -- Fuel Cell GT -- Simple-cycle Combustion (gas) turbine (includes jet engine design) HY -- Hydraulic turbine (includes turbines associated with delivery of water by pipeline IC -- Internal combustion (diesel, piston) engine NA -- Unknown at this time (planned units only) OT -- Other PS -- Hydraulic Turbine - Reversible (pumped storage) PV -- Photovoltaic ST -- Steam Turbine including nuclear, geothermal and solar. Does not include combined cycle. WT -- Wind Turbine | R | R | R
Unit Information | X | X | X |  | MVA | Name Plate Rating | Name Plate MVA Rating of this unit at its rated power factor. | R | R | R
Unit Information | X | X | X |  | MW | Real Power Rating | Maximum rated MW at rated power factor. | R | R | R
Unit Information | X | X | X |  | MVAr | Reactive Power Rating | Maximum MVAr at rated power factor | R | R | R
Unit Information | X | X | X |  | MW | Turbine Rating | Maximum gross designed MW of the turbine | R | R | R
Unit Information | X | X | X |  | kV | Unit Generating Voltage | Terminal voltage of generating unit | R | R | R
Unit Information | X | X | X |  | % | Governor Droop Settings | The percent change in nominal frequency that will cause generator output to change from no Load to full Load. |  |  | C
Unit Information | X | X | X |  | Hz | Goverrnor Dead-band | The Hz deviation of system frequency (+/-) that produces no turbine Governor response, and therefore, no frequency (speed) regulation. |  |  | R
Unit Information | X | X | X |  | degree F | Design Max Ambient Temperature | This is the plant design maximum (high) air temperature. |  |  | O
Unit Information | X | X | X |  | degree F | Design Min Ambient Temperature | This is the plant design minimum (low) air temperature. |  |  | O
Unit Information | X |  |  |  | degree F | Maximum Operating Temperature | The highest ambient temperature at which individual turbines may cease operating due to procedural requirements or equipment limitations. (Most limiting condition) |  |  | R | Insert field upon system implementation of RRGRR003
Unit Information | X |  |  |  | degree F | Minimum Operating Temperature | The lowest ambient temperature at which individual turbines may cease operating due to procedural requirements or equipment limitations. (Most limiting condition) |  |  | R | Insert field upon system implementation of RRGRR003
Unit Information | X |  |  |  | m/s | High Wind Speed Cut-Out | Sustained wind speed in meters per second at which the turbine will cease operations due to high wind speed |  |  | R | Insert field upon system implementation of RRGRR003
Unit Information |  |  |  |  | minutes | High Wind Speed Cut-Out time | The amount of time associated with the high wind speed cut-out value. (The time used to determine if it is a sustained value, instead of a gust value) |  |  | R | Insert field upon system implementation of RRGRR003
Unit Information | X |  |  |  | m/s | High Wind Speed Cut-Out Reset | The wind speed at which a turbine will begin operating following a cut-out event |  |  | R | Insert field upon system implementation of RRGRR003
Unit Information |  |  |  |  | minutes | High Wind Speed Cut-Out Reset Time | The amount of time associated with the high wind speed cut-out reset value. (The amount of time at or below the reset value following a high wind speed cut-out event before the turbine will begin operating) |  |  | R | Insert field upon system implementation of RRGRR003
Unit Information | X | X | X |  | decimal degrees (N) | Latitude of Center of Plant | The geographic coordinate that specifies the north-south position of the plant provided in decimal degrees | R | R | R
Unit Information | X | X | X |  | decimal degrees (W) | Longitude of Center of Plant | The geographic coordinate that specifies the east-west position of the plant provided in decimal degrees | R | R | R
Unit Information - Train
Unit Info - TRAIN |  |  | X |  | List | Train Name | Train name assigned by ERCOT | R | R | R
Unit Info - TRAIN |  |  | X |  | Automatic | Train Code | A sitecode and train code concatenation |  |  | A
Unit Info - TRAIN |  |  | X |  | Date | Train Unit Commercial Date | Train Unit Commercial Operations Date. It is the date on which Generator declares that the construction of the plant has been substantially completed, trial operation of the plant has been completed, and commercial operations has been declared. Format is MM/DD/YYYY | R | R | R
Unit Info - TRAIN |  |  | X |  | Date | Train Unit Retirement Date | Train Unit Retirement Date in MM/DD/YYYY format. Leave blank if unknown. |  |  | O
Unit Info - TRAIN |  |  | X |  | Y/N | Is train augmented with Duct Burner(s)? | Indicate whether Duct Burner(s) augmentation is available for use |  |  | R
Unit Info - TRAIN |  |  | X |  | Y/N | Is train augmented with Evap Cooler(s)? | Indicate whether Evap Cooler(s) augmentation is available for use |  |  | R
Unit Info - TRAIN |  |  | X |  | Y/N | Is train augmented with Chiller(s)? | Indicate whether Chiller(s) augmentation is available for use |  |  | R
Unit Info - TRAIN |  |  | X |  | Y/N | Other augmentation? | Indicate whether other augmentation is available for use |  |  | R
Unit Info - Wind - Additional Wind Unit Information
Unit Info - Wind | X |  |  |  | meters | Average Height above ground of Turbine Hub | Used for Wind Generation Forecasting |  |  | R
Unit Info - Wind | X |  |  |  | decimal degrees (N) | Latitude of Meteorological Tower | Used for Wind Generation Forecasting |  |  | R
Unit Info - Wind | X |  |  |  | decimal degrees (W) | Longitude of Meteorological Tower | Used for Wind Generation Forecasting |  |  | R
Unit Info - Wind | X |  |  |  | meters | Height of Meteorological Instrumentation - Wind speed | Used for Wind Generation Forecasting |  |  | R
Unit Info - Wind | X |  |  |  | meters | Height of Meteorological Instrumentation - Wind direction | Used for Wind Generation Forecasting |  |  | R
Unit Info - Wind | X |  |  |  | meters | Height of Meteorological Instrumentation - Barometric pressure | Used for Wind Generation Forecasting |  |  | R
Unit Info - Wind | X |  |  |  | meters | Height of Meteorological Instrumentation - Temperature | Used for Wind Generation Forecasting |  |  | R
Unit Info - Turbine Details
Turbine Details | X |  |  |  | Automatic | Resource Name (Unit Code/Mnemonic) | Concatenated mnemonic of Resource Site Code and Unit name (e.g. CBY_CBYG1). |  |  | A
Turbine Details | X |  |  |  | Number | WGR Group | WGR Group # 1,2,3… only if grouping two or more WGRs. Leave blank if not grouping. |  |  | O
Turbine Details | X |  |  |  | Automatic | Site_Group | Automatic field |  |  | A
Turbine Details | X |  |  |  | Number | Total Number of Turbines | Count total of wind turbines | R | R | R
Turbine Details | X |  |  |  | All Caps | Turbine Manufacturer and Model | From name-plate or manufacturer data sheet | R | R | R
Turbine Details | X |  |  |  | MW | MW Rating for this model of Turbine | From name-plate or manufacturer data sheet | R | R | R
Turbine Details | X |  |  |  | Number | Number of Turbine Manufacturer/Model | Count of wind turbines in this group | R | R | R
Turbine Details | X |  |  |  | Number | Turbine Type | Indicate the electrical type of Turbine (eg. Type 1, 2, 3, 4) |  |  | R
Turbine Details | X |  |  |  | MVA | What is the MVA base that the following data is based on? | The MVA Base for stated impedances. |  | R | R
Turbine Details | X |  |  |  | KV | What is the kV base that the following data is based on? | The KV Base for stated impedances. |  | R | R
Turbine Details | X |  |  |  | p.u. | Subtransient Reactance X'',(Instantaneous Fault Current Period) (unsaturated) | Enter the instantaneous subtransient reactance (unsaturated) for the fault. |  | R | R
Turbine Details | X |  |  |  | p.u. | Transient Reactance, X' (First 2-3 cycles of the Fault) (unsaturated) | Enter the transient reactance (unsaturated) for the first 2-3 cycles of the fault. |  | R | R
Turbine Details | X |  |  |  | R in p.u. | Negative Sequence Z (unsaturated) | Enter the negative sequence resistance (unsaturated) for system models. |  | R | R
Turbine Details | X |  |  |  | X in p.u. | Negative Sequence Z (unsaturated) | Enter the negative sequence reactance (unsaturated) for system models. |  | R | R
Turbine Details | X |  |  |  | R in p.u. | Zero Sequence Z (unsaturated) | Enter the zero sequence resistance (unsaturated) for system models. |  | R | R
Turbine Details | X |  |  |  | X in p.u. | Zero Sequence Z (unsaturated) | Enter the zero sequence reactance (unsaturated) for system models. |  | R | R
Turbine Details | X |  |  |  | p.u. | Subtransient Reactance X'',(Instantaneous Fault Current Period) (saturated | Enter the instantaneous subtransient reactance (saturated) for the fault. |  | R | R
Turbine Details | X |  |  |  | p.u. | Transient Reactance, X' (First 2-3 cycles of the Fault) (saturated) | Enter the transient reactance (saturated) for the first 2-3 cycles of the fault. |  | R | R
Turbine Details | X |  |  |  | R in p.u. | Positive Sequence Resistance (saturated) | Enter the positive sequence resistance (saturated) for system models. |  | R | R
Turbine Details | X |  |  |  | X in p.u. | Synchronous Reactance X (After 4 cycles of the fault) (saturated) | Enter the synchronous reactance (saturated) after 4 cycles of the fault. |  | R | R
Turbine Details | X |  |  |  | R in p.u. | Negative Sequence Z (saturated) | Enter the negative sequence resistance (saturated) for system models. |  | R | R
Turbine Details | X |  |  |  | X in p.u. | Negative Sequence Z (saturated) | Enter the negative sequence reactance (saturated) for system models. |  | R | R
Turbine Details | X |  |  |  | R in p.u. | Zero Sequence Z (saturated) | Enter the zero sequence resistance (saturated) for system models. |  | R | R
Turbine Details | X |  |  |  | X in p.u. | Zero Sequence Z (saturated) | Enter the zero sequence reactance (saturated) for system models. |  | R | R
Turbine Details | X |  |  |  | p.u. | Grounding Resistance For An Impedance Grounded Generator In p.u. (100 MVA Base) | Zero sequence resistance value of the generator grounding impedance is required. The value must be specified on a 100 MVA base. |  | R | R
Turbine Details | X |  |  |  | p.u. | Grounding Reactance For An Impedance Grounded Generator In p.u. (100 MVA Base) | Zero sequence reactance value of the generator grounding impedance is required. The value must be specified on a 100 MVA base. |  | R | R
Turbine Details | X |  |  |  | p.u. | Instantaneous Controlled Fault Current Magnitude (Multiple of full Load current) for Turbine Types 3 & 4 | Wind turbine instantaneous fault current magnitude for Type 4 and Type 3, if the controls operate (no crowbar operation) as a percent of full Load current, expressed in per unit. |  |  | C
Turbine Details | X |  |  |  | p.u. | Controlled Fault Current Magnitude At 2 to 3 cycles after fault (Multiple of full Load current) for Turbine Types 3 & 4 | Wind turbine fault current magnitude at 2 – 3 cycles after a fault for Type 4 and Type 3, if the controls operate (no crowbar operation) as a percent of full Load current, expressed in per unit. |  |  | C
Turbine Details | X |  |  |  | p.u. | Controlled Fault Current Magnitude At 4 plus cycles after fault (Multiple of full Load current) for Turbine Types 3 & 4 | Wind turbine fault current magnitude at 4+ cycles after a fault for Type 4 and Type 3, if the controls operate (no crowbar operation) as a percent of full Load current, expressed in per unit. |  |  | C
Turbine Details | X |  |  |  | kV | High Side Voltage Level (nominal) | Enter the voltage level (in kV) on the high-voltage side of the wind generator pad-mount transformer. |  |  | R
Turbine Details | X |  |  |  | kV | Low Side Voltage Level (nominal) | Enter the voltage level (in kV) on the low-voltage side of the wind generator pad-mount transformer. |  |  | R
Turbine Details | X |  |  |  | List | High Side Voltage Connection | Identify the type of connection used for the windings (Wye/Delta and Neutral Grounding) on the high-voltage side of the transformer. |  |  | R
Turbine Details | X |  |  |  | List | Low Side Voltage Connection | Identify the type of connection used for the windings (Wye/Delta and Neutral Grounding) on the low-voltage side of the transformer. |  |  | R
Turbine Details | X |  |  |  | p.u. | Impedance Z | Enter the impedance of the transformer. |  |  | R
Turbine Details | X |  |  |  |  | X/R Ratio | Enter the ratio of the reactance to the resistance of the transformer. |  |  | R
Turbine Details | X |  |  |  | p.u. | Zero Sequence Z | Enter the zero sequence impedance of the transformer. |  |  | R
Turbine Details | X |  |  |  |  | Zero Sequence X/R Ratio | Enter the ratio of the zero sequence reactance to the zero sequence resistance of the transformer. |  |  | R
Turbine Details | X |  |  |  | MVA | Base MVA for Transformer Data | Enter the base MVA upon which the per unit transformer data is provided. |  |  | R
Ownership
Ownership | X | X |  |  | List | Unit Name | Code for name of generator unit, as provided on the Unit Information Train tab. |  |  | R
Ownership |  |  | X |  | List | Train Name | Code for name of Train, as provided on the Unit Information Train tab. |  |  | R
Ownership | X | X | X |  | Automatic | Resource Name (Unit Code/Mnemonic) | Concatenated mnemonic of Resource Site Code and Unit name (e.g. CBY_CBYG1). |  |  | A
Ownership | X | X |  |  | Y/N | Joint Ownership | Does unit have multiple owners? (does not apply to CC Units, as they must have a single owner for each Train.) |  |  | R
Ownership | X | X | X |  | Text | Resource Entity Name | Enter the name of the Resource Entity who owns all or a portion of this unit. |  |  | C
Ownership | X | X | X |  | Number | Resource Duns Number | Enter the name of the Resource Entity DUNS # who owns all or a portion of this unit (or Train). |  |  | C
Ownership | X | X | X |  | % | Fixed Ownership | Percentage of ownership for this unit that this Resource Entity owns in decimal format. (Does not apply to CC Units, as they must have a single owner for each Train.) |  |  | C
Ownership | X | X | X |  | Y/N | Master Owner | Is this Resource Entity the Master Owner of the unit? (does not apply to CC Units, as they must have a single owner for each Train.) |  |  | R
Ownership | X | X | X |  | Date | Ownership Start Date | Date this Resource Entity ownership was started |  |  | O
Ownership | X | X | X |  | Date | Ownership Stop Date | Date this Resource Entity ownership was stopped |  |  | O
Parameters
Parameters | X | X | X |  | List | Unit Name | Code for name of generator unit, as provided on the Unit Information tab. |  |  | R
Parameters | X | X | X |  | Automatic | Resource Name (Unit Code/Mnemonic) | Concatenated mnemonic of Resource Site Code and Unit name (e.g. CBY_CBYG1). |  |  | A
Parameters | X | X | X |  | MW | High Reasonability Limit | An "Out-of-Bounds" value chosen by RE and used by ERCOT to alarm/reject data exceeding this value. Per Protocol 3.7.1, Resource Parameter Criteria, also used to validate reactive capability curves |  |  | R
Parameters | X | X | X |  | MW | Low Reasonability Limit | An "Out-of-Bounds" value chosen by Resource Entity and used by ERCOT to alarm/reject data below this value. Per Protocol Section 3.7.1, also used to validate reactive capability curves. |  |  | R
Parameters | X | X | X |  | MW/min | High Reasonability Ramp Rate Limit | An "Out-of-Bounds" value chosen by Resource Entity and used by ERCOT to alarm/reject data exceeding this value, SCED is also bounded by this value. |  |  | R
Parameters | X | X | X |  | MW/min | Low Reasonability Ramp Rate Limit | An "Out-of-Bounds" value chosen by Resource Entity and used by ERCOT to alarm/reject data below this value, SCED is also bounded by this value. |  |  | R
Parameters | X | X | X |  | MW | Seasonal Net Max Sustainable Rating - Spring | Spring months are March, April, and May. These are not the HSL/LSL or HEL/LEL values that are submitted in the COP. |  |  | R
Parameters | X | X | X |  | MW | Seasonal Net Min Sustainable Rating - Spring | Spring months are March, April, and May. These are not the HSL/LSL or HEL/LEL values that are submitted in the COP. |  |  | R
Parameters | X | X | X |  | MW | Seasonal Net Max Emergency Rating - Spring | Spring months are March, April, and May. These are not the HSL/LSL or HEL/LEL values that are submitted in the COP. |  |  | R
Parameters | X | X | X |  | MW | Seasonal Net Min Emergency Rating - Spring | Spring months are March, April, and May. These are not the HSL/LSL or HEL/LEL values that are submitted in the COP. |  |  | R
Parameters | X | X | X |  | MW | Seasonal Net Max Sustainable Rating - Summer | Summer months are June, July, and August. These are not the HSL/LSL or HEL/LEL values that are submitted in the COP. |  |  | R
Parameters | X | X | X |  | MW | Seasonal Net Min Sustainable Rating - Summer | Summer months are June, July, and August. These are not the HSL/LSL or HEL/LEL values that are submitted in the COP. |  |  | R
Parameters | X | X | X |  | MW | Seasonal Net Max Emergency Rating - Summer | Summer months are June, July, and August. These are not the HSL/LSL or HEL/LEL values that are submitted in the COP. |  |  | R
Parameters | X | X | X |  | MW | Seasonal Net Min Emergency Rating - Summer | Summer months are June, July, and August. These are not the HSL/LSL or HEL/LEL values that are submitted in the COP. |  |  | R
Parameters | X | X | X |  | MW | Seasonal Net Max Sustainable Rating - Fall | Fall months are September, October, and November. These are not the HSL/LSL or HEL/LEL values that are submitted in the COP. |  |  | R
Parameters | X | X | X |  | MW | Seasonal Net Min Sustainable Rating - Fall | Fall months are September, October, and November. These are not the HSL/LSL or HEL/LEL values that are submitted in the COP. |  |  | R
Parameters | X | X | X |  | MW | Seasonal Net Max Emergency Rating - Fall | Fall months are September, October, and November. These are not the HSL/LSL or HEL/LEL values that are submitted in the COP. |  |  | R
Parameters | X | X | X |  | MW | Seasonal Net Min Emergency Rating - Fall | Fall months are September, October, and November. These are not the HSL/LSL or HEL/LEL values that are submitted in the COP. |  |  | R
Parameters | X | X | X |  | MW | Seasonal Net Max Sustainable Rating - Winter | Winter months are December, January, and February. These are not the HSL/LSL or HEL/LEL values that are submitted in the COP. |  |  | R
Parameters | X | X | X |  | MW | Seasonal Net Min Sustainable Rating - Winter | Winter months are December, January, and February. These are not the HSL/LSL or HEL/LEL values that are submitted in the COP. |  |  | R
Parameters | X | X | X |  | MW | Seasonal Net Max Emergency Rating - Winter | Winter months are December, January, and February. These are not the HSL/LSL or HEL/LEL values that are submitted in the COP. |  |  | R
Parameters | X | X | X |  | MW | Seasonal Net Min Emergency Rating - Winter | Winter months are December, January, and February. These are not the HSL/LSL or HEL/LEL values that are submitted in the COP. |  |  | R
Parameters | X | X | X |  | MW | 0°f - 120°f | Unit De-rating MW values for different temperatures. Each temperature value is a separate field. |  |  | R
Parameters | X | X | X |  | MW | 0°f - 120°f | Unit De-rating MW values for different temperatures. Each temperature value is a separate field. |  |  | R | Delete the field above, upon system implementation of RRGRR003
Operational Parameters
Operational Parameters | X | X | X |  | List | Unit Name | Code for name of generator unit, as provided on the Unit Information tab. |  |  | R
Operational Parameters | X | X | X |  | Automatic | Resource Name (Unit Code/Mnemonic) | Concatenated mnemonic of Resource Site Code and Unit name (e.g. CBY_CBYG1). |  |  | A
Operational Parameters | X | X | X |  | hours | Minimum On Line Time | The minimum number of consecutive hours the Resource must be On-Line before being shut down. For Combined Cycle Generation Resources, this value applies to the configuration, and not the subcomponent (e.g. GT, steamer) |  |  | R
Operational Parameters | X | X | X |  | hours | Minimum Off Line Time | The minimum number of consecutive hours the Resource must be Off-Line before being restarted. |  |  | R
Operational Parameters | X | X | X |  | hours | Hot Start Time | The time, in hours, from the ERCOT startup notice to LSL, for a Resource in its hot-temperature state. New nodal value from Protocol Section 3.7.1 Criteria Hot, Cold, Intermediate start times are not additive. |  |  | R
Operational Parameters | X | X | X |  | hours | Intermediate Start Time | The time interval, in hours, from the ERCOT startup notice to LSL, for a Resource in its intermediate temperature state. New nodal value from Protocol Section 3.7.1. Hot, Cold, Intermediate start times are not additive. |  |  | R
Operational Parameters | X | X | X |  | hours | Cold Start Time | The time interval, in hours, from the ERCOT startup notice to LSL, for a Resource in its cold-temperature state. New nodal value from Protocol Section 3.7.1. Hot, Cold, Intermediate start times are not additive. |  |  | R
Operational Parameters | X | X | X |  |  | Max Weekly Starts | The maximum number of times a Resource can be started in seven consecutive days under normal operating conditions. New nodal value from Protocols Section 3.7. For Combined Cycle Generation Resources, this value applies to the configuration, and not the subcomponent (e.g. GT, steamer) |  |  | R
Operational Parameters | X | X | X |  | hours | Max On Line Time | The maximum number of consecutive hours a Resource can run before it needs to be shut down. New nodal value from Protocol Section 3.7.1. For Combined Cycle Generation Resources, this value applies to the configuration, and not the subcomponent (e.g. GT, steamer) |  |  | R
Operational Parameters | X | X | X |  |  | Max Daily Starts | The maximum number of times a Resource can be started in a 24 hour period under normal operating conditions. New nodal value from Protocol Section 3.7.1. For Combined Cycle Generation Resources, this value applies to the configuration, and not the subcomponent (e.g. GT, steamer) |  |  | R
Operational Parameters | X | X | X |  | MWh | Max Weekly Energy | The maximum amount of energy, in MWh, a Resource can produce in seven consecutive days. |  |  | R
Operational Parameters | X | X | X |  | hours | Hot-to-Intermediate Time | The time, in hours, after shutdown that a hot-temperature-state Resource takes to cool down to intermediate-temperature state. |  |  | R
Operational Parameters | X | X | X |  | hours | Intermediate-to-Cold Time | The time, in hours, after shutdown that an intermediate-temperature-state Resource takes to cool down to cold-temperature state. |  |  | R
Operational Parameters |  | X |  |  | MW | MW1 | Net MW value where the steam generator typically reaches rated pressure (required value for steam turbines). |  |  | C
Operational Parameters |  | X |  |  | PSI | PSI1 | Rated throttle pressure (required value for steam turbines) at MW1 |  |  | C
Operational Parameters |  | X |  |  | MW | MW2 | Net unit output (breakpoint value used to define the pressure/MW curve). If pressure is constant for the normal operating range enter the same value as is entered for MW1. |  |  | C
Operational Parameters |  | X |  |  | PSI | PSI2 | Throttle steam pressure (psi) at MW2 value (breakpoint value used to define the pressure/MW curve). If pressure is constant for the normal operating range enter the same value as is entered for PSI1. |  |  | C
Operational Parameters |  | X |  |  | MW | MW3 | Net unit output (breakpoint value used to define the pressure/MW curve). If pressure is constant for the normal operating range, or is not needed, enter the same value as is entered for MW2. |  |  | C
Operational Parameters |  | X |  |  | PSI | PSI3 | Throttle steam pressure (psi) at MW3 value (breakpoint value used to define the pressure/MW curve). If pressure is constant for the normal operating range, or is not needed, enter the same value as is entered for PSI2. |  |  | C
Operational Parameters |  | X |  |  | MW | MW4 | Net unit output (breakpoint value used to define the pressure/MW curve). If pressure is constant for the normal operating range, or is not needed, enter the same value as is entered for MW3. |  |  | C
Operational Parameters |  | X |  |  | PSI | PSI4 | Throttle steam pressure (psi) at MW4 value (breakpoint value used to define the pressure/MW curve). If pressure is constant for the normal operating range, or point is not needed, enter the same value as is entered for PSI3. |  |  | C
Operational Parameters |  | X |  |  | MW | MW5 | Net unit output (breakpoint value used to define the pressure/MW curve). If pressure is constant for the normal operating range, or point is not needed, enter the same value as is entered for MW4. |  |  | C
Operational Parameters |  | X |  |  | PSI | PSI5 | Throttle steam pressure (psi) at MW5 value (breakpoint value used to define the pressure/MW curve). If pressure is constant for the normal operating range, or point is not needed, enter the same value as is entered for PSI4. |  |  | C
Operational Parameters |  | X |  |  | MW | MW6 | Net unit MW output where the steam generator typically reaches minimum pressure (required value for steam turbines). |  |  | C
Operational Parameters |  | X |  |  | PSI | PSI6 | Throttle steam pressure (psi) at MW6 value (required value for steam turbines). |  |  | C
Operational Parameters |  | X |  |  |  | Limiting K Factor | The K factor is used to model the stored energy available to the resource. The value ranges between 0.0 and 0.6 psig per MW change. Additional information on determining the K factor can be found in Attachment 2, Primary Frequency Response Reference Document, of NERC Reliability Standard, of BAL-001-TRE-1, Primary Frequency Response in the ERCOT Region. The default value would be zero (required for steam turbines). |  |  | C
Operational Parameters - NRRC (Normal Ramp Rate Curve)
Operational Parameters - NRRC | X | X | X |  | List | Unit Name | Code for name of generator unit, as provided on the Unit Information tab. |  |  | R
Operational Parameters - NRRC | X | X | X |  | Automatic | Resource Name (Unit Code/Mnemonic) | Concatenated mnemonic of Resource Site Code and Unit name (e.g. CBY_CBYG1). |  |  | A
Operational Parameters - NRRC | X | X | X |  | List | MW Number | Select MW1- MW10 from list |  |  | R
Operational Parameters - NRRC | X | X | X |  | Automatic | NRRC Code | Concatenated code of the Unit Code, MW Number and the Ramp Rate type |  |  | A
Operational Parameters - NRRC | X | X | X |  | MW | NRRC MW | Normal Ramp Rate curve as defined by the Protocols spans from Low Sustainable Limit (LSL) to High Sustainable Limit (HSL). As LSL/HSL are subject to change, it is recommended to establish this curve from the Low Reasonability Limit (LRL) to the High Reasonability Limit (HRL)for registration purposes. The curve is reflected in ERCOT systems as steps. The curve is not interpolated between points. |  |  | R
Operational Parameters - NRRC | X | X | X |  | MW/min | Normal Upward RampRate1 | Enter Normal Ramp Rate for each NRRC MW value. This is the rate at which the Resource can increase MW output in MW/minute for the given output level. |  |  | R
Operational Parameters - NRRC | X | X | X |  | MW/min | Normal Downward RampRate1 | Enter Normal Ramp Rate for each NRRC MW value. This is the rate at which the Resource can decrease MW output in MW/minute for the given output level. |  |  | R
Operational Parameters - ERRC (Emergency Ramp Rate Curve)
Operational Parameters - ERRC | X | X | X |  | List | Unit Name | Code for name of generator unit, as provided on the Unit Information tab. |  |  | R
Operational Parameters - ERRC | X | X | X |  | Automatic | Resource Name (Unit Code/Mnemonic) | Concatenated mnemonic of Resource Site Code and Unit name (e.g. CBY_CBYG1). |  |  | A
Operational Parameters - ERRC | X | X | X |  | List | MW Number | Select MW1- MW10 from list. |  |  | R
Operational Parameters - ERRC | X | X | X |  | Automatic | ERRC Code | Concatenated code of the Unit Code, MW Number and the Ramp Rate type |  |  | A
Operational Parameters - ERRC | X | X | X |  | MW | ERRC MW | Eemrgency Ramp Rate curve as defined by the Protocols spans from Low Sustainable Limit LSL to High Sustainable Limit HSL. As LSL/HSL are subject to change, it is recommended to establish this curve from the Low Reasonability Limit LRLto the High Reasonability Limit HRL for registration purposes. The curve is reflected in ERCOT systems as steps. The curve is not interpolated between points. |  |  | R
Operational Parameters - ERRC | X | X | X |  | MW/min | Upward RampRate1 | Enter Emergency Ramp Rate for each ERRC MW value. This is the rate at which the Resource can increase MW output in MW/minute for the given output level. |  |  | R
Operational Parameters - ERRC | X | X | X |  | MW/min | Downward RampRate1 | Enter Emergency Ramp Rate for each ERRC MW value. This is the rate at which the Resource can decrease MW output in MW/minute for the given output level. |  |  | R
CC Configurations
CC Configurations |  |  | X |  | List | Train Code | Train Code as provided on the Unit Information Train tab. |  |  | R
CC Configurations |  |  | X |  | Automatic | Site Code | Site Code as provided on the General and Site Information tab. |  |  | A
CC Configurations |  |  | X |  | List | Resource Name (Unit Code/Mnemonic) | Concatenated mnemonic of Resource Site Code and Unit name as provided on the Unit Info tab. |  |  | R
CC Configurations |  |  | X |  | Number | Configuration # | Number of this configuration,. The onfiguration numbers should increase based on increasing capability, not necessarily by increasing number of components. |  |  | R
CC Configurations |  |  | X |  | Automatic | Configuration Code | Concatenated code of the Train Code and the Configuration Number |  |  | A
CC Configurations |  |  | X |  | List | Configuration Type | Register all operationally unique configurations. Additional background to assist with this step can be obtained from the Combined Cycle Whitepaper. |  |  | R
CC Transitions
CC Configurations |  |  | X |  | List | Site Code | Site Code as provided on the General and Site Information tab. |  |  | R
CC Configurations |  |  | X |  | List | Train Code | A sitecode and train code concatenation |  |  | R
CC Configurations |  |  | X |  | List | Configuration Code From | Additional background to assist with this step can be obtained from the Combined Cycle Whitepaper |  |  | C
CC Configurations |  |  | X |  | List | Configuration Code To | Additional background to assist with this step can be obtained from the Combined Cycle Whitepaper |  |  | C
Private Network - Unit
Private Network - Unit | X | X | X |  | List | Unit Name | Unit Code as provided on the Unit Info tab. | R | R | R
Private Network - Unit | X | X | X |  | Automatic | Site Code | Site Code as provided on the General and Site Information tab. |  |  | A
Private Network - Unit | X | X | X |  | Automatic | Resource Name (Unit Code/Mnemonic) | Resource name as provided on the General and Site Information tab. |  |  | A
Private Network - Unit | X | X | X |  | MW | Average Amount of Self-Serve private Load | Amount of the total site generation MW output used for self serve and not available for the grid. | C | C | C
Private Network - Unit | X | X | X |  | MVAr | Average Amount of Self-Serve private reactive Load | Amount of the total site generation MVAr output used for self serve and not available for the grid. | C | C | C
Private Network - Unit | X | X | X |  | MW | Expected Typical Private Network Net Interchange | MW Net Interchange with ERCOT grid (typical Net=Gen-Load) | C | C | C
Private Network - Unit | X | X | X |  | MVAr | Expected Typical Private Network Net Reactive Interchange | MVAr Net Interchange with ERCOT grid (typical Net=Gen-Load) | C | C | C
Private Network - Unit | X | X | X |  | MW | Private Network Gross Unit Capability | MW Gross Generation Capability for the Site | C | C | C
Private Network - Unit | X | X | X |  | MVAr | Private Network Gross Unit Reactive Capability | MVAr Gross Generation Capability for the Site | C | C | C
Private Network - Unit | X | X | X |  | Y/N | If Unit trips, does Load trip? | This is necessary to determine how much Load will appear on the ERCOT grid if the unit trips. |  |  | C
Private Network - Unit | X | X | X |  | % | If yes, approximate percentage of Load that will trip? | If unit trips what percentage of Load associated with this unit is tripped? Enter % (ex. 70% is entered as 70.0) |  |  | C
Reactive Capability
Reactive Capability | X | X | X |  | List | Unit Name | Unit Code as provided on the Unit Info tab. | R | R | R
Reactive Capability | X | X | X |  | Automatic | Resource Name (Unit Code/Mnemonic) | Concatenated mnemonic of Resource Site Code and Unit name (e.g. CBY_CBYG1). |  |  | A
Reactive Capability | X | X | X |  | List | Reactive Capability Provided is Gross/Net Values? | Select whether the Reactive data is based on Gross or Net values. | R | R | R
Reactive Capability | X | X | X |  | List | Reactive Capability Data Provided is from NDCRC Test Data | Indicate (Y/N) if the reactive capability data is from test data |  |  | R
Reactive Capability | X | X | X |  | Date | Reactive Test Date | Include the Reactive Test Date, if the Reactive Capability Data Provided is from NDCRC test data |  |  | R
Reactive Capability | X | X | X |  | MW | MW1 | Reactive Capability curve - point on curve of MW output for this unit, MW1. This should equal the Resource LRL. |  | R | R
Reactive Capability | X | X | X |  | MVAr | Lagging MVAr limit associated with MW1 output | Unit's Lagging Reactive Power output capability associated with its MW1 output, in MVAr. |  | R | R
Reactive Capability | X | X | X |  | MVAr | Leading MVAr limit associated with MW1 output | Unit's Leading Reactive Power output capability associated with its MW1 output, in MVAr; input as negative number |  | R | R
Reactive Capability | X | X | X |  | MW | MW2 | Reactive Capability curve - point on curve of MW output for this unit, MW2 |  | R | R
Reactive Capability | X | X | X |  | MVAr | Lagging MVAr limit associated with MW2 output | Unit's Lagging Reactive Power output capability associated with its MW2 output, in MVAr. |  | R | R
Reactive Capability | X | X | X |  | MVAr | Leading MVAr limit associated with MW2 output | Unit's Leading Reactive Power output capability associated with its MW2 output, in MVAr; input as negative number |  | R | R
Reactive Capability | X | X | X |  | MW | MW3 | Reactive Capability curve - point on curve of MW output for this unit, MW3 |  | R | R
Reactive Capability | X | X | X |  | MVAr | Lagging MVAr limit associated with MW3 output | Unit's Lagging Reactive Power output capability associated with its MW3 output, in MVAr. |  | R | R
Reactive Capability | X | X | X |  | MVAr | Leading MVAr limit associated with MW3 output | Unit's Leading Reactive Power output capability associated with its MW3 output, in MVAr; input as negative number |  | R | R
Reactive Capability | X | X | X |  | MW | MW4 | Reactive Capability curve - point on curve of MW output for this unit, MW4. This should equal the Resource High Reasonability Limit. |  | R | R
Reactive Capability | X | X | X |  | MVAr | Lagging MVAr limit associated with MW4 output | Unit's Lagging Reactive Power output capability associated with its MW4 output, in MVAr. |  | R | R
Reactive Capability | X | X | X |  | MVAr | Leading MVAr limit associated with MW4 output | Unit's Leading Reactive Power output capability associated with its MW4 output, in MVAr; input as negative number |  | R | R
Reactive Capability |  | X | X |  | MW | MW5 - Unity Power Factor | From the Reactive Capability curve - the MW output at Unity power factor (zero MVAr) |  | R | R
Reactive Capability |  | X | X |  | PSI | If hydrogen cooled, indicate hydrogen pressure (psi) associated with your Reactive Curve submitted for ERCOT studies | From manufacturer Reactive Capability Curve or data sheet. |  |  | C
Reactive Capability | X | X | X |  | MVAr | Maximum Leading Operating Capability (MVAr) | Enter the maximum lagging MVArs that can be produced. Input as negative number | R | R | R
Reactive Capability | X | X | X |  | MVAr | Maximum Lagging Operating Capability (MVAr) | Enter the maximum leading MVArs that can be produced. Input as positive number | R | R | R
Reactive Capability | X | X | X |  | Y/N | Manufacturer's Capability Curve submitted? | Has the most recent curve been submitted to ERCOT? If not, please attach. |  | R | R
Planning
Planning |  | X | X |  | List | Unit Name | Unit Code as provided on the Unit Info tab. |  | R | R
Planning | X | X | X |  | Automatic | Resource Name (Unit Code/Mnemonic) | Concatenated mnemonic of Resource Site Code and Unit name (e.g. CBY_CBYG1). |  |  | A
Planning |  | X | X |  | MVA | What is the MVA base that the following data is based on? | The MVA Base for stated impedances. |  | R | R
Planning |  | X | X |  | KV | What is the kV base that the following data is based on? | The KV Base for stated impedances. |  | R | R
Planning |  | X | X |  | p.u. | Direct Axis Subtransient reactance, X"di (unsaturated) | Enter the direct axis subtransient reactance (unsaturated) for the fault. |  | R | R
Planning |  | X | X |  | p.u. | Direct Axis Transient reactance, X'di (unsaturated) | Enter the direct axis transient reactance (unsaturated) for the first 2-3 cycles of the fault. |  | R | R
Planning |  | X | X |  | R in p.u. | Positive Sequence Z (unsaturated) | Enter the positive sequence resistance (unsaturated) for system models. |  | R | R
Planning |  | X | X |  | X in p.u. | Positive Sequence Z (unsaturated) | Enter the positive sequence reactance (unsaturated) for system models. |  | R | R
Planning |  | X | X |  | R in p.u. | Negative Sequence Z (unsaturated) | Enter the negative sequence resistance (unsaturated) for system models. |  | R | R
Planning |  | X | X |  | X in p.u. | Negative Sequence Z (unsaturated) | Enter the negative sequence reactance (unsaturated) for system models. |  | R | R
Planning |  | X | X |  | Y/N | Does Zero Sequence Z exist? | Select whether the generator has Zero Sequence Z data. If no, then the zero sequence data fields will not be required. |  | R | R
Planning |  | X | X |  | R in p.u. | Zero Sequence Z (unsaturated) | Enter the zero sequence resistance (unsaturated) for system models. |  | R | R
Planning |  | X | X |  | X in p.u. | Zero Sequence Z (unsaturated) | Enter the zero sequence reactance (unsaturated) for system models. |  | R | R
Planning |  | X | X |  | p.u. | Direct Axis Subtransient reactance, X"di (saturated) | Enter the direct axis subtransient reactance (saturated) for the fault. |  | R | R
Planning |  | X | X |  | p.u. | Direct Axis Transient reactance, X"di (saturated) | Enter the direct axis transient reactance (saturated) for the first 2-3 cycles of the fault. |  | R | R
Planning |  | X | X |  | R in p.u. | Positive Sequence Z (saturated) | Enter the positive sequence resistance (saturated) for system models. |  | R | R
Planning |  | X | X |  | X in p.u. | Positive Sequence Z (saturated) | Enter the positive sequence reactance (saturated) for system models. |  | R | R
Planning |  | X | X |  | R in p.u. | Negative Sequence Z (saturated) | Enter the negative sequence resistance (saturated) for system models. |  | R | R
Planning |  | X | X |  | X in p.u. | Negative Sequence Z (saturated) | Enter the negative sequence reactance (saturated) for system models. |  | R | R
Planning |  | X | X |  | R in p.u. | Zero Sequence Z (saturated) | Enter the zero sequence resistance (saturated) for system models. |  | R | R
Planning |  | X | X |  | X in p.u. | Zero Sequence Z (saturated) | Enter the zero sequence reactance (saturated) for system models. |  | R | R
Planning |  | X | X |  | p.u. | Zero Sequence Grounding Resistance For An Impedance Grounded Generator in p.u. (100 MVA Base) | Zero Sequence Grounding Resistance value of the Generator Grounding Inpedance is required. The value must be specified on a 100 MVA base. |  | R | R
Planning |  | X | X |  | p.u. | Zero Sequence Grounding Reactance For An Impedance Grounded Generator in p.u. (100 MVA Base) | Zero Sequence Grounding Reactance value of the Generator Grounding Inpedance is required. The value must be specified on a 100 MVA base. |  | R | R
Planning | X | X | X |  | MW | Average Amount of Auxiliary Real Power | Enter average MW for auxiliary Load | R | R | R
Planning | X | X | X |  | MVAr | Average Amount of Auxiliary Reactive Power | Enter average MVAr for auxiliary Load | C | C | C
Planning | X | X | X |  |  | Auxiliary Load Power Factor | Enter power factor for auxiliary Load | C | C | C
Planning | X | X | X |  | % | Large Motor, percent of total MW Load | Enter % of total MW Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  | C
Planning | X | X | X |  | % | Small Motor, percent of total MW Load | Enter % of total MW Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  | C
Planning | X | X | X |  | % | Resistive (Heating) Load, percent of total MW Load | Enter % of total MW Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  | C
Planning | X | X | X |  | % | Discharge Lighting, percent of total MW Load | Enter % of total MW Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  | C
Planning | X | X | X |  | % | Other, percent of total MW Load | Enter % of total MW Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  | C
Planning | X | X | X |  | % | Large Motor, percent of total MVAr Load | Enter % of total MVAr Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  | C
Planning | X | X | X |  | % | Small Motor, percent of total MVAr Load | Enter % of total MVAr Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  | C
Planning | X | X | X |  | % | Discharge Lighting, percent of total MVAr Load | Enter % of total MVAr Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  | C
Planning | X | X | X |  | % | Other, percent of total MVAr Load | Enter % of total MVAr Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  | C
Protection
Protection | X | X | X |  | List | Unit Name | Unit Code as provided on the Unit Info tab. |  | R | R
Protection | X | X | X |  | Automatic | Resource Name (Unit Code/Mnemonic) | Concatenated mnemonic of Resource Site Code and Unit name (e.g. CBY_CBYG1). |  |  | A
Protection | X | X | X |  | cycles | Breaker Interruption Time | Time taken (in cycles) between the breaker receiving the trip signal, and the breaker contacts opening to interrupt the flow of current. |  | R | R
Protection | X | X | X |  | p.u. | Instantaneous Undervoltage Trip | The per unit value (below nominal) of the undervoltage relay instantaneous set point. |  | O | O
Protection | X | X | X |  | p.u. | Undervoltage 1 | Enter the first level undervoltage relay set point in per unit. |  | C | C
Protection | X | X | X |  | sec | Time 1 | Enter the first level undervoltage time delay set point. |  | C | C
Protection | X | X | X |  | p.u. | Undervoltage 2 | Enter the second level undervoltage relay set point in per unit. |  | C | C
Protection | X | X | X |  | sec | Time 2 | Enter the second level undervoltage time delay set point. |  | C | C
Protection | X | X | X |  | p.u. | Undervoltage 3 | Enter the third level undervoltage relay set point in per unit. |  | C | C
Protection | X | X | X |  | sec | Time 3 | Enter the third level undervoltage time delay set point. |  | C | C
Protection | X | X | X |  | p.u. | Undervoltage 4 | Enter the fourth level undervoltage relay set point in per unit. |  | C | C
Protection | X | X | X |  | sec | Time 4 | Enter the fourth level undervoltage time delay set point. |  | C | C
Protection | X | X | X |  | p.u. | Instantaneous Overvoltage Trip | The per unit value (above nominal) of the overvoltage relay instantaneous set point. |  | O | O
Protection | X | X | X |  | p.u. | Overvoltage 1 | Enter the first level overvoltage relay set point in per unit. |  | C | C
Protection | X | X | X |  | sec | Time 1 | Enter the first level overvoltage relay time delay set point. |  | C | C
Protection | X | X | X |  | p.u. | Overvoltage 2 | Enter the second level overvoltage relay set point in per unit. |  | C | C
Protection | X | X | X |  | sec | Time 2 | Enter the second level overvoltage relay time delay set point. |  | C | C
Protection | X | X | X |  | p.u. | Ovrvoltage 3 | Enter the third level overvoltage relay set point in per unit. |  | C | C
Protection | X | X | X |  | sec | Time 3 | Enter the third level overvoltage relay time delay set point. |  | C | C
Protection | X | X | X |  | p.u. | Overvoltage 4 | Enter the fourth level overvoltage relay set point in per unit. |  | C | C
Protection | X | X | X |  | sec | Time 4 | Enter the fourth level overvoltage relay time delay set point. |  | C | C
Protection | X | X | X |  | Hz | Instantaneous Underfrequency Trip | The per unit value (below 60Hz) of the underfrequency relay instantaneous set point. |  | O | O
Protection | X | X | X |  | Hz | Underfrequency 1 | Enter the first level underfrequency relay set point in Hz. |  | C | C
Protection | X | X | X |  | sec | Time 1 | Enter the first level underfrequency relay time delay set point. |  | C | C
Protection | X | X | X |  | Hz | Underfrequency 2 | Enter the second level underfrequency relay set point in Hz. |  | C | C
Protection | X | X | X |  | sec | Time 2 | Enter the second level underfrequency relay time delay set point. |  | C | C
Protection | X | X | X |  | Hz | Underfrequency 3 | Enter the third level underfrequency relay set point in Hz. |  | C | C
Protection | X | X | X |  | sec | Time 3 | Enter the third level underfrequency relay time delay set point. |  | C | C
Protection | X | X | X |  | Hz | Underfrequency 4 | Enter the fourth level underfrequency relay set point in Hz. |  | C | C
Protection | X | X | X |  | sec | Time 4 | Enter the fourth level underfrequency relay time delay set point. |  | C | C
Protection | X | X | X |  | Hz | Instantaneous Overfrequency Trip | The per unit value (above 60Hz) of the overfrequency relay instantaneous set point. |  | O | O
Protection | X | X | X |  | Hz | Overfrequency 1 | Enter the first level overfrequency relay set point in Hz. |  | C | C
Protection | X | X | X |  | sec | Time 1 | Enter the first level overfrequency relay time delay set point. |  | C | C
Protection | X | X | X |  | Hz | Overfrequency 2 | Enter the second level overfrequency relay set point in Hz. |  | C | C
Protection | X | X | X |  | sec | Time 2 | Enter the second level overfrequency relay time delay set point. |  | C | C
Protection | X | X | X |  | Hz | Overfrequency 3 | Enter the third level overfrequency relay set point in Hz. |  | C | C
Protection | X | X | X |  | sec | Time 3 | Enter the third level overfrequency relay time delay set point. |  | C | C
Protection | X | X | X |  | Hz | Overfrequency 4 | Enter the fourth level overfrequency relay set point in Hz. |  | C | C
Protection | X | X | X |  | sec | Time 4 | Enter the fourth level overfrequency relay time delay set point. |  | C | C
Subsynchronous Information (if requested by ERCOT)
Subsync |  | X | X |  | List | Unit Name | Unit Code as provided on the Unit Info tab. |  | R | R
Subsync |  | X | X |  | Automatic | Resource Name (Unit Code/Mnemonic) | Concatenated mnemonic of Resource Site Code and Unit name (e.g. CBY_CBYG1). |  |  | A
Subsync |  | X | X |  | List | Mass Number | Select a unique number for each mass. |  | C | C
Subsync |  | X | X |  | Automatic | Mass Code | Concatenated code automatically provided of the Resource Name and Mass Number |  |  | A
Subsync |  | X | X |  | Automatic | Name | Identification of the masses- HP, IP, LP1, LP2, EXC, etc. |  |  | A
Subsync |  | X | X |  |  | Mass Inertia | H-value. The inertia constant of each mass, either in MW's, MVA, or lbm.ft² |  | C | C
Subsync |  | X | X |  |  | Inertia units | MW's, MVA, or lbm.ft² |  | C | C
Subsync |  | X | X |  |  | Associated damping | The damping associated with each mass either in p.u. torque/p.u. speed deviation, or lbf.ft.sec/rad |  | C | C
Subsync |  | X | X |  |  | Damping units | p.u. torque/p.u. speed or lbf.ft.sec/rad |  | C | C
Subsync |  | X | X |  |  | Stiffness between Masses | The stiffness (spring constant) between each two mass, either in p.u. torque/rad, or lbf.ft/rad (coupling). |  | C | C
Subsync |  | X | X |  |  | Stiffness units | p.u. torque/rad or lbf.ft/rad |  | C | C
Collector System - WIND
Collector System - WIND | X |  |  |  | Automatic | Resource Name (Unit Code/Mnemonic) | Concatenated mnemonic of Resource Site Code and Unit name (e.g. CBY_CBYG1). |  |  | A
Collector System - WIND | X |  |  |  |  | Cable Type | Enter the type(s) of conductor(s) used in the collector system. |  | R | R
Collector System - WIND | X |  |  |  | kV | Voltage Level kV | Enter the voltage level (in kV) of the collector system. Used when calculating Positive and Zero Sequence resistance and reactance. |  | R | R
Collector System - WIND | X |  |  |  | p.u. | Positive Sequence R/kft (p.u. on 100 MVA base) | Enter in per unit, the positive sequence resistance per kilo-foot of the collector system calculated on a 100 MVA base. |  | R | R
Collector System - WIND | X |  |  |  | p.u. | Positive Sequence X/kft (p.u. on 100 MVA base) | Enter in per unit, the positive sequence reactance per kilo-foot of the collector system calculated on a 100 MVA base. |  | R | R
Collector System - WIND | X |  |  |  | p.u. | Positive Charging Bc/kft (p.u. on 100 MVA base) | Enter in per unit, the positive sequence line charging reactance per kilo-foot of the collector system calculated on a 100 MVA base. |  | R | R
Collector System - WIND | X |  |  |  | p.u. | Zero Sequence R0/kft (p.u. on 100 MVA base) | Enter in per unit, the zero sequence resistance per kilo-foot of the collector system calculated on a 100 MVA base. |  | R | R
Collector System - WIND | X |  |  |  | p.u. | Zero Sequence X0/kft (p.u. on 100 MVA base) | Enter in per unit, the zero sequence reactance per kilo-foot of the collector system calculated on a 100 MVA base. |  | R | R
Collector System - Wind Segment Data
Collector System - Wind Segment Data | X |  |  |  | Automatic | Resource Name (Unit Code/Mnemonic) | Concatenated mnemonic of Resource Site Code and Unit name (e.g. CBY_CBYG1). |  |  | A
Collector System - Wind Segment Data | X |  |  |  | List | Cable Type | Cable Type as provided on the Collector System - Wind tab |  | R | R
Collector System - Wind Segment Data | X |  |  |  | Integer | From | Enter the bus number for the sending end or "from" bus of the cable segment. |  | R | R
Collector System - Wind Segment Data | X |  |  |  | Integer | To | Enter the bus number for the receiving end or "to" bus of the cable segment. |  | R | R
Collector System - Wind Segment Data | X |  |  |  | Integer | Circuit Number | Enter the circuit number for the cable segment. |  | R | R
Collector System - Wind Segment Data | X |  |  |  | kV | Voltage Level | Enter the voltage level of the cable segment in kV. |  | R | R
Collector System - Wind Segment Data | X |  |  |  | kft | Cable Segment Length | Enter the length of the cable segment in kilo-feet. |  | R | R
Collector System - Wind Segment Data | X |  |  |  | Integer | Number of Turbines On Cable Segment | Enter the number of turbines connected to the cable segment. |  | R | R
General Information - Load Resource
General Information - Load Resource |  |  |  | X | List | This submittal is for | Select from drop down list of reason for this submittal - New Resource Entity, Revisions, Additions, Deletions |  |  | R
General Information - Load Resource |  |  |  | X | mm/dd/yyyy | Date Form Completed | Enter date in the format MM/DD/YYYY. |  |  | O
General Information - Load Resource |  |  |  | X |  | Resource Entity Submitting Form | Enter the name of the Resource Entity. This must be the same entity name that filed as a Resource Entity on the Standard Form Agreement. The Protocols require that a Load Acting as a Resource must also complete and submit an Application. |  |  | R
General Information - Load Resource |  |  |  | X | Number | Resource Entity DUNS # | Enter the Market Participant unique identifier as registered with ERCOT for the Resource Entity (DUNS number plus 4 as assigned by ERCOT). |  |  | R
General Information - Load Resource |  |  |  | X | Text | Primary Contact | Enter the Primary Contact person who can address ERCOT questions regarding Resource Registration submittal. Enter the contact's name, title, phone number, email address, and fax number. |  |  | R
General Information - Load Resource |  |  |  | X | Text | Title: | Enter the Title of the Primary Contact |  |  | R
General Information - Load Resource |  |  |  | X |  | Phone Number: | Enter the Phone Number for the Primary Contact |  |  | R
General Information - Load Resource |  |  |  | X |  | E-mail Address: | Enter the E-mail Address for the Primary Contact |  |  | R
General Information - Load Resource |  |  |  | X |  | Fax Number: | Enter the Fax Number for the Primary Contact |  |  | O
General Information - Load Resource |  |  |  | X | Text | Secondary Contact | Enter the Secondary Contact person who can address ERCOT questions regarding Resource Registration submittal. Enter the contact's name, title, phone number, email address, and fax number. |  |  | O
General Information - Load Resource |  |  |  | X | Text | Title: | Enter the Title of the Secondary Contact |  |  | O
General Information - Load Resource |  |  |  | X |  | Phone Number: | Enter the Phone Number for the Secondary Contact |  |  | O
General Information - Load Resource |  |  |  | X |  | E-mail Address: | Enter the E-mail Address for the Secondary Contact |  |  | O
General Information - Load Resource |  |  |  | X |  | Fax Number: | Enter the Fax Number for the Secondary Contact |  |  | O
Load Resource Information
Load Resource Information |  |  |  | X |  | Common Name for Load Resource | Enter the common name of the Load that will be acting as a resource. ( e.g.. South Gulf Refinery, etc.) |  |  | R
Load Resource Information |  |  |  | X |  | Dispatch Asset Code (provided by ERCOT) | Enter the Dispatch Asset Code (this code will be provided by ERCOT) |  |  | R
Load Resource Information |  |  |  | X |  | Physical Street Address for Point of Delivery (POD) | Physical street address |  |  | R
Load Resource Information |  |  |  | X |  | Name of City for Point of Delivery (POD) | Name of city |  |  | R
Load Resource Information |  |  |  | X | Y/N | Is Load Netted From Generation at ERCOT Read Gensite? | Select whether Load is netted from generation |  |  | R
Load Resource Information |  |  |  | X | Y/N | Is Load Behind a NOIE Settlement Meter Point? | Select whether Load is behind a NOIE Settlement Meter |  |  | R
Load Resource Information |  |  |  | X | List | Load Resource Type (CLR/UFR/Interruptible) | Select from drop down list the Load Resource Type - CLR, UFR or Interruptible |  |  | R
Load Resource Information |  |  |  | X | Y/N | If CLR, will CLR be Dynamically Scheduling? | Select only if this Load Resource is a Controllable Load Resource |  |  | C
Load Resource Information |  |  |  | X | Y/N | If CLR, ability to operate as a UFR type Resource? | Select only if this Load Resource is a Controllable Load Resource |  |  | C
Load Resource Information |  |  |  | X | mm/dd/yyyy | Load Resource Effective Date | Enter the date the Load became a Load Resource. |  |  | R
Load Resource Information |  |  |  | X | mm/dd/yyyy | Load Resource Expiration Date | Enter the date the Load ceased being a Load Resource. |  |  | O
Load Resource Information |  |  |  | X | All Caps | Substation Name for POD | Enter the name of the substation that supplies service to the Point of Delivery of the Load Resource. |  |  | R
Load Resource Information |  |  |  | X | All Caps | Substation Code for POD | Enter the TDSP substation code. |  |  | R
Load Resource Information |  |  |  | X |  | Transmission Bus POD (PTI Bus No) | Enter the transmission bus location by bus number or by specifying the transmission line. (Luling to Gonzales 138KV, etc.) |  |  | R
Load Resource Information |  |  |  | X | KV | Transmission Station Voltage | Enter the voltage level of the station. Normally this will be between 2.4 and 138 KV. |  |  | R
Load Resource Information |  |  |  | X | All Caps | Transmission Station Load Name in Network Operations Model | Enter the Load Name as listed in the ERCOT model |  |  | R
Load Resource Information |  |  |  | X | List | Meter Reading Entity (TDSP) | Enter who reads the meter. |  |  | R
Load Resource Information |  |  |  | X | Automatic | Meter Reading Entity Duns Number | Enter the Duns number for the entity above. |  |  | R
Load Resource Information |  |  |  | X |  | ESIID assigned to meter | ESI ID number assigned to the meter |  |  | R
Load Resource Information |  |  |  | X | Y/N | Wholesale Delivery Point? | Enter Y or N, if the point of delivery is a wholesale delivery point. |  |  | R
Load Resource Information |  |  |  | X | List | Load Resource Control Device | Select the type of interrupting device. (Control Technology / Interruptible Switch / Circuit Breaker) |  |  | R
Load Resource Information |  |  |  | X | List | ERCOT Load Zone | Select the ERCOT Load Zone from the drop down list |  |  | R
Load Resource Information |  |  |  | X | MW | Maximum POD Total Load | Maximum MW Load total |  |  | R
Load Resource Information |  |  |  | X | MW | Maximum Interruptible Load MW | Maximum MW Interruptible Load total |  |  | R
Load Resource Information |  |  |  | X | MW | High Reasonability Limit | The High "Out-of-Bounds" value chosen by the Resource Entity and used by ERCOT for validation purposes |  |  | R
Load Resource Information |  |  |  | X | MW | Low Reasonability Limit | The Low "Out-of-Bounds" value chosen by the Resource Entity and used by ERCOT for validation purposes |  |  | R
Load Resource Information |  |  |  | X | MW/min | CLR High Reasonability Ramp Rate Limit | The High "Out-of-Bounds" ramp rate value chosen by the Resource Entity and used by ERCOT for validation purposes. Applies to Controllable Load Resources only |  |  | C
Load Resource Information |  |  |  | X | MW/min | CLR Low Reasonability Ramp Rate Limit | The Low "Out-of-Bounds" ramp rate value chosen by the Resource Entity and used by ERCOT for validation purposes. Applies to Controllable Load Resources only |  |  | C
Load Resource Information |  |  |  | X | Y/N | Private Use Network? | Select whether Load is part of a Private Use Network |  |  | R
Load Resource Parameters
Load Resource Parameters |  |  |  | X | List | Dispatch Asset Code | Select the Dispatch Asset Code as provided from the Load Resources Information tab |  |  | R
Load Resource Parameters |  |  |  | X | hours | Minimum Interruption Time (Non-CLR) | The minimum number of consecutive hours the Resource can be deployed (between breaker open to breaker close). |  |  | C
Load Resource Parameters |  |  |  | X | hours | Minimum Restoration Time (Non-CLR) | The minimum number of consecutive hours the Resource must remain energized (not deployed), from the time the Resource is restored from interruption and available for the next potential interruption. |  |  | C
Load Resource Parameters |  |  |  | X |  | Max WEEKLY Deployments (Non-CLR) | The maximum number of times the Resource can be deployed in seven consecutive days under normal operating conditions; |  |  | C
Load Resource Parameters |  |  |  | X | hours | Max Interruption Time (Non-CLR) | The maximum number of consecutive hours the Resource can remain deployed before it needs to be energized. |  |  | C
Load Resource Parameters |  |  |  | X |  | Max DAILY Deployments (Non-CLR) | The maximum number of times the Resource can be deployed in a day under normal operating conditions. |  |  | C
Load Resource Parameters |  |  |  | X | MWh | Max Weekly Energy (Non-CLR) | The maximum amount of energy, in MWh, a for which the Resource can be deployed in seven consecutive days |  |  | C
Load Resource Parameters |  |  |  | X | minutes | Minimum Notice Time (Non-CLR) | The notice time that the Resource requires before deployment (e.g., instantaneous, 30 minutes, etc.). |  |  | C
Load Resource Parameters |  |  |  | X | hours | Max Deployment Time (CLR) | The maximum amount of time a Controllable Load Resource can be deployed before it must return to normal operating conditions. |  |  | C
Load Resource Parameters |  |  |  | X | MWh | Max Weekly Energy (CLR) | The maximum amount of energy a Controllable Load Resource can be deployed in seven consecutive days. |  |  | C
Load Resource Parameters |  |  |  | X | MW | MW1 (CLR NRRC) | Normal Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate1 (CLR NRRC) | Enter Normal Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate1 (CLR NRRC) | Enter Normal Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW | MW2 (CLR NRRC) | Normal Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate2 (CLR NRRC) | Enter Normal Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate2 (CLR NRRC) | Enter Normal Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW | MW3 (CLR NRRC) | Normal Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate3 (CLR NRRC) | Enter Normal Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate3 (CLR NRRC) | Enter Normal Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW | MW4 (CLR NRRC) | Normal Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate4 (CLR NRRC) | Enter Normal Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate4 (CLR NRRC) | Enter Normal Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW | MW5 (CLR NRRC) | Normal Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate5 (CLR NRRC) | Enter Normal Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate5 (CLR NRRC) | Enter Normal Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW | MW6 (CLR NRRC) | Normal Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate6 (CLR NRRC) | Enter Normal Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate6 (CLR NRRC) | Enter Normal Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW | MW7 (CLR NRRC) | Normal Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate7 (CLR NRRC) | Enter Normal Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate7 (CLR NRRC) | Enter Normal Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW | MW8 (CLR NRRC) | Normal Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate8 (CLR NRRC) | Enter Normal Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate8 (CLR NRRC) | Enter Normal Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW | MW9 (CLR NRRC) | Normal Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate9 (CLR NRRC) | Enter Normal Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate9 (CLR NRRC) | Enter Normal Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW | MW10 (CLR NRRC) | Normal Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate10 (CLR NRRC) | Enter Normal Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate10 (CLR NRRC) | Enter Normal Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW | MW1 (CLR ERRC) | Emergency Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate1 (CLR ERRC) | Enter Emergency Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate1 (CLR ERRC) | Enter Emergency Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW | MW2 (CLR ERRC) | Emergency Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate2 (CLR ERRC) | Enter Emergency Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate2 (CLR ERRC) | Enter Emergency Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW | MW3 (CLR ERRC) | Emergency Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate3 (CLR ERRC) | Enter Emergency Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate3 (CLR ERRC) | Enter Emergency Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW | MW4 (CLR ERRC) | Emergency Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate4 (CLR ERRC) | Enter Emergency Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate4 (CLR ERRC) | Enter Emergency Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW | MW5 (CLR ERRC) | Emergency Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate5 (CLR ERRC) | Enter Emergency Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate5 (CLR ERRC) | Enter Emergency Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW | MW6 (CLR ERRC) | Emergency Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate6 (CLR ERRC) | Enter Emergency Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate6 (CLR ERRC) | Enter Emergency Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW | MW7 (CLR ERRC) | Emergency Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate7 (CLR ERRC) | Enter Emergency Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate7 (CLR ERRC) | Enter Emergency Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW | MW8 (CLR ERRC) | Emergency Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate8 (CLR ERRC) | Enter Emergency Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate8 (CLR ERRC) | Enter Emergency Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW | MW9 (CLR ERRC) | Emergency Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate9 (CLR ERRC) | Enter Emergency Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate9 (CLR ERRC) | Enter Emergency Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW | MW10 (CLR ERRC) | Emergency Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate10 (CLR ERRC) | Enter Emergency Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate10 (CLR ERRC) | Enter Emergency Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
Line Data (as applicable)
Line Data | X | X | X |  | List | Description of Change | Select: description of change from drop down list: Add, Change or Delete |  |  | C
Line Data | X | X | X |  | All Caps | Line Name | Line names as listed in the ERCOT model, which must meet the character limitation of the system. |  |  | R
Line Data | X | X | X |  | kV | Line Voltage Level | Line Voltage Level |  | R | R
Line Data | X | X | X |  | p.u. | Resistance in p.u. (100 MVA Base) | Resistance in p.u. (100 MVA Base) |  | R | R
Line Data | X | X | X |  | p.u. | Reactance in p.u. (100 MVA Base) | Reactance in p.u. (100 MVA Base) |  | R | R
Line Data | X | X | X |  | p.u. | Charging Susceptance in p.y. (100 MVA Base) | Charging Susceptance in p.y. (100 MVA Base) |  | R | R
Line Data | X | X | X |  | p.u. | Zero Sequence Line Resistance in p.u. (100 MVA Base) | Zero Sequence Line Resistance in p.u. (100 MVA Base) |  | R | R
Line Data | X | X | X |  | p.u. | Zero Sequence Line Reactance in p.u. (100 MVA Base) | Zero Sequence Line Reactance in p.u. (100 MVA Base) |  | R | R
Line Data | X | X | X |  | p.u. | Zero Sequence Charging Susceptance in p.y. (100 MVA Base) | Zero Sequence Charging Susceptance in p.y. (100 MVA Base) |  | R | R
Line Data | X | X | X |  | List | Type | Select line type from drop down list: Overhead, Underground or Both |  |  | R
Line Data | X | X | X |  | miles | Segment Length | Length of this line segment |  | R | R
Line Data | X | X | X |  | All Caps | ERCOT TO Station Code Mnemonic | Enter the station code mnemonic of the TO station for this Line |  |  | R
Line Data | X | X | X |  | Y/N | Internal Line? | Is this line internal to the station (i.e. not directly connected to the TDSP)? |  |  | C
Line Data | X | X | X |  | List | TSP Name | Select TSP Name from the drop down list |  |  | C
Line Data | X | X | X |  | All Caps | Connected Device 1 | Enter device connected to this line in the TO station (can provide up to 10) |  |  | R
Line Data | X | X | X |  | All Caps | Connected Device 2 | Enter device connected to this line in the TO station (can provide up to 10) |  |  | C
Line Data | X | X | X |  | All Caps | Connected Device 3 | Enter device connected to this line in the TO station (can provide up to 10) |  |  | C
Line Data | X | X | X |  | All Caps | Connected Device 4 | Enter device connected to this line in the TO station (can provide up to 10) |  |  | C
Line Data | X | X | X |  | All Caps | Connected Device 5 | Enter device connected to this line in the TO station (can provide up to 10) |  |  | C
Line Data | X | X | X |  | All Caps | Connected Device 6 | Enter device connected to this line in the TO station (can provide up to 10) |  |  | C
Line Data | X | X | X |  | All Caps | Connected Device 7 | Enter device connected to this line in the TO station (can provide up to 10) |  |  | C
Line Data | X | X | X |  | All Caps | Connected Device 8 | Enter device connected to this line in the TO station (can provide up to 10) |  |  | C
Line Data | X | X | X |  | All Caps | Connected Device 9 | Enter device connected to this line in the TO station (can provide up to 10) |  |  | C
Line Data | X | X | X |  | All Caps | Connected Device 10 | Enter device connected to this line in the TO station (can provide up to 10) |  |  | C
Line Data | X | X | X |  | Number | Bus Number (PTI Bus Number) | Enter PTI Bus number connecting this line in the TO station |  |  | O
Line Data | X | X | X |  | List | Weather Zone / Weather Station (used for Dynamic Ratings) | Select Weather zone or station from the drop down list |  |  | C
Line Data | X | X | X |  | All Caps | ERCOT FROM Station Code Mnemonic | Enter the station code mnemonic of the FROM station for this Line |  |  | R
Line Data | X | X | X |  | All Caps | Connected Device 1 | Enter device connected to this line in the FROM station (can provide up to 10) |  |  | R
Line Data | X | X | X |  | All Caps | Connected Device 2 | Enter device connected to this line in the FROM station (can provide up to 10) |  |  | C
Line Data | X | X | X |  | All Caps | Connected Device 3 | Enter device connected to this line in the FROM station (can provide up to 10) |  |  | C
Line Data | X | X | X |  | All Caps | Connected Device 4 | Enter device connected to this line in the FROM station (can provide up to 10) |  |  | C
Line Data | X | X | X |  | All Caps | Connected Device 5 | Enter device connected to this line in the FROM station (can provide up to 10) |  |  | C
Line Data | X | X | X |  | All Caps | Connected Device 6 | Enter device connected to this line in the FROM station (can provide up to 10) |  |  | C
Line Data | X | X | X |  | All Caps | Connected Device 7 | Enter device connected to this line in the FROM station (can provide up to 10) |  |  | C
Line Data | X | X | X |  | All Caps | Connected Device 8 | Enter device connected to this line in the FROM station (can provide up to 10) |  |  | C
Line Data | X | X | X |  | All Caps | Connected Device 9 | Enter device connected to this line in the FROM station (can provide up to 10) |  |  | C
Line Data | X | X | X |  | All Caps | Connected Device 10 | Enter device connected to this line in the FROM station (can provide up to 10) |  |  | C
Line Data | X | X | X |  | Number | Bus Number (PTI Bus Number) | Enter PTI Bus number connecting this line in the FROM station |  |  | O
Line Data | X | X | X |  | List | Weather Zone / Weather Station (used for Dynamic Ratings) | Select Weather zone or station from the drop down list |  |  | C
Line Data | X | X | X |  | Automatic | Line Code | Concatenated code automatically provided |  |  | A
Line Data | X | X | X |  |  | Comments | Enter any comments regarding this Line data |  |  | O
Line Data | X | X | X |  | mm/dd/yyyy | Effective Date | Date this line was added, removed or updated in the model |  |  | R
Line Temperature (as applicable)
Line Temperature | X | X | X |  | Automatic | Line Name | Automatically provided based on lines listed in the Line data tab |  |  | A
Line Temperature | X | X | X |  | Automatic | Line Code | Automatically provided based on line codes listed in the Line data tab |  |  | A
Line Temperature | X | X | X |  | List | Line Rating | Select Static or Dynamic line rating |  |  | R
Line Temperature | X | X | X |  | MVA | Continuous Rating | Rating that line can operate at indefinitely without damage, or violation fo NESC clearances. |  | R | R
Line Temperature | X | X | X |  | MVA | 2-hr Emergency Rating | Rating that line can operate at this rating for two hours without violation of NESC clearances or equipment failure |  | R | R
Line Temperature | X | X | X |  | MVA | 15-min Rating | Rating that line can operate at this rating for fifteen minutes without violation of NESC clearances or equipment failure |  | R | R
Line Temperature | X | X | X |  | MVA | Planning Rate C | Represents the two hour MVA rating of the conductor or transformer only,excluding substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature without violation of NESC clearances or equipment failure. |  | R | R
Line Temperature | X | X | X |  | MVA | 20 °F - Continuous Rating - 115 °F Continuous Rating | Rating that line can operate at indefinitely without damage, or violation fo NESC clearances at the stated temperature. |  |  | C
Line Temperature | X | X | X |  | MVA | 20 °F - 2-hr Emergency Rating - 115 °F 2-hr Emergency Rating | Rating that line can operate at this rating for two hours without violation of NESC clearances or equipment failure at the stated temperature. |  |  | C
Line Temperature | X | X | X |  | MVA | 20 °F - 15-min Rating - 115 °F 15-min Rating | Rating that line can operate at this rating for fifteen minutes without violation of NESC clearances or equipment failure at the stated temperature. |  |  | C
Line Temperature | X | X | X |  | MVA | 20 °F - Planning Rate C - 115 °F - Planning Rate C | Represents the two hour MVA rating of the conductor or transformer only,excluding substation terminal equipment in series with a conductor or transformer, at the stated ambient temperature without violation of NESC clearances or equipment failure. |  |  | C
Breaker Switch Data (as applicable)
Breaker Switch Data | X | X | X |  | List | Description of Change | Select: description of change from drop down list: Add, Change or Delete |  |  | C
Breaker Switch Data | X | X | X |  | All Caps | Switch Name | Breaker or Switch name as provided in the ERCOT model, which must meet the character limitation of the system. |  |  | R
Breaker Switch Data | X | X | X |  | All Caps | ERCOT Station Name (Station Code or Station Mnemonic) | ERCOT Station Code Mnemonic that the breaker or switch is located, as listed in the model |  |  | R
Breaker Switch Data | X | X | X |  | Automatic | Switch Code | Concatenated code automatically provided |  |  | A
Breaker Switch Data | X | X | X |  | Y/N | Is This A Fault Islating Device (e.g. Circuit Breaker) | Select Y if device is Breaker, or N if device is a Switch |  | R | R
Breaker Switch Data | X | X | X |  | List | Normal Operating Status (when in service) | Select whether Open or Closed during normal operations |  | R | R
Breaker Switch Data | X | X | X |  | kV | Voltage Level | Enter voltage level of this breaker or switch |  | R | R
Breaker Switch Data | X | X | X |  | MVA | Continuous Rating | Rating that device can operate at indefinitely without damage, or violation fo NESC clearances. |  | R | R
Breaker Switch Data | X | X | X |  | MVA | 2-hr Emergency Rating | Rating that device can operate at this rating for two hours without violation of NESC clearances or equipment failure |  | R | R
Breaker Switch Data | X | X | X |  | MVA | 15-min Rating | Rating that device can operate at this rating for fifteen minutes without violation of NESC clearances or equipment failure |  | R | R
Breaker Switch Data | X | X | X |  | All Caps | Connected Device 1 | Enter device connected to this breaker or switch on Side 1 (can provide up to 10) |  |  | R
Breaker Switch Data | X | X | X |  | All Caps | Connected Device 2 | Enter device connected to this breaker or switch on Side 1 (can provide up to 10) |  |  | C
Breaker Switch Data | X | X | X |  | All Caps | Connected Device 3 | Enter device connected to this breaker or switch on Side 1 (can provide up to 10) |  |  | C
Breaker Switch Data | X | X | X |  | All Caps | Connected Device 4 | Enter device connected to this breaker or switch on Side 1 (can provide up to 10) |  |  | C
Breaker Switch Data | X | X | X |  | All Caps | Connected Device 5 | Enter device connected to this breaker or switch on Side 1 (can provide up to 10) |  |  | C
Breaker Switch Data | X | X | X |  | All Caps | Connected Device 6 | Enter device connected to this breaker or switch on Side 1 (can provide up to 10) |  |  | C
Breaker Switch Data | X | X | X |  | All Caps | Connected Device 7 | Enter device connected to this breaker or switch on Side 1 (can provide up to 10) |  |  | C
Breaker Switch Data | X | X | X |  | All Caps | Connected Device 8 | Enter device connected to this breaker or switch on Side 1 (can provide up to 10) |  |  | C
Breaker Switch Data | X | X | X |  | All Caps | Connected Device 9 | Enter device connected to this breaker or switch on Side 1 (can provide up to 10) |  |  | C
Breaker Switch Data | X | X | X |  | All Caps | Connected Device 10 | Enter device connected to this breaker or switch on Side 1 (can provide up to 10) |  |  | C
Breaker Switch Data | X | X | X |  | All Caps | Connected Device 1 | Enter device connected to this breaker or switch on Side 2 (can provide up to 10) |  |  | R
Breaker Switch Data | X | X | X |  | All Caps | Connected Device 2 | Enter device connected to this breaker or switch on Side 2 (can provide up to 10) |  |  | C
Breaker Switch Data | X | X | X |  | All Caps | Connected Device 3 | Enter device connected to this breaker or switch on Side 2 (can provide up to 10) |  |  | C
Breaker Switch Data | X | X | X |  | All Caps | Connected Device 4 | Enter device connected to this breaker or switch on Side 2 (can provide up to 10) |  |  | C
Breaker Switch Data | X | X | X |  | All Caps | Connected Device 5 | Enter device connected to this breaker or switch on Side 2 (can provide up to 10) |  |  | C
Breaker Switch Data | X | X | X |  | All Caps | Connected Device 6 | Enter device connected to this breaker or switch on Side 2 (can provide up to 10) |  |  | C
Breaker Switch Data | X | X | X |  | All Caps | Connected Device 7 | Enter device connected to this breaker or switch on Side 2 (can provide up to 10) |  |  | C
Breaker Switch Data | X | X | X |  | All Caps | Connected Device 8 | Enter device connected to this breaker or switch on Side 2 (can provide up to 10) |  |  | C
Breaker Switch Data | X | X | X |  | All Caps | Connected Device 9 | Enter device connected to this breaker or switch on Side 2 (can provide up to 10) |  |  | C
Breaker Switch Data | X | X | X |  | All Caps | Connected Device 10 | Enter device connected to this breaker or switch on Side 2 (can provide up to 10) |  |  | C
Breaker Switch Data | X | X | X |  |  | Comments | Enter any comments regarding this breaker-switch data |  |  | O
Breaker Switch Data | X | X | X |  | mm/dd/yyyy | Effective Date | Date this breaker or switch was added, removed or updated in the model |  |  | R
Capacitor and Reactor Data (as applicable)
Capacitor and Reactor Data | X | X | X |  | List | Description of Change | Select: description of change from drop down list: Add, Change or Delete |  |  | C
Capacitor and Reactor Data | X | X | X |  | All Caps | Device Name | Capacitor or Reactor name as provided in the ERCOT model, which must meet the character limitation of the system. |  |  | R
Capacitor and Reactor Data | X | X | X |  | All Caps | ERCOT Station Name (Station Code or Station Mnemonic) | ERCOT Station Code Mnemonic that the breaker or switch is located, as listed in the model |  |  | R
Capacitor and Reactor Data | X | X | X |  | Automatic | Device Code | Concatenated code automatically provided |  |  | A
Capacitor and Reactor Data | X | X | X |  | List | Capacitor or Reactor | Select whether this device is a capacitor or reactor |  | R | R
Capacitor and Reactor Data | X | X | X |  | MVAr | Nominal MVAr | Rated MVAr rating of a capacitor or reactor (name plate data) |  | R | R
Capacitor and Reactor Data | X | X | X |  | kV | Voltage Level kV | Enter voltage level of this capacitor or reactor |  | R | R
Capacitor and Reactor Data | X | X | X |  | Number | Bus Number (PTI Bus Number) | Enter PTI Bus Number for this device |  |  | O
Capacitor and Reactor Data | X | X | X |  | Y/N | Automatic Voltage Regulation | Select Y or N whether this device has automatic voltage regulation |  | R | R
Capacitor and Reactor Data | X | X | X |  | kV | Voltage Level of Busbar being regulated | Enter voltage of busbar where device is located |  | C | C
Capacitor and Reactor Data | X | X | X |  | kV | Desired Regulating Voltage | Desired Regulating Voltage |  | C | C
Capacitor and Reactor Data | X | X | X |  | kV | Minimum Regulating Voltage | Lower limit of voltage specified in the Protocols |  | C | C
Capacitor and Reactor Data | X | X | X |  | kV | Maximum Regulating Voltage | Higher limit of voltage specified in the Protocols |  | C | C
Capacitor and Reactor Data | X | X | X |  | p.u. | Zero Sequence Reactance Increment in p.u. | Zero Sequence Reactance Increment in p.u. |  | R | R
Capacitor and Reactor Data | X | X | X |  | All Caps | Directly Connected Device 1 | Enter device connected to this capacitor or reactor (can provide up to 10) |  |  | R
Capacitor and Reactor Data | X | X | X |  | All Caps | Directly Connected Device 2 | Enter device connected to this capacitor or reactor (can provide up to 10) |  |  | C
Capacitor and Reactor Data | X | X | X |  | All Caps | Directly Connected Device 3 | Enter device connected to this capacitor or reactor (can provide up to 10) |  |  | C
Capacitor and Reactor Data | X | X | X |  | All Caps | Directly Connected Device 4 | Enter device connected to this capacitor or reactor (can provide up to 10) |  |  | C
Capacitor and Reactor Data | X | X | X |  | All Caps | Directly Connected Device 5 | Enter device connected to this capacitor or reactor (can provide up to 10) |  |  | C
Capacitor and Reactor Data | X | X | X |  | All Caps | Directly Connected Device 6 | Enter device connected to this capacitor or reactor (can provide up to 10) |  |  | C
Capacitor and Reactor Data | X | X | X |  | All Caps | Directly Connected Device 7 | Enter device connected to this capacitor or reactor (can provide up to 10) |  |  | C
Capacitor and Reactor Data | X | X | X |  | All Caps | Directly Connected Device 8 | Enter device connected to this capacitor or reactor (can provide up to 10) |  |  | C
Capacitor and Reactor Data | X | X | X |  | All Caps | Directly Connected Device 9 | Enter device connected to this capacitor or reactor (can provide up to 10) |  |  | C
Capacitor and Reactor Data | X | X | X |  | All Caps | Directly Connected Device 10 | Enter device connected to this capacitor or reactor (can provide up to 10) |  |  | C
Capacitor and Reactor Data | X | X | X |  |  | Comments | Enter any comments regarding this breaker-switch data |  |  | C
Capacitor and Reactor Data | X | X | X |  | mm/dd/yyyy | Effective Date | Date this breaker or switch was added, removed or updated in the model |  |  | R
Transformer Data (as applicable)
Transformer Data | X | X | X |  | List | Description of Change | Select: description of change from drop down list: Add, Change or Delete |  |  | C
Transformer Data | X | X | X |  | All Caps | Transformer Name | Transformer name as provided in the ERCOT model, which must meet the character limitation of the system. |  |  | R
Transformer Data | X | X | X |  | All Caps | ERCOT Station Name (Station Code or Station Mnemonic) | ERCOT Station Code Mnemonic that the breaker or switch is located, as listed in the model |  |  | R
Transformer Data | X | X | X |  | Automatic | Transformer Code | Concatenated code automatically provided |  |  | A
Transformer Data | X | X | X |  | Y/N | Transformer Test Report Attached? | Is the Transformer test report attached to this Resource Registration? |  |  | R
Transformer Data | X | X | X |  | Y/N | Is this Transformer in a Master-follower current balancing configuration? | Select Y or N whether this transformer is part of a master - following configuration |  |  | R
Transformer Data | X | X | X |  | Y/N | Generator Step up Transformer? | Select Y or N whether this transformer is a generator step up transformer |  | R | R
Transformer Data | X | X | X |  |  | Zero Sequence Data Winding Connect code (1-9) | Enter zero sequence data winding connect code 1 - 5 as noted below. Transformer Connection Codes: Two Winding Transformers (in order of Voltage highest first) 1 -- Wye-Wye Bank Both Neutrals Grounded 2 -- Wye - Delta Bank Grounded Wye 3 -- Delta - Wye Bank Grounded Wye 4 -- Delta - Delta Bank; Wye-Delta Bank Ungrounded Wye; Delta-Wye Bank Ungrounded Wye; Wye-Wye Bank Either Wye Grounded 5 -- Three Winding only (Test Reports needed for Code 5) 6 through 9 -- Unused |  | R | R
Transformer Data | X | X | X |  | p.u. | Zero Sequence Grounding Resistance For An Impedance Grounded Transformer in p.u. (100 MVA Base) | Zero Sequence Grounding Resistance For An Impedance Grounded Generator in p.u. (100 MVA Base) and the nominal system voltage (69, 138 or 345 kV) |  | R | R
Transformer Data | X | X | X |  | p.u. | Zero Sequence Grounding Reactance For An Impedance Grounded Transformer In P.u. (100 MVA Base) | Zero Sequence Grounding Reactance For An Impedance Grounded Transformer In P.u. (100 MVA Base) and the nominal system voltage (69, 138 or 345 kV) |  | R | R
Transformer Data | X | X | X |  | p.u. | Zero Sequence Resistance In p.u. (100 MVA Base) | Zero Sequence Resistance In p.u. (100 MVA Base) and the nominal system voltage (69, 138 or 345 kV) |  | R | R
Transformer Data | X | X | X |  | p.u. | Zero Sequence Reactance In P.u. (100 MVA Base) | Zero Sequence Reactance In P.u. (100 MVA Base) and the nominal system voltage (69, 138 or 345 kV) |  | R | R
Transformer Data | X | X | X |  | p.u. | Zero Sequence Reactance Increment in p.u. | Zero Sequence Reactance Increment in p.u. |  |  | R
Transformer Data | X | X | X |  | p.u. | Positive Sequence Resistance (100 MVA Base) | Positive Sequence Resistance (100 MVA Base) and the nominal system voltage (69, 138 or 345 kV) |  | R | R
Transformer Data | X | X | X |  | p.u. | Positive Sequence Reactance (100 MVA Base) | Positive Sequence Reactance (100 MVA Base) and the nominal system voltage (69, 138 or 345 kV) |  | R | R
Transformer Data | X | X | X |  | MVA | Continuous Rating | Rating that transformer can operate at indefinitely without damage, or violation fo NESC clearances. |  | R | R
Transformer Data | X | X | X |  | MVA | 2-hr Emergency Rating | Rating that transformer can operate at this rating for two hours without violation of NESC clearances or equipment failure |  | R | R
Transformer Data | X | X | X |  | MVA | 15-min Rating | Rating that transformer can operate at this rating for fifteen minutes without violation of NESC clearances or equipment failure |  | R | R
Transformer Data | X | X | X |  | All Caps | Unit(s) Associated With This Transformer | Enter the Unit(s) Associated With This Transformer (name must match unit names provided on the unit info tab) |  |  | C
Transformer Data | X | X | X |  | All Caps | Unit(s) Associated With This Transformer | Enter the Unit(s) Associated With This Transformer (name must match unit names provided on the unit info tab) |  |  | C
Transformer Data | X | X | X |  | All Caps | Unit(s) Associated With This Transformer | Enter the Unit(s) Associated With This Transformer (name must match unit names provided on the unit info tab) |  |  | C
Transformer Data | X | X | X |  | All Caps | Unit(s) Associated With This Transformer | Enter the Unit(s) Associated With This Transformer (name must match unit names provided on the unit info tab) |  |  | C
Transformer Data | X | X | X |  | All Caps | Unit(s) Associated With This Transformer | Enter the Unit(s) Associated With This Transformer (name must match unit names provided on the unit info tab) |  |  | C
Transformer Data | X | X | X |  | All Caps | Unit(s) Associated With This Transformer | Enter the Unit(s) Associated With This Transformer (name must match unit names provided on the unit info tab) |  |  | C
Transformer Data | X | X | X |  | All Caps | Unit(s) Associated With This Transformer | Enter the Unit(s) Associated With This Transformer (name must match unit names provided on the unit info tab) |  |  | C
Transformer Data | X | X | X |  | All Caps | Unit(s) Associated With This Transformer | Enter the Unit(s) Associated With This Transformer (name must match unit names provided on the unit info tab) |  |  | C
Transformer Data | X | X | X |  | All Caps | Unit(s) Associated With This Transformer | Enter the Unit(s) Associated With This Transformer (name must match unit names provided on the unit info tab) |  |  | C
Transformer Data | X | X | X |  | All Caps | Unit(s) Associated With This Transformer | Enter the Unit(s) Associated With This Transformer (name must match unit names provided on the unit info tab) |  |  | C
Transformer Data | X | X | X |  | All Caps | Unit(s) Associated With This Transformer | Enter the Unit(s) Associated With This Transformer (name must match unit names provided on the unit info tab) |  |  | C
Transformer Data | X | X | X |  | All Caps | Unit(s) Associated With This Transformer | Enter the Unit(s) Associated With This Transformer (name must match unit names provided on the unit info tab) |  |  | C
Transformer Data | X | X | X |  | kV | High Side Voltage level (no-Load) | Enter the voltage level of the high side for this transformer system nominal voltage (69, 138, 345 kV) |  |  | R
Transformer Data | X | X | X |  | Number | High Side Voltage level (PTI) | Enter the PTI bus number for the high side of this transformer |  |  | O
Transformer Data | X | X | X |  | List | High Side Voltage Connection - Wye or Delta | Select whether this high side connection is a Wye or Delta connection |  | R | R
Transformer Data | X | X | X |  | All Caps | High Side Voltage Connected Devices | Enter a device connected to the high side of this transformer |  |  | R
Transformer Data | X | X | X |  | All Caps | High Side Voltage Connected Devices | Enter a device connected to the high side of this transformer |  |  | R
Transformer Data | X | X | X |  | All Caps | High Side Voltage Connected Devices | Enter a device connected to the high side of this transformer |  |  | R
Transformer Data | X | X | X |  | All Caps | High Side Voltage Connected Devices | Enter a device connected to the high side of this transformer |  |  | R
Transformer Data | X | X | X |  | All Caps | High Side Voltage Connected Devices | Enter a device connected to the high side of this transformer |  |  | R
Transformer Data | X | X | X |  | kV | High Side Manufactured Nominal Voltage | Enter the high side system nominal voltage (69, 138, 345 kV) for this transformer |  | R | R
Transformer Data | X | X | X |  | kV | Low Side Voltage level (no-Load) | Enter the voltage level of the low side for this transformer |  |  | R
Transformer Data | X | X | X |  | Number | Low Side Voltage level (PTI) | Enter the PTI bus number for the low side of this transformer |  |  | O
Transformer Data | X | X | X |  | List | Low Side Voltage Connection - Wye or Delta | Select whether this low side connection is a Wye or Delta connection |  | R | R
Transformer Data | X | X | X |  | All Caps | Low Side Voltage Connected Devices | Enter a device connected to the low side of this transformer |  |  | R
Transformer Data | X | X | X |  | All Caps | Low Side Voltage Connected Devices | Enter a device connected to the low side of this transformer |  |  | R
Transformer Data | X | X | X |  | All Caps | Low Side Voltage Connected Devices | Enter a device connected to the low side of this transformer |  |  | R
Transformer Data | X | X | X |  | All Caps | Low Side Voltage Connected Devices | Enter a device connected to the low side of this transformer |  |  | R
Transformer Data | X | X | X |  | All Caps | Low Side Voltage Connected Devices | Enter a device connected to the low side of this transformer |  |  | R
Transformer Data | X | X | X |  | kV | Low Side Manufactured Nominal Voltage | Enter the low side nominal voltage for this transformer |  | R | R
Transformer Data | X | X | X |  | Y/N | Automatic Voltage Regulation | Select Y or N whether this transformer has automatic voltage regulation |  | R | R
Transformer Data | X | X | X |  | Y/N | Does Transformer have a Load Tap Changer? | Select Y or N whether this transformer has Load Tap changer |  | C | C
Transformer Data | X | X | X |  | List | Location of Load Tap Changer - High or Low | If this transformer has Load Tap changer, select whether it is on High or Low side |  | C | C
Transformer Data | X | X | X |  | kV | Base kV of Regulated Side | Base kV of Regulated Side |  |  | C
Transformer Data | X | X | X |  | kV | Target kV of Regulated Side | Target kV of Regulated Side |  |  | C
Transformer Data | X | X | X |  | % | Acceptable Deviation of Target Voltage | Acceptable Deviation of Target Voltage |  |  | C
Transformer Data | X | X | X |  |  | Comments | Enter any comments regarding this transformer data |  |  | O
Transformer Data | X | X | X |  | mm/dd/yyyy | Effective Date | Date this transformer was added, removed or updated in the model |  |  | R
Transformer Tap Settings (as applicable)
Transformer Tap Settings | X | X | X |  | List | Description of Change | Select: description of change from drop down list: Add, Change or Delete |  |  | C
Transformer Tap Settings | X | X | X |  | List | Transformer Name | Transformer name as provided in the ERCOT model, which must meet the character limitation of the system. |  |  | R
Transformer Tap Settings | X | X | X |  | List | ERCOT Station Name (Station Code or Station Mnemonic) | ERCOT Station Code Mnemonic that the breaker or switch is located, as listed in the model |  |  | R
Transformer Tap Settings | X | X | X |  | Automatic | Transformer Code | Concatenated code automatically provided |  |  | A
Transformer Tap Settings | X | X | X |  | List | High-Low Flag | Select from list whether taps are on high side or low side |  | C | C
Transformer Tap Settings | X | X | X |  | Number | Tap Position At Manufactured Nominal Voltage | Tap Position At Manufactured Nominal Voltage |  | C | C
Transformer Tap Settings | X | X | X |  | Number | Total Number of Tap Positions | Total Number of Tap Positions |  | C | C
Transformer Tap Settings | X | X | X |  | Number | Normal Tap Position | Normal Tap Position |  | C | C
Transformer Tap Settings | X | X | X |  | Number | Lowest Tap Position | Lowest Tap Position |  | C | C
Transformer Tap Settings | X | X | X |  | kV | Voltage at Lowest Tap Position | Voltage at Lowest Tap Position |  | C | C
Transformer Tap Settings | X | X | X |  | Number | Highest Tap Position | Highest Tap Position |  | C | C
Transformer Tap Settings | X | X | X |  | kV | Voltage at Highest Tap Position | Voltage at Highest Tap Position |  | C | C
Transformer Tap Settings | X | X | X |  | kV | Size of Each Voltage Level Step | Size of Each Voltage Level Step |  | C | C
Static Var Compensator Data (as applicable)
Static Var Compensator Data | X | X | X |  | List | Description of Change | Select: description of change from drop down list: Add, Change or Delete |  |  | C
Static Var Compensator Data | X | X | X |  | All Caps | SVC Name | Static Var Compensator name as provided in the ERCOT model, which must meet the character limitation of the system. |  |  | R
Static Var Compensator Data | X | X | X |  | All Caps | ERCOT Station Name (Station Code or Station Mnemonic) | ERCOT Station Code Mnemonic that the breaker or switch is located, as listed in the model |  |  | R
Static Var Compensator Data | X | X | X |  | Automatic | SVC Code | Concatenated code automatically provided |  |  | A
Static Var Compensator Data | X | X | X |  | kV | SVC Base Voltage Level | Enter base voltage for this SVC device |  | R | R
Static Var Compensator Data | X | X | X |  | MVAr | Fixed MVAr (var injections at Nominal Voltage) | Enter fixed MVAr for this SVC device at nominal voltage |  | R | R
Static Var Compensator Data | X | X | X |  | p.u. | Minimum Admittance Limits (100 MVA base) | Minimum Admittance Limits (100 MVA base) |  | R | R
Static Var Compensator Data | X | X | X |  | p.u. | Maximum Admittance Limits (100 MVA base) | Maximum Admittance Limits (100 MVA base) |  | R | R
Static Var Compensator Data | X | X | X |  | MVAr | Minimum Steady State Reactive power Limits (100 MVA base) | Minimum Steady State Reactive power Limits (100 MVA base) |  | R | R
Static Var Compensator Data | X | X | X |  | MVAr | Maximum Steady State Reactive power Limits (100 MVA base) | Maximum Steady State Reactive power Limits (100 MVA base) |  | R | R
Static Var Compensator Data | X | X | X |  | MVAr | Minimum Threshold (post contingency) Reactive Power Limits | Minimum Threshold (post contingency) Reactive Power Limits |  | R | R
Static Var Compensator Data | X | X | X |  | MVAr | Maximum Threshold (post contingency) Reactive Power Limits | Maximum Threshold (post contingency) Reactive Power Limits |  | R | R
Static Var Compensator Data | X | X | X |  | kV | Minimum Voltage Threshold | Minimum Voltage Threshold |  | R | R
Static Var Compensator Data | X | X | X |  | kV | Maximum Voltage Threshold | Maximum Voltage Threshold |  | R | R
Static Var Compensator Data | X | X | X |  | All Caps | Directly Connected Device 1 | Enter device connected to this SVC (can provide up to 10) |  |  | R
Static Var Compensator Data | X | X | X |  | All Caps | Directly Connected Device 2 | Enter device connected to this SVC (can provide up to 10) |  |  | C
Static Var Compensator Data | X | X | X |  | All Caps | Directly Connected Device 3 | Enter device connected to this SVC (can provide up to 10) |  |  | C
Static Var Compensator Data | X | X | X |  | All Caps | Directly Connected Device 4 | Enter device connected to this SVC (can provide up to 10) |  |  | C
Static Var Compensator Data | X | X | X |  | All Caps | Directly Connected Device 5 | Enter device connected to this SVC (can provide up to 10) |  |  | C
Static Var Compensator Data | X | X | X |  | All Caps | Directly Connected Device 6 | Enter device connected to this SVC (can provide up to 10) |  |  | C
Static Var Compensator Data | X | X | X |  | All Caps | Directly Connected Device 7 | Enter device connected to this SVC (can provide up to 10) |  |  | C
Static Var Compensator Data | X | X | X |  | All Caps | Directly Connected Device 8 | Enter device connected to this SVC (can provide up to 10) |  |  | C
Static Var Compensator Data | X | X | X |  | All Caps | Directly Connected Device 9 | Enter device connected to this SVC (can provide up to 10) |  |  | C
Static Var Compensator Data | X | X | X |  | All Caps | Directly Connected Device 10 | Enter device connected to this SVC (can provide up to 10) |  |  | C
Static Var Compensator Data | X | X | X |  |  | Comments | Enter any comments regarding this breaker-switch data |  |  | O
Static Var Compensator Data | X | X | X |  | mm/dd/yyyy | Effective Date | Date this breaker or switch was added, removed or updated in the model |  |  | R
Series Device Data (as applicable)
Series Device Data | X | X | X |  | List | Description of Change | Select: description of change from drop down list: Add, Change or Delete |  |  | C
Series Device Data | X | X | X |  | All Caps | Series Device Name | Series Device name as provided in the ERCOT model, which must meet the character limitation of the system. |  |  | R
Series Device Data | X | X | X |  | All Caps | ERCOT Station Name (Station Code or Station Mnemonic) | ERCOT Station Code Mnemonic that the breaker or switch is located, as listed in the model |  |  | R
Series Device Data | X | X | X |  | Automatic | SD Code | Concatenated code automatically provided |  |  | A
Series Device Data | X | X | X |  | kV | Voltage Level | Enter voltage for this Series device |  | R | R
Series Device Data | X | X | X |  | p.u. | Resistance | Enter resistance for this series device (100 MVA base) |  | R | R
Series Device Data | X | X | X |  | p.u. | Reactance | Enter reactance for this series device (100 MVA base) |  | R | R
Series Device Data | X | X | X |  | MVA | Continuous Rating | Rating that device can operate at indefinitely without damage, or violation fo NESC clearances. |  | R | R
Series Device Data | X | X | X |  | MVA | 2-hr Emergency Rating | Rating that device can operate at this rating for two hours without violation of NESC clearances or equipment failure |  | R | R
Series Device Data | X | X | X |  | MVA | 15-min Rating | Rating that device can operate at this rating for fifteen minutes without violation of NESC clearances or equipment failure |  | R | R
Series Device Data | X | X | X |  | All Caps | Connected Device 1 | Enter device connected to side 1 of this Series Device (can provide up to 10) |  |  | R
Series Device Data | X | X | X |  | All Caps | Connected Device 2 | Enter device connected to side 1 of this Series Device (can provide up to 10) |  |  | C
Series Device Data | X | X | X |  | All Caps | Connected Device 3 | Enter device connected to side 1 of this Series Device (can provide up to 10) |  |  | C
Series Device Data | X | X | X |  | All Caps | Connected Device 4 | Enter device connected to side 1 of this Series Device (can provide up to 10) |  |  | C
Series Device Data | X | X | X |  | All Caps | Connected Device 5 | Enter device connected to side 1 of this Series Device (can provide up to 10) |  |  | C
Series Device Data | X | X | X |  | All Caps | Connected Device 6 | Enter device connected to side 1 of this Series Device (can provide up to 10) |  |  | C
Series Device Data | X | X | X |  | All Caps | Connected Device 7 | Enter device connected to side 1 of this Series Device (can provide up to 10) |  |  | C
Series Device Data | X | X | X |  | All Caps | Connected Device 8 | Enter device connected to side 1 of this Series Device (can provide up to 10) |  |  | C
Series Device Data | X | X | X |  | All Caps | Connected Device 9 | Enter device connected to side 1 of this Series Device (can provide up to 10) |  |  | C
Series Device Data | X | X | X |  | All Caps | Connected Device 10 | Enter device connected to side 1 of this Series Device (can provide up to 10) |  |  | C
Series Device Data | X | X | X |  | Number | Bus Number (PTI Bus Number) | Bus number for Side 1 of this Series Device |  |  | O
Series Device Data | X | X | X |  | All Caps | Connected Device 1 | Enter device connected to side 2 of this Series Device (can provide up to 10) |  |  | R
Series Device Data | X | X | X |  | All Caps | Connected Device 2 | Enter device connected to side 2 of this Series Device (can provide up to 10) |  |  | C
Series Device Data | X | X | X |  | All Caps | Connected Device 3 | Enter device connected to side 2 of this Series Device (can provide up to 10) |  |  | C
Series Device Data | X | X | X |  | All Caps | Connected Device 4 | Enter device connected to side 2 of this Series Device (can provide up to 10) |  |  | C
Series Device Data | X | X | X |  | All Caps | Connected Device 5 | Enter device connected to side 2 of this Series Device (can provide up to 10) |  |  | C
Series Device Data | X | X | X |  | All Caps | Connected Device 6 | Enter device connected to side 2 of this Series Device (can provide up to 10) |  |  | C
Series Device Data | X | X | X |  | All Caps | Connected Device 7 | Enter device connected to side 2 of this Series Device (can provide up to 10) |  |  | C
Series Device Data | X | X | X |  | All Caps | Connected Device 8 | Enter device connected to side 2 of this Series Device (can provide up to 10) |  |  | C
Series Device Data | X | X | X |  | All Caps | Connected Device 9 | Enter device connected to side 2 of this Series Device (can provide up to 10) |  |  | C
Series Device Data | X | X | X |  | All Caps | Connected Device 10 | Enter device connected to side 2 of this Series Device (can provide up to 10) |  |  | C
Series Device Data | X | X | X |  | Number | Bus Number (PTI Bus Number) | Bus number for Side 2 of this Series Device |  |  | O
Series Device Data | X | X | X |  |  | Comments | Enter any comments regarding this breaker-switch data |  |  | O
Series Device Data | X | X | X |  | mm/dd/yyyy | Effective Date | Date this breaker or switch was added, removed or updated in the model |  |  | R
Load Data (as applicable)
Load Data | X | X | X |  | List | Description of Change | Select: description of change from drop down list: Add, Change or Delete |  |  | C
Load Data | X | X | X |  | All Caps | ERCOT Station Name (Station Code or Station Mnemonic) | ERCOT Station Code Mnemonic that the breaker or switch is located, as listed in the model |  |  | R
Load Data | X | X | X |  | All Caps | Load Name | Load name as provided in the ERCOT model, which must meet the character limitation of the system. |  |  | R
Load Data | X | X | X |  | Automatic | Load Code | Concatenated code automatically provided |  |  | A
Load Data | X | X | X |  | kV | Load Voltage Level | Enter voltage for this Load device |  |  | R
Load Data | X | X | X |  | Number | PTI Bus Number | Enter bus number for this Load device |  |  | O
Load Data | X | X | X |  | MW | Average Load Under Normal Operations | Enter average amount of MW Load under normal operations |  |  | R
Load Data | X | X | X |  | MVAr | Average MVAr Under Normal Operations | Enter average MVAr amount for this Load under normal operations |  |  | R
Load Data | X | X | X |  | All Caps | Directly Connected Device 1 | Enter device connected to this Load (can provide up to 10) |  |  | R
Load Data | X | X | X |  | All Caps | Directly Connected Device 2 | Enter device connected to this Load (can provide up to 10) |  |  | C
Load Data | X | X | X |  | All Caps | Directly Connected Device 3 | Enter device connected to this Load (can provide up to 10) |  |  | C
Load Data | X | X | X |  | All Caps | Directly Connected Device 4 | Enter device connected to this Load (can provide up to 10) |  |  | C
Load Data | X | X | X |  | All Caps | Directly Connected Device 5 | Enter device connected to this Load (can provide up to 10) |  |  | C
Load Data | X | X | X |  | All Caps | Directly Connected Device 6 | Enter device connected to this Load (can provide up to 10) |  |  | C
Load Data | X | X | X |  | All Caps | Directly Connected Device 7 | Enter device connected to this Load (can provide up to 10) |  |  | C
Load Data | X | X | X |  | All Caps | Directly Connected Device 8 | Enter device connected to this Load (can provide up to 10) |  |  | C
Load Data | X | X | X |  | All Caps | Directly Connected Device 9 | Enter device connected to this Load (can provide up to 10) |  |  | C
Load Data | X | X | X |  | All Caps | Directly Connected Device 10 | Enter device connected to this Load (can provide up to 10) |  |  | C
Load Data | X | X | X |  |  | Comments | Enter any comments regarding this breaker-switch data |  |  | O
Load Data | X | X | X |  | mm/dd/yyyy | Effective Date | Date this breaker or switch was added, removed or updated in the model |  |  | R
PUN Load Data
PUN Load Data | X | X | X |  | All Caps | ERCOT Station Name (Station Code or Station Mnemonic) | Enter Station Code for this PUN Load |  |  | C
PUN Load Data | X | X | X |  | List | Load Name | Select Load Name from drop down list (as provided from the Load Data tab) |  |  | C
PUN Load Data | X | X | X |  | Automatic | Load Code | Concatenated code automatically provided |  |  | A
PUN Load Data | X | X | X |  | Automatic | Hour Ending | Ending Hour of the day that the MW amount is provided |  |  | A
PUN Load Data | X | X | X |  | Automatic | Day of the Week | Day of the week for each Ending Hour of the Day that the MW amount is provided |  |  | A
PUN Load Data | X | X | X |  | MW | MW | MW Amount for each ending hour of each day of the week for this Load (168 hour period) |  |  | C
Note on I4: RDWG 31OCT2013: R - Required C - Conditional O - Optional A - Automatic
Note on J4: RDWG 31OCT2013: R - Required C - Conditional O - Optional A - Automatic
Note on K4: RDWG 31OCT2013: R - Required C - Conditional O - Optional A - Automatic

## RARF Workbook Tabs
Resource Registration Glossary Workbook Contents
Workbooks | Tabs --->
General Site ESIID | Instructions | General and Site Information | GEN Load Split - ESIID | Private Network - Site
Generation | Instructions | Unit Info - GEN | Unit Info - AGR | Ownership - GEN | Parameters - GEN | Operational Parameters - GEN | Operational Parameters - NRRC | Operational Parameters - ERRC | Private Network - Unit | Reactive Capability - GEN | Planning - GEN | Protection - GEN | SubSync - GEN | Stability Study Model | PSCAD Model | Dynamic Data
Wind | Instructions | Unit Info - WIND | Turbine Details | Ownership - WIND | Parameters - WIND | Operational Parameters - WIND | Operational Parameters - NRRC | Operational Parameters - ERRC | Private Network - Unit | Reactive Capability - WIND | Planning - WIND | Protection - WIND | Collector System - WIND | Collector System - Wind Seg Data | Stability Study Model | PSCAD Model | Dynamic Data
Combined Cycle | Instructions | Unit Info - TRAIN | Unit Info - CC | Ownership - CC | Parameters - CC | CC Configurations | CC Transitions | Parameters - CFG | Operational Parameters - CFG | Operational Parameters - NRRC | Operational Parameters - ERRC | Private Network - Unit | Reactive Capability - CC | Planning - CC | Protection - CC | SubSync - CC | Stability Study Model | PSCAD Model | Dynamic Data
Transmission | Instructions | Line Data | Line Temperature | Breaker Switch Data | Capacitor and Reactor Data | Transformer Data | Transformer Tap Settings | Static Var Compensator Data | Series Device Data | Load Data | PUN Load | One Line | Transformer Test Data
Non-Modeled Gen | Instructions | Unit Info - DG

## Sheet2 - dropdown field lists (hidden)
Breaker Switch Data | ALL | Y/N
Capacitor and Reactor Data | ALL GEN RES | MVA
CC Configurations | CC | MW
Collector System - WIND | GEN | MVAR
Collector System - Wind Segment Data | GEN, CC | KV
Gen Load Split - ESIID | GEN, CC, WIND | decimal degrees
General and Site | GEN, WIND | meters
General Information - Load Resource | LOAD | MW/min
Line Data | PUN | hours
Line Temperature | WIND | MWh
Load Data | GEN, CC, CFG, WIND | PSI
Load Resource Information |  | p.u.
Load Resource Parameters |  | %
Operational Parameters |  | R in p.u.
Operational Parameters |  | X in p.u.
Operational Parameters - ERRC |  | sec
Operational Parameters - NRRC |  | Hz
Ownership |  | cycles
Ownership |  | minutes
Planning |  | List
Private Network |  | Automatic
Private Network - Site |  | Text
Private Network - Unit
Protection
PUN Load Data
Reactive Capability
Series Device Data
Static Var Compensator Data
Subsync
Transformer Data
Transformer Tap Settings
Unit Info - Wind
Turbine Details
Unit Info - TRAIN
Unit Information