## Slide 1
West Texas Export Capability Assessment Results
System Planning and Operations
October 30, 2014
ERCOT Reliability Operating Subcommittee Meeting

## Slide 2: Assessment Purpose
To assess the impact of series capacitors on the West Texas export capability
To revise the existing West-North Interconnection Reliability Operating Limit (IROL)

## Slide 3: I. Series Capacitor Impact
2016 HWLL + wind generation projects meet Planning Guide
  System load: 36.5 GW
  Total wind generation capacity is 15,850 MW, dispatched output is 12,714 MW
  Wind generation in the West Texas is 13,943 MW, dispatched output is 11,461 MW

## Slide 4: West Texas Wind Generation
Zone | Capacity (MW)
Panhandle | 3,155
Far West | 3,467
West | 4,838
North | 1,900
West Others | 583

## Slide 5: West Texas Series Capacitors
# | Series Cap
1 | Edison
2 | Orsted
3 | Romney
4 | Kopperl
5 | Kirchhoff
6 | Gauss
7 | Cross
8 | Rocky Mound
1
2
3
4
5
6
7
8

## Slide 6: Assessment
Steady State Voltage Stability (PV) Analysis
System Strength Impact on the Panhandle Region
Dynamic Stability Analysis
Economic Cost Analysis – Congestion Impact

## Slide 7: Dynamic Stability Simulations
2016 HWLL
  Wind projects that meet Planning Guide 6.9 added
Total System Generation: 38,357 MW
Total Wind Generation: 15,037 MW
  South Wind: 1,253 MW (65.6% of 1,911 MW capacity)
  Panhandle Wind: 2,997 MW (95% of 3,155 MW capacity)
  Other Wind: 10,787 MW (100% of 10,787 MW capacity)
39.2% Wind Penetration Level
~8,300 MW of Non-wind Spinning Reserves

## Slide 8: Dynamic Simulation Tests
144 Total Contingencies
  Panhandle & CREZ System
  Single Circuit/3-Phase Fault
  Double Circuit/3-Phase Fault
  Breaker Failure Event/1-Phase Fault
Monitor System Response
  Amount of Wind Trip
  Voltage Response - West Texas 345 kV Buses
Evaluate with CREZ series capacitors in service and bypassed

## Slide 9: Dynamic Simulations Results
Acceptable Response Observed for 144 Contingencies
  Post-disturbance voltage settles between 0.9 and 1.1 pu
  Higher wind trip amounts observed when series capacitors bypassed
Better performance for Panhandle when adding Gauss and Cross series capacitors.
# of Contingencies with: | CREZ Series Capacitor Status | 
 | In Service | Bypassed
Acceptable Response | 144 | 144
>1400 MW Wind Trip | 1 | 9

## Slide 10: Series Capacitors -- Conclusion
# | Series Cap | Increase Panhandle Export | Improve Voltage Stability | Reduce Congestion Cost | Improve Dynamic Stability
1 | Edison |  | marginal |  | 
2 | Orsted |  | marginal |  | 
3 | Romney |  | marginal |  | 
4 | Kipperl |  | marginal |  | 
5 | Kirchhoff |  |  |  | 
6 | Gauss | High |  | High | High
7 | Cross | High |  | High | High
8 | Rocky Mound | Medium |  | marginal | marginal

## Slide 11: II. W-N IROL Study
Study to assess whether the W-N stability limit is an IROL
CREZ transmission fully online
Determine the limit under various outage scenarios, particularly around the W-N Interface
  Use Operations cases for various conditions
  Only include wind capacity in the Operations case
  Planned wind generation not included
Tool used for study: TSAT, VSAT

## Slide 12: Study Case and Assumption
Five real-time operational cases were assessed.
System Wind Generation Capacity ~ 11,000 MW
Scenario | System Load (MW) | West Texas Wind (MW) | W-N Transfer (MW)
High Wind, Low Load | 28,655 | 7,175 | 3,856
High Wind, Medium Load | 36,450 | 6,760 | 4,121
High W-N Transfer | 45,400 | 7,100 | 4,850
No Conventional Generation online in West Texas | 38,900 | 7,100 | 3,466
All conventional generation in West Texas online | 58,000 | 3,244 | 2,540
W-N Transfer: Flow on the sixteen 345 kV lines between West Texas and the rest of ERCOT

## Slide 13: Study Case and Criteria
By-pass all the series capacitors in West Texas.
All available TSAT wind models were included.
Load was adjusted in both North Central and South Central weather zones in the transfer analysis.
Horse Hollow wind farm was assumed to be interconnected in West Texas to increase available generation for transfer study.
SOL Methodology

## Slide 14: Study Results
No loss of load due to Cascading or voltage collapse
No trigger of under-frequency load shed at 59.3 Hz
No inter-area oscillation with damping ratio less than 3%
No issues found for all tested scenarios taking up to six line outages on the W-N Interface
Observe local voltage stability in regions of West Texas when more than six 345 kV circuits out on the W-N Interface

## Slide 15: WN-IROL Conclusion
Propose retirement of the W-N-IROL/GTL
  following the criteria in the SOL Methodology, no stability limit for the tested planning and operation scenarios.
Post-retirement: Only allow up to 6 circuits on outage on the W-N interface

## Slide 16: Next steps
Finalize report and post
Notify TRE/NERC
Issue Market Notice for retirement date of the W to N GTL/IROL
Retire GTL/IROL from Operation