September 2014 ERCOT Monthly Operations Report

Reliability and Operations Subcommittee Meeting

October 30, 2014

Table of Contents

1.	Report Highlights	1

2.	Frequency Control	2

2.1.	Frequency Events	2

2.2.	Responsive Reserve Events	3

2.3.	Load Resource Events	3

3.	Reliability Unit Commitment	4

4.	Wind Generation as a Percent of Load	4

5.	Congestion Analysis	5

5.1.	Notable Constraints for September	5

5.2.	Generic Transmission Constraint Congestion	6

5.3.	Congestion Costs for Calendar Year 2014	6

6.	System Events	8

6.1.	ERCOT Peak Load	8

6.2.	Load Shed Events	8

6.3.	Stability Events	8

6.4.	Notable PMU Events	8

6.5.	TRE/DOE Reportable Events	8

6.6.	New/Updated Constraint Management Plans	8

6.7.	New/Modified/Removed SPS	9

6.8.	New Procedures/Forms/Operating Bulletins	9

7.	Emergency Conditions	9

7.1.	OCNs	9

7.2.	Advisories	9

7.3.	Watches	9

7.4.	Emergency Notices	9

8.	Application Performance	9

8.1.	TSAT/VSAT Performance Issues	9

8.2.	Communication Issues	9

9.	Net-Forecast Bias Applied to NSRS Procurement for October 2014	10

10.	Appendix A: Real-Time Constraints	11

# Report Highlights

- The unofficial ERCOT peak for September was 64,397 MW.

- There were four frequency events in September. PMU data indicates the ERCOT system transitioned well in each case.

- There were four instances where Responsive Reserves were deployed. All of them were the result of frequency events.

- There was a single RUC Commitment in September for local congestion.

- The level of SCED congestion due to high loads dropped in September as temperatures began to cool. However, there was a greater amount of outage-related congestion.

- There was one system even event this month when ERCOT’s State Estimator and RTCA could not solve for approximately 40 minutes due to an invalid solution. A hotline call was made at the time of the event to the ERCOT TOs to monitor their own systems until the issue was resolved.

- ERCOT Applications performed well throughout the month. There was one instance where the VSAT tool was unavailable due to an application error. The error has since been corrected.

# Frequency Control

## Frequency Events

The ERCOT Interconnection experienced four frequency events in September, all of which resulted from Resource trips. The average event duration was approximately 73 seconds.

When analyzing frequency events, ERCOT evaluates PMU data according to industry standards. Events with an oscillating frequency of less than 1 Hz are considered to be inter-area, while higher frequencies indicate local events. Industry standards specify that damping ratio for inter-area oscillations should be 3.0% or greater. All events listed below indicate the ERCOT system met these standards and transitioned well after each disturbance. Further details on the Resource trip events can be seen in the Performance Disturbance Compliance Working Group report.  A summary of the frequency events is provided below:

| Date and Time | Max/Min Frequency (Hz) | Duration of Event (seconds) | PMU Data |  | Comments |
| --- | --- | --- | --- | --- | --- |
|  |  |  | Oscillation Mode | Damping Ratio |  |
| 9/3/2014 14:38 | 59.834 | 152 | 0.588 Hz | 9.41% | Unit trip with approximately 930 MW |
| 9/11/2014 6:41 | 59.857 | 59 | 0.644 Hz 0.640 Hz | 11.26% 11.90% | Plant trip with approximately 644 MW |
| 9/11/2014 7:32 | 59.886 | 8 | No significant oscillation modes captured |  | Unit trip with approximately 584 MW |
| 9/29/2014 15:41 | 59.835 | 72 | 0.595 Hz 0.597 Hz | 8.16% 6.98% | Plant trip with approximately 645 MW |

(Note: the duration of the frequency events is defined to be the time at which the frequency was outside the range of 60±0.1 Hz)

## Responsive Reserve Events

There were four events where Responsive Reserve MWs were released to SCED in September.  The events highlighted in blue were related to frequency events reported in section 2.1 above.

| Date and Time Released to SCED | Date and Time Recalled | Duration of Event | Maximum MWs Released | Comments |
| --- | --- | --- | --- | --- |
| 9/3/14 14:38:34 | 9/3/14 14:43:30 | 0:04:56 | 494.53 |  |
| 9/11/14 6:41:38 | 9/11/14 6:44:42 | 0:03:04 | 523.84 |  |
| 9/11/14 7:32:58 | 9/11/14 7:36:26 | 0:03:28 | 321.15 |  |
| 9/29/14 15:41:33 | 9/29/14 15:46:10 | 0:04:37 | 768.39 |  |

## Load Resource Events

There were no load resource deployment events in September.

# Reliability Unit Commitment

ERCOT reports on Reliability Unit Commitments (RUC) on a monthly basis. Commitments are reported grouped by operating day and weather zone. The total number of hours committed is the sum of the hours for all the units in the specified region. Additional information on RUC commitments can be found on the MIS secure site at Grid  Generation  Reliability Unit Commitment.

There were no DRUC commitments in September.

| HRUC Commitments |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Resource Location | # of Resources | Operating Day | # Hours Committed | Total MWhs | Reason for commitment |
| Southern | 1 | 9/25/2014 | 1 | 41 | Local Congestion |

# Wind Generation as a Percent of Load

# Congestion Analysis

The number of congestion events experienced by the ERCOT system remained steady in September due to continued warm temperatures and ongoing outages. There was no activity on any of the Generic Transmission Constraints (GTCs) in September.

## Notable Constraints for September

Nodal protocol section 3.20 specifies that ERCOT shall identify transmission constraints that are active or binding three or more times within a calendar month. As part of this process, ERCOT reports congestion that meets this criterion to ROS. In addition ERCOT also highlights notable constraints that have an estimated congestion rent exceeding $1,000,000 for a calendar month. These constraints are detailed in the table below. Rows highlighted in blue indicate the congestion was affected by one or more outages. For a list of all constraints activated in SCED for the month of September, please see Appendix A at the end of this report.

| Contingency | Overload | # of Days Constraint Active | Estimated Congestion Rent | Transmission Project |
| --- | --- | --- | --- | --- |
| Tejas Tnp - Greenbelt Tnp 138 kV | Heights Tnp HEIGHAT2 138/69 kV | 5 | $29,367,010 |  |
| Holt Switch - Bakke and Andrews North 138 kV | Wink Sub - Cheyenne Tap 138 kV | 2 | $5,492,756 | 15TPIT0058, 14TPIT0118 |
| Odessa Ehv Switch Axfmr 2 345/138 kV | Odessa Ehv Switch Axfmr1 345/138 kV | 5 | $4,251,858 |  |
| Key Sub - Willow Valley Switch 138 kV | Holt Switch - Amoco Midland Farms Tap 138 kV | 2 | $4,080,599 | 15TPIT0092 |
| Permian Basin Ses Axfmr2 138/69 kV | Permian Basin Ses - Wink Sub 138 kV | 1 | $3,659,307 | 14TPIT0118 |
| Eskota Switch - Abilene South 138 kV | Abilene Northwest - Ely Rea Tap 69 kV | 4 | $3,136,317 | TPIT Project 3402 |
| La Palma - Rio Hondo 138 kV | Harlingen Switch - Oleander 138 kV | 4 | $3,112,899 |  |
| Winks Sub - No Trees Switch 138 kV | Holt Switch - Amoco Midland Farms Tap 138 kV | 2 | $2,742,947 | 15TPIT0092 |
| DCKT Flewellen - Obrien and Maso Road 138 kV | Hockley - Betka 138 kV | 3 | $2,506,015 |  |
| Lewisville Switch Axfmr12 345/138 kV | Euless - Grapevine Highway 360 138 kV (1065_L) | 1 | $2,406,158 | 11TPIT0012 |
| Hutto Switch Axfmr 1 (3) 345/138 kV | Gilleland - Pflugerville 138 kV | 1 | $1,992,265 | 16TPIT0062 |
| DCKT Ph Robinson - Center - Cedar Bayou 345 kV | Meadow AT1 345/138 kV | 1 | $1,617,650 |  |
| Falcon Seaboard - Midland East 345 kV | Glenhaven - Crmwd 8 Tap 138 kV | 1 | $1,581,520 | 15TPIT0091 |
| Winks Sub - Permian Basin Ses 138 kV | Permian Basin Ses Axfmr2 138/69 kV | 1 | $1,144,586 |  |
| DCKT Randolph - Weiderstein and Fratt - Parkway Lcra 138 kV | Skyline - Nacdches 138 kV | 2 | $1,072,930 |  |
| Shamburger Switch - Martin Lake Ses 345 kV | Delek Poi - Tyler East 138 kV (1770_A) | 3 | $888,313 | 17TPIT0029 |
| DCKT Singleton - Tomball 345 kV | Singleton - Zenith 345 kV (SNGZEN99) | 13 | $418,639 | TPIT Project 3937 |
| Koch Up River - Gila 138 kV | Gila - Hiway 9 138 kV (GILA_HIWAY_2) | 15 | $315,123 |  |
| Orange Grove Switching Station - Lon Hill 138 kV | Lon Hill - Smith 69 kV | 4 | $279,452 | 16TPIT0026 |
| DCKT Jewett - Singleton 345 kV | Twin Oak Switch - Btu_Jack_Creek 345 kV | 5 | $242,280 | TPIT Project 3937 |
| DCKT Ferguson - Granite Mountain and Wirtz - Starcke - Paleface 138 kV | Wirtz - Flat Rock Lcra 138 kV | 8 | $141,649 |  |
| Salem LCRA AT4 345/138kV | Fayetteville 26AT2 345/138kV | 6 | $92,821 |  |
| DCKT Gibbons Creek - Singleton 345 kV | Jewett - Singleton 345 kV (260_A) | 9 | $92,173 | TPIT Project 3937 |
| Yellow Jacket - Fort Mason 138 kV | Fort Mason - Mason 69 kV | 3 | $52,356 | TPIT Project 3673 |
| Uvalde Aep - Odlaw Switchyard 138 kV | Hamilton Road - Maverick 138 kV | 5 | $49,663 | 16TPIT0024 |
| Laquinta - Lobo 138 kV | Bruni 138_69_1 138/69 kV | 7 | $32,229 | 13TPIT0158 |
| Eskota Switch Axfmr1 138/69 kV | Abilene Northwest - Ely Rea Tap 69 kV | 3 | $31,248 | TPIT Project 3402 |
| Lobo - San Miguel 345_138 kV Switchyards 345 kV | San Diego - Freer 69kV | 3 | $18,373 |  |
| Gibbons Creek - Singleton 345 kV (SNGXGC75) | Gibbons Creek - Singleton 345 kV (SNGXGC99) | 3 | $10,488 | TPIT Project 3937 |

## Generic Transmission Constraint Congestion

There was no activity on any ERCOT GTCs in September.

## Congestion Costs for Calendar Year 2014

The following table represents the top twenty active constraints for the calendar year to date based on the estimated congestion rent attributed to the congestion. ERCOT updates this list on a monthly basis.

| Contingency | Binding Element | # of 5-min SCED Intervals | Estimated Congestion Rent | Transmission Project |
| --- | --- | --- | --- | --- |
| Lytton Springs LY_AT1 345/138 kV | Lytton Springs LY_AT1 345/138 kV | 1,997 | $55,956,002 |  |
| Skywest - Spraberry Switch 138 kV, Skywest - Salt Flat Road 138 kV, and Salt Mine - Barber Lake Switch 138 kV | Midland East - Pecan Grove 138 kV | 3,738 | $46,790,259 | 14TPIT0052 |
| Tejas Tnp - Greenbelt Tnp 138 kV | Heights Tnp HEIGHAT2 138/69 kV | 1,104 | $29,367,010 |  |
| Midland East Axfmr 1 (3) 345/138 kV, Moss Switch Axfmr 1 345/138 kV, and Midland East - Moss Switch - Odessa Ehv Switch 345 kV | Odessa North Sd3 138 kV | 5,310 | $23,944,433 | 2012-R3, 2012-R4 |
| Orange Grove Switching Station - Lon Hill 138 kV, DCKT Lon Hill - North Edinburg 345 kv and Orange Grove Switching Station 138 kV, and Lon Hill 345_138_2 (3) 345/138 kV | Lon Hill - Smith 69 kV | 8,181 | $13,772,263 | 16TPIT0026, 2012-R18 |
| DCKT Flewellen - Obrien and Maso Road 138 kV, DCKT Singleton - Zenith 345 kV | Hockley - Betka 138 kV | 600 | $11,942,217 | TPIT Project 3682A, 3682B |
| Basecase | Valley Import | 495 | $11,577,259 |  |
| DCKT Jewett - Singleton 345 kV | Twin Oak Switch - Gibbons Creek 345 kV | 273 | $10,912,808 |  |
| DCKT Gabriel - Glasscock LCRA and Rivery 138 kV, Glasscock LCRA - Gabriel 138 kV, and DCKT Gabriel - Bell County - Hutto Switch 138 kV | Marshall Ford - Lago Vista 138 kV | 209 | $9,871,526 | 15TPIT0061 |
| DCKT Paris Switch - Valley Ses and Valley South 345 kV | Paris Switch AXFMR1 (3) 345/138 kV | 1,442 | $9,291,357 | 14TPIT0093 |
| DCKT Wa Parish - Jeanetta 345 kV | Smithers - Bellaire 345 kV | 1,058 | $7,870,155 |  |
| Alice - Kingsville 138 kV, Kingsville - Lon Hill 138 kV, Nelson Sharpe - Lon Hill 345 kV | Lon Hill - Calallen Sub 69 kV | 912 | $7,699,219 | 12TPIT0181, 2012-R13 |
| Koch Up River - Gila 138 kV | Gila - Hiway 9 138 kV (GILA_HIWAY_2) | 24,054 | $7,158,255 |  |
| Laquinta - Lobo 138 kV | Bruni 138_69_1 138/69 kV | 10,782 | $7,031,903 | 13TPIT0148 |
| Key Sub - Willow Valley Switch 138 kV and Winks Sub - No Trees Switch 138 kV | Holt Switch - Amoco Midland Farms Tap 138 kV | 450 | $6,904,311 | 15TPIT0092 |
| DCKT Gibbons Creek - Singleton 345 kV and DCKT Twin Oak Switch - Gibbons Creek and Btu_Jack_Creek 345 kV | Jewett - Singleton 345 kV (260_A) | 7,377 | $6,858,562 | TPIT Project 3937 |
| McNeil Lcra - Gilleland 138 kV, Hutto Switch Axfmr 1 (3) 345/138 kV, and DCKT Austrop - Sandow Switch 345 kV | Hutto Switch - Round Rock Northeast 138 kV (1661_B) | 315 | $6,787,059 | 16TPIT0062 |
| La Palma - Rio Hondo 138 kV | Harlingen Switch - Oleander 138 kV | 430 | $6,749,092 |  |
| Sun Switch - Morgan Creek Ses 138 kV and Bluff Creek Switch - Ennis Creek Switch 138 kV | Snyder - Sacroc 138 kV | 509 | $6,283,276 | 09TPIT0120 |
| DCKT Singleton - Tomball 345 kV | Singleton - Zenith 345 kV (SNGZEN99) | 5,159 | $6,160,369 | TPIT Project 3937 |

# System Events

## ERCOT Peak Load

The unofficial ERCOT peak load for the month was 64,397 MW and occurred on September 10 during the hour ending 17:00.

## Load Shed Events

None

## Stability Events

None

## Notable PMU Events

ERCOT analyzes PMU data for any significant system disturbances that do not fall into the Frequency Events category reported in section 2.1. The results are summarized in this section once the analysis has been completed.

There were no reportable events in September.

## TRE/DOE Reportable Events

ERCOT experienced one reportable system event this month. On September 5, ERCOT’s State Estimator and RTCA could not solve for approximately 40 minutes due to an invalid solution. A hotline call was made at the time of the event to the ERCOT TOs to monitor their own systems until the issue was resolved.

## New/Updated Constraint Management Plans

None

## New/Modified/Removed SPS

None

## New Procedures/Forms/Operating Bulletins

None

# Emergency Conditions

## OCNs

| Date and Time | Description |
| --- | --- |
| 9/10/2014 03:50 | ERCOT issued an OCN for a possible capacity shortage for hours ending 16:00 through 19:00. |

## Advisories

| Date and Time | Description |
| --- | --- |
| 9/6/2014 00:14 | Advisory issued due to ERCOT's Real-time Contingency Analysis and State Estimator not solved for more than 15 minutes. |
| 9/12/2014 19:06 | ERCOT issued an Advisory for a geomagnetic disturbance storm of K-7 or higher. |
| 9/25/2014 05:25 | Advisory issued due to ERCOT’s Voltage Security Assessment Tool being unavailable. |

## Watches

None

## Emergency Notices

None

# Application Performance

ERCOT system applications performed well in September. There was one issue with the VSAT application.

## TSAT/VSAT Performance Issues

| Date and Time | Description |
| --- | --- |
| 9/25/2014 05:25 | Advisory issued due to ERCOT’s Voltage Security Assessment Tool being unavailable. |

## Communication Issues

None

# Net-Forecast Bias Applied to NSRS Procurement for October 2014

Each month, ERCOT calculates a net Forecast Bias pursuant to the ERCOT Ancillary Services Methodology for procurement of Non-Spinning Reserve Service (NSRS).  The table below indicates the amount of net Forecast Bias that was applied to the NSRS procurement for specified blocks of time for the month of October, 2014.

| Blocks | Negative Net Load Forecast Average Error - By Weather Zone for the 5 Largest Zones |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Coast | East | North Central | South Central | Southern |
| 1-2 | 0 | 0 | 0 | 0 | 0 |
| 3-6 | 0 | 0 | 0 | 0 | 0 |
| 7-10 | 0 | 0 | 0 | 0 | 0 |
| 11-14 | -8 | -1 | -8 | -4 | -2 |
| 15-18 | -144 | -24 | -170 | -85 | -43 |
| 19-22 | 0 | 0 | 0 | 0 | 0 |
| 23-24 | 0 | 0 | 0 | 0 | 0 |

# Appendix A: Real-Time Constraints

The following is a complete list of constraints activated in SCED for the month of September. Full contingency descriptions can be found in the Standard Contingencies List located on the MIS secure site at Grid  Generation  Reliability Unit Commitment.

| Contingency | Constrained Element | From Station | To Station | # of Days Constraint Active |
| --- | --- | --- | --- | --- |
| SKOCNU28 | GILA_HIWAY_2_1 | GILA | HIWAY_9 | 15 |
| DTB_SNG5 | SNGZEN99_A | SNG | ZEN | 13 |
| DGIBSNG5 | 260_A_1 | JEWET | SNG | 9 |
| DFERPAL8 | 38T365_1 | WIRTZ | FLATRO | 8 |
| SLAQLOB8 | BRUNI_69_1 | BRUNI | BRUNI | 7 |
| XSAL258 | FAYETT_6AT2 | FAYETT | FAYETT | 6 |
| DJEWSNG5 | JK_TOKSW_1 | TOKSW | JK_CK | 5 |
| SBRAUVA8 | HAMILT_MAVERI1_1 | HAMILTON | MAVERICK | 5 |
| STEJGR38 | HEIGHTTN_HAT2 | HEIGHTTN | HEIGHTTN | 5 |
| XODE58 | ODEHV_MR1H | ODEHV | ODEHV | 5 |
| SLA_RIO8 | HARLNS_OLEAND1_1 | HARLNSW | OLEANDER | 4 |
| SMCEABS8 | ABNW_ELYT1_1 | ABNW | ELYT | 4 |
| SORNLON8 | LON_HI_SMITH1_1 | LON_HILL | SMITH | 4 |
| DFL_MAR8 | BETHK_66_A | HK | BET | 3 |
| SFORYEL8 | FORTMA_MASN1_1 | FORTMA | MASN | 3 |
| SGIBSNG5 | SNGXGC99_1 | GIBCRK | SNG | 3 |
| SLOBSAN5 | FREER_SAN_DI1_1 | SAN_DIEG | FREER | 3 |
| SSHBMLS5 | 1770__A | DLPOI | TYEST | 3 |
| XESK89 | ABNW_ELYT1_1 | ABNW | ELYT | 3 |
| DCHBJOR5 | BRNLAN86_A | LAN | BRN | 2 |
| DEMSSAG8 | 6265__A | EMSES | MRSDO | 2 |
| DFPPFAY5 | 190T152_1 | GIDEON | WINCHE | 2 |
| DFRAPAR8 | K2_P3_1 | SKYLINE | K2 | 2 |
| DHUTGAB8 | 211T147_1 | GILLCR | MCNEIL_ | 2 |
| DWLV89N8 | 3410__A | ELVSW | REGST | 2 |
| DWLVWTR5 | 3130__B | INDST | CMPST | 2 |
| SCHYWIN8 | 6090__D | HLTSW | AMMFT | 2 |
| SILLFTL8 | FDR_OZN_1 | FRIEND_R | OZNA | 2 |
| SKEYWLV8 | 6090__D | HLTSW | AMMFT | 2 |
| SLOBSAN5 | LAQUIN_LOBO1_1 | LAQUINTA | LOBO | 2 |
| SMDFHLT8 | 6101__B | WINKS | CHEYT | 2 |
| SRDODES8 | 940__C | ENWSW | WXHCH | 2 |
| XMOS258 | 6475__C | ODEHV | ODESA | 2 |
| DAUSSND5 | 1661__B | HUTTO | RRNES | 1 |
| DAUSSND5 | 211T147_1 | GILLCR | MCNEIL_ | 1 |
| DCMTBNB8 | 6495__C | SAGNA | AMFTP | 1 |
| DFPPFAY5 | MAGRUD_VICTOR2_1 | VICTORIA | MAGRUDER | 1 |
| DGABBEL8 | 1661__B | HUTTO | RRNES | 1 |
| DHCKRNK5 | 1065__L | EULES | GRHWY | 1 |
| DLONOR58 | LON_HI_SMITH1_1 | LON_HILL | SMITH | 1 |
| DLONOR58 | WES_MV_W_1 | WESLACO | MV_WESL4 | 1 |
| DMARPA_8 | 38T365_1 | WIRTZ | FLATRO | 1 |
| DMARZOR5 | 293T304_1 | CIBOLO | SCHERT | 1 |
| DNAVLEG5 | 60__A | BBSES | NAVARRO | 1 |
| DPHRCTR5 | MDO_AT1 | MDO | MDO | 1 |
| DPHRCTR5 | MDO_AT1L | MDO | MDO | 1 |
| DSKYCAL5 | R5_U3_1 | BRAUNIG | CAGNON | 1 |
| DWALCAL8 | E1_M1_1 | M1 | E1 | 1 |
| SBOSELM5 | 1030__B | BOSQUESW | RGH | 1 |
| SCHABSP9 | 6815__D | MDKSW | RGNST | 1 |
| SCRSBAT9 | UVALDE_69A1 | UVALDE | UVALDE | 1 |
| SFLCMDL5 | 6510__A | GLNHV | CRM8T | 1 |
| SKEYWLV8 | 6550__A | PBSES | WINKS | 1 |
| SLOBSAN5 | PALDRO_PEARSAL_1 | PEARSALL | PALODURO | 1 |
| SNEDLON5 | WES_MV_W_1 | WESLACO | MV_WESL4 | 1 |
| SPOACSS8 | CSSWCS-CSSC_1 | CSSWCS | CSSC | 1 |
| SVICCO28 | COLETO_VICTOR2_1 | COLETO | VICTORIA | 1 |
| SVLDOW8 | MRK_VNVL_1 | MRKHMSW | VNVLKSW | 1 |
| SWICPBS9 | 6550__A | PBSES | WINKS | 1 |
| SWINPBS8 | 6100__D | ANDNR | ANDWT | 1 |
| SWINPBS8 | PBSES_FMR2 | PBSES | PBSES | 1 |
| XHUT58 | 1666__B | GILLCR | PFLGV | 1 |
| XLOB58 | FREER_SAN_DI1_1 | SAN_DIEG | FREER | 1 |
| XLOB58 | PALDRO_PEARSAL_1 | PEARSALL | PALODURO | 1 |
| XLOB58 | LAQUIN_LOBO1_1 | LAQUINTA | LOBO | 1 |
| XLWS58 | 1065__L | EULES | GRHWY | 1 |
| XOKL58 | VERS_69_1 | VERS | VERS | 1 |
| XPB1S89 | 6550__A | PBSES | WINKS | 1 |
| XPH2R58 | PHR_AT1L | PHR | PHR | 1 |
| XRIO358 | WES_MV_W_1 | WESLACO | MV_WESL4 | 1 |
| XRN2K58 | 1065__L | EULES | GRHWY | 1 |
| XWL2V58 | 3130__B | INDST | CMPST | 1 |