## Slide 1: Unannounced Capacity Testing Summary
September 2013 to August 2014
Notes: As required per ERCOT Nodal Protocols 8.1.1.2
Report to ROS per…
(7) ERCOT shall maintain historical records of unannounced Generation Resource test results, using the information contained therein to adjust the Reserve Discount Factor (RDF) subject to the approval of the appropriate TAC subcommittee. ERCOT shall report to the Reliability and Operations Subcommittee (ROS) annually or as requested by ROS the aggregated results of such unannounced testing (excluding retests), including, but not limited to, the number and total capacity of Resources tested, the percentage of Resources that met or exceeded their HSL reported by telemetry, the percentage that failed to meet their HSL reported by telemetry, and the total MW capacity shortfall of those Resources that failed to meet their HSL reported by telemetry.

## Slide 2: Unannounced Capacity Testing Summary
Unannounced Resource Capacity Testing Summary |  |  |  |  | 
From 9/1/2013 to 8/31/2014 |  |  |  |  | 
Resources Tested: |  | 111 |  |  | 
Distinct Resources Tested: |  | 66 |  |  | 
Distinct QSE's Tested: |  | 45 |  |  | 
Distinct Capacity of Resources Tested: |  | 28,204 MW |  |  | 
Cumulative Capacity of Resources Tested: |  | 45,500 MW |  |  | 
Resources Passed: | 74 | Resources Failed: |  | 37 | 
Total MW Capacity Shortfall of Failed Resources: |  |  | 223.24 MW |  | 

## Slide 3: Capacity Testing Results by Resource Ambient Temperature
Chart: Capacity Testing Results by Ambient Temperature for 09/01/2013 to 08/31/2014
| T <= 85 | 85 < T <= 95 | 95 > T
Pass | 34 | 37 | 3
Fail | 12 | 20 | 5
73.91%
Capacity Shortfall By Ambient Temperature for 9/1/2013 to 8/31/2014 |  |  | 
Range | T <= 85 | 85 < T <= 95 | 95 > T
Capacity Tested (MW) | 18129 | 24411 | 2965
Shortfall (MW) | 42.7 | 160 | 20.54
 | 0.24% | 0.66% | 0.69%

## Slide 4: Current Reserve Discount Factor

## Slide 5: Possible changes based on observed results
Change discount factor to 1 (no discount) for Temp below 85⁰F
Change discount factor to 1 (no discount) for Temp between 85⁰F and 95⁰F
ERCOT sees benefit in adjusting the discount factor for temperatures below 95 ⁰F
ERCOT does not have a large sample of generation above 95 ⁰F
  Prefer to collect more test for greater than 95 ⁰F like to have 10% or greater capacity tested in that temperature range before making adjustment.