## Summary
Release Date: October 31, 2014
FINAL Seasonal Assessment of Resource Adequacy for the ERCOT Region Winter 2014/2015 SUMMARY The ERCOT region is expected to have sufficient installed generating capacity to serve forecasted peak demands in conditions that include a historically typical amount of generation outages. Based on the results of this study, even an extreme higher-than-normal number of forced generation outages occurring during a period of unusually high demand would be unlikely to result in insufficient resources being available to serve those demands, unless those conditions coincided with extreme fuel supply curtailments. For this final winter assessment, the peak capacity percentage applied to wind resources changed from 8.7 percent of nameplate capacity to a winter season value of 19 percent for non-Coastal resources and 36 percent for Coastal resources. This change reflects a new methodology, which is based on historical performance during peak periods and was approved by the ERCOT Board of Directors on October 14, 2014. New summer capacity percentages for wind generation will be included in the preliminary and final summer and fall SARA reports. Capacity ratings reported for most other generation resources are higher in the winter due to the effects of lower ambient temperatures. Based on ERCOT's drought risk analysis, no changes to unit capacities due to drought conditions are anticipated or reflected over the period covered by this winter assessment. Coal plant owners also are reporting sufficient coal inventories for peak load operations this winter. On October 23, 2014, the U.S. Court of Appeals lifted the stay on the U.S. Environmental Protection Agency's (EPA) implementation of the Cross-State Air Pollution Rule (CSAPR). Based on court filings by the EPA, the rule could go into effect as early as January 2015. Compliance planning information received in late August 2014 indicates that generation companies in the ERCOT region have not reported any anticipated changes to available generation capacity attributable to CSAPR. Resource owners will likely wait to finalize their compliance plans until they receive rule implementation details from the EPA, but it is reasonable to expect that additional coal units could be placed into seasonal mothball status when CSAPR is implemented, reducing the capacity available to serve load during the periods from September through May. ERCOT is monitoring EPA's implementation of CSAPR and potential changes to generation company compliance plans. This system-wide winter assessment does not address localized resource adequacy concerns associated with operational transmission issues, such as the events that occurred in the Lower Rio Grande Valley in early October. ERCOT continues to work closely with transmission service providers to address electric reliability concerns associated with growth in the Valley region and other areas of ERCOT.

## Scenarios
2014 Seasonal Assessment of Resource Adequacy for the ERCOT Region (SARA)
Winter 2014/2015 - Final
Release Date: October 31, 2014
Forecasted Capacity and Demand
| Operational Resources (excluding wind), MW | 66621.1 | Based on current Seasonal Maximum Sustainable Limits reported through the unit registration process
| Private Use Network Capacity Contribution, MW | 4318 | Average capability of the top 20 hours in the winter seasons for the past three years (2011-2013)
| Capacity Contribution of Non-Coastal Wind Resources, MW | 1867.301 | Based on 19% of installed capacity for non-coastal wind resources per ERCOT Nodal Protocols Section 3.2.6.2.2 and approved NPRR 611
| Capacity Contribution of Coastal Wind Resources, MW | 604.944 | Based on 36% of installed capacity for coastal wind resources per ERCOT Nodal Protocols Section 3.2.6.2.2. and approved NPRR 611
| RMR Resources to be under Contract, MW | -0.001 | No RMR Resources currently under contract
| Non-Synchronous Ties Capacity Contribution, MW | 494.8 | Average capability of the top 20 hours in the winter seasons in the past three years (2011-2013)
| Switchable Capacity Total, MW | 3702 | Installed capacity of units that can switch to other Regions
| less Switchable Capacity Unavailable to ERCOT, MW | -470 | Based on survey responses of Switchable Resource owners
| Mothball Resources, MW | 0 | Based on Probability of Return responses of Mothball Resource owners
| Planned Resources (not wind) with signed IA and Air Permit, MW | 30 | Based on in-service dates provided by developers of generation resources
| Capacity Contribution of Planned Non-Coastal Wind with Signed IA, MW | 182.02 | Based on in-service dates provided by developers of generation resources and 19% of installed capacity for non-coastal wind resources
| Capacity Contribution of Planned Coastal Wind with Signed IA, MW | 0 | Based on in-service dates provided by developers of generation resources and 36% of installed capacity for coastal wind resources
[a] Total Resources, MW |  | 77350.164
[b] Peak Demand, MW |  | 52837 | Winter peak forecast is based on normal weather conditions for 2002 – 2013
[c] Reserve Capacity [a - b], MW |  | 24513.164
Range of Potential Risks
|  | Forecasted Season Peak Load | Extreme Load / Expected Generation Outages | Extreme Load / Extreme Generation Outages
| Extreme Load Adjustment for December-February Peak | 0 | 6805 | 6805 | Winter extreme peak forecast is 59,642 MW
| Typical Maintenance Outages | 4151 | 4151 | 4151 | Based on historical average of planned outages for December through February weekdays (August 2010 to October 9, 2014)
| Forced Outages | 3729 | 7373 | 7373 | Based on historical average of forced outages for December through February weekdays (August 2010 to October 9, 2014). Extreme load scenarios also include a forecast of derated unit capacity due to natural gas curtailments caused by low temperatures at the time of peak load.
| 90th Percentile Forced Outages | 0 | 0 | 5028 | Includes a forecast of derated unit capacity due to extreme fuel supply curtailments caused by extremely low temperatures at the time of peak load
[d] Total Uses of Reserve Capacity |  | 7880 | 18329 | 23357
[e] Capacity Available for Operating Reserves [c - d], MW |  | 16633.164 | 6184.164 | 1156.164
Less than 2,300 MW indicates risk of EEA1

## Capacity
COMMON NAME | GENERATION INTERCONNECTION PROJECT CODE | UNIT CODE | COUNTY | FUEL | ZONE | START DATE | WINTER RATING (MW)
Operational Resources
COMANCHE PEAK U1 |  | CPSES_UNIT1 | SOMERVELL | NUCLEAR | NORTH | 1990 | 1235
COMANCHE PEAK U2 |  | CPSES_UNIT2 | SOMERVELL | NUCLEAR | NORTH | 1993 | 1225
SOUTH TEXAS U1 |  | STP_STP_G1 | MATAGORDA | NUCLEAR | SOUTH | 1988 | 1350
SOUTH TEXAS U2 |  | STP_STP_G2 | MATAGORDA | NUCLEAR | SOUTH | 1989 | 1354
BIG BROWN U1 |  | BBSES_UNIT1 | FREESTONE | COAL | NORTH | 1971 | 606
BIG BROWN U2 |  | BBSES_UNIT2 | FREESTONE | COAL | NORTH | 1972 | 602
COLETO CREEK |  | COLETO_COLETOG1 | GOLIAD | COAL | SOUTH | 1980 | 660
FAYETTE POWER PROJECT U1 |  | FPPYD1_FPP_G1 | FAYETTE | COAL | SOUTH | 1979 | 603
FAYETTE POWER PROJECT U2 |  | FPPYD1_FPP_G2 | FAYETTE | COAL | SOUTH | 1980 | 605
FAYETTE POWER PROJECT U3 |  | FPPYD2_FPP_G3 | FAYETTE | COAL | SOUTH | 1988 | 449
GIBBONS CREEK U1 |  | GIBCRK_GIB_CRG1 | GRIMES | COAL | NORTH | 1983 | 470
J K SPRUCE U1 |  | CALAVERS_JKS1 | BEXAR | COAL | SOUTH | 1992 | 562
J K SPRUCE U2 | 09INR0002 | CALAVERS_JKS2 | BEXAR | COAL | SOUTH | 2010 | 775
J T DEELY U1 |  | CALAVERS_JTD1 | BEXAR | COAL | SOUTH | 1977 | 430
J T DEELY U2 |  | CALAVERS_JTD2 | BEXAR | COAL | SOUTH | 1978 | 420
LIMESTONE U1 |  | LEG_LEG_G1 | LIMESTONE | COAL | NORTH | 1985 | 831
LIMESTONE U2 |  | LEG_LEG_G2 | LIMESTONE | COAL | NORTH | 1986 | 858
MARTIN LAKE U1 |  | MLSES_UNIT1 | RUSK | COAL | NORTH | 1977 | 815
MARTIN LAKE U2 |  | MLSES_UNIT2 | RUSK | COAL | NORTH | 1978 | 820
MONTICELLO U3 |  | MNSES_UNIT3 | TITUS | COAL | NORTH | 1978 | 795
OAK GROVE SES U1 | 09INR0006a | OGSES_UNIT1A | ROBERTSON | COAL | NORTH | 2010 | 840
OAK GROVE SES U2 | 09INR0006b | OGSES_UNIT2 | ROBERTSON | COAL | NORTH | 2011 | 825
OKLAUNION U1 |  | OKLA_OKLA_G1 | WILBARGER | COAL | WEST | 1986 | 650
SAN MIGUEL U1 |  | SANMIGL_SANMIGG1 | ATASCOSA | COAL | SOUTH | 1982 | 391
SANDOW U5 | 08INR0003 | SD5SES_UNIT5 | MILAM | COAL | SOUTH | 2010 | 570
SANDY CREEK U1 |  | SCES_UNIT1 | MCLENNAN | COAL | NORTH | 2013 | 970
TWIN OAKS U1 |  | TNP_ONE_TNP_O_1 | ROBERTSON | COAL | NORTH | 1990 | 158
TWIN OAKS U2 |  | TNP_ONE_TNP_O_2 | ROBERTSON | COAL | NORTH | 1991 | 158
W A PARISH U5 |  | WAP_WAP_G5 | FT. BEND | COAL | HOUSTON | 1977 | 659
W A PARISH U6 |  | WAP_WAP_G6 | FT. BEND | COAL | HOUSTON | 1978 | 658
W A PARISH U7 |  | WAP_WAP_G7 | FT. BEND | COAL | HOUSTON | 1980 | 577
W A PARISH U8 |  | WAP_WAP_G8 | FT. BEND | COAL | HOUSTON | 1982 | 610
A VON ROSENBERG 1 CTG 1 | 00INR0017 | BRAUNIG_AVR1_CT1 | BEXAR | GAS | SOUTH | 2000 | 155
A VON ROSENBERG 1 CTG 2 | 00INR0017 | BRAUNIG_AVR1_CT2 | BEXAR | GAS | SOUTH | 2000 | 155
A VON ROSENBERG 1 STG | 00INR0017 | BRAUNIG_AVR1_ST | BEXAR | GAS | SOUTH | 2000 | 170
B M DAVIS CTG 3 | 09INR0038 | B_DAVIS_B_DAVIG3 | NUECES | GAS | SOUTH | 2010 | 165
B M DAVIS CTG 4 | 09INR0038 | B_DAVIS_B_DAVIG4 | NUECES | GAS | SOUTH | 2010 | 165
B M DAVIS STG 2 |  | B_DAVIS_B_DAVIG2 | NUECES | GAS | SOUTH | 1976 | 320
BASTROP ENERGY CENTER CTG 1 | 01INR0021 | BASTEN_GTG1100 | BASTROP | GAS | SOUTH | 2002 | 167
BASTROP ENERGY CENTER CTG 2 | 01INR0021 | BASTEN_GTG2100 | BASTROP | GAS | SOUTH | 2002 | 167
BASTROP ENERGY CENTER STG | 01INR0021 | BASTEN_ST0100 | BASTROP | GAS | SOUTH | 2002 | 234
BOSQUE COUNTY PEAKING CTG 1 | 00INR0018 | BOSQUESW_BSQSU_1 | BOSQUE | GAS | NORTH | 2000 | 166.6
BOSQUE COUNTY PEAKING CTG 2 | 00INR0018 | BOSQUESW_BSQSU_2 | BOSQUE | GAS | NORTH | 2000 | 166.6
BOSQUE COUNTY PEAKING CTG 3 | 00INR0018 | BOSQUESW_BSQSU_3 | BOSQUE | GAS | NORTH | 2001 | 168.5
BOSQUE COUNTY PEAKING STG 4 | 00INR0028 | BOSQUESW_BSQSU_4 | BOSQUE | GAS | NORTH | 2001 | 85.2
BOSQUE COUNTY PEAKING STG 5 | 08INR0046 | BOSQUESW_BSQSU_5 | BOSQUE | GAS | NORTH | 2009 | 200.7
BRAZOS VALLEY CTG 1 | 01INR0031 | BVE_UNIT1 | FORT BEND | GAS | HOUSTON | 2003 | 168
BRAZOS VALLEY CTG 2 | 01INR0031 | BVE_UNIT2 | FORT BEND | GAS | HOUSTON | 2003 | 168
BRAZOS VALLEY STG 3 | 01INR0031 | BVE_UNIT3 | FORT BEND | GAS | HOUSTON | 2003 | 270
CALENERGY (FALCON SEABOARD) CTG 1 |  | FLCNS_UNIT1 | HOWARD | GAS | WEST | 1987 | 77.5
CALENERGY (FALCON SEABOARD) CTG 2 |  | FLCNS_UNIT2 | HOWARD | GAS | WEST | 1987 | 77.5
CALENERGY (FALCON SEABOARD) STG 3 |  | FLCNS_UNIT3 | HOWARD | GAS | WEST | 1988 | 74
CEDAR BAYOU CTG 4 | 08INR0035 | CBY4_CT41 | CHAMBERS | GAS | HOUSTON | 2009 | 173
CEDAR BAYOU CTG 5 | 08INR0035 | CBY4_CT42 | CHAMBERS | GAS | HOUSTON | 2009 | 173
CEDAR BAYOU STG 6 | 08INR0035 | CBY4_ST04 | CHAMBERS | GAS | HOUSTON | 2009 | 186
COLORADO BEND ENERGY CENTER CTG 1 | 06INR0035 | CBEC_GT1 | WHARTON | GAS | HOUSTON | 2007 | 88
COLORADO BEND ENERGY CENTER CTG 2 | 06INR0035 | CBEC_GT2 | WHARTON | GAS | HOUSTON | 2007 | 84
COLORADO BEND ENERGY CENTER CTG 3 | 06INR0035 | CBEC_GT3 | WHARTON | GAS | HOUSTON | 2008 | 88
COLORADO BEND ENERGY CENTER CTG 4 | 06INR0035 | CBEC_GT4 | WHARTON | GAS | HOUSTON | 2008 | 83
COLORADO BEND ENERGY CENTER STG 1 | 06INR0035 | CBEC_STG1 | WHARTON | GAS | HOUSTON | 2007 | 105
COLORADO BEND ENERGY CENTER STG 2 | 06INR0035 | CBEC_STG2 | WHARTON | GAS | HOUSTON | 2008 | 108
CVC CHANNELVIEW CTG 1 | 02INR0004 | CVC_CVC_G1 | HARRIS | GAS | HOUSTON | 2008 | 157.8
CVC CHANNELVIEW CTG 2 | 02INR0004 | CVC_CVC_G2 | HARRIS | GAS | HOUSTON | 2008 | 166.5
CVC CHANNELVIEW CTG 3 | 02INR0004 | CVC_CVC_G3 | HARRIS | GAS | HOUSTON | 2008 | 165.8
CVC CHANNELVIEW STG 5 | 02INR0004 | CVC_CVC_G5 | HARRIS | GAS | HOUSTON | 2008 | 132.9
DEER PARK ENERGY CENTER CTG 1 | 02INR0020 | DDPEC_GT1 | HARRIS | GAS | HOUSTON | 2002 | 203
DEER PARK ENERGY CENTER CTG 2 | 02INR0020 | DDPEC_GT2 | HARRIS | GAS | HOUSTON | 2002 | 215
DEER PARK ENERGY CENTER CTG 3 | 02INR0020 | DDPEC_GT3 | HARRIS | GAS | HOUSTON | 2002 | 203
DEER PARK ENERGY CENTER CTG 4 | 02INR0020 | DDPEC_GT4 | HARRIS | GAS | HOUSTON | 2002 | 215
DEER PARK ENERGY CENTER STG | 02INR0020 | DDPEC_ST1 | HARRIS | GAS | HOUSTON | 2002 | 290
DEER PARK ENERGY CENTER CTG 6 | 14INR0015 | DDPEC_GT6 | HARRIS | GAS | HOUSTON | 2014 | 190
ENNIS POWER STATION CTG 2 | 01INR0008 | ETCCS_CT1 | ELLIS | GAS | NORTH | 2002 | 231
ENNIS POWER STATION STG 1 | 01INR0008 | ETCCS_UNIT1 | ELLIS | GAS | NORTH | 2002 | 127
FERGUSON REPLACEMENT CTG1 | 13INR0021 | FERGCC_FERGGT1 | LLANO | GAS | SOUTH | 2014 | 186.1
FERGUSON REPLACEMENT CTG2 | 13INR0021 | FERGCC_FERGGT2 | LLANO | GAS | SOUTH | 2014 | 186.1
FERGUSON REPLACEMENT STG | 13INR0021 | FERGCC_FERGST1 | LLANO | GAS | SOUTH | 2014 | 194.9
FORNEY ENERGY CENTER CTG 11 | 01INR0007 | FRNYPP_GT11 | KAUFMAN | GAS | NORTH | 2003 | 191
FORNEY ENERGY CENTER CTG 12 | 01INR0007 | FRNYPP_GT12 | KAUFMAN | GAS | NORTH | 2003 | 183
FORNEY ENERGY CENTER CTG 13 | 01INR0007 | FRNYPP_GT13 | KAUFMAN | GAS | NORTH | 2003 | 183
FORNEY ENERGY CENTER CTG 21 | 01INR0007 | FRNYPP_GT21 | KAUFMAN | GAS | NORTH | 2003 | 191
FORNEY ENERGY CENTER CTG 22 | 01INR0007 | FRNYPP_GT22 | KAUFMAN | GAS | NORTH | 2003 | 183
FORNEY ENERGY CENTER CTG 23 | 01INR0007 | FRNYPP_GT23 | KAUFMAN | GAS | NORTH | 2003 | 183
FORNEY ENERGY CENTER STG 10 | 01INR0007 | FRNYPP_ST10 | KAUFMAN | GAS | NORTH | 2003 | 417
FORNEY ENERGY CENTER STG 20 | 01INR0007 | FRNYPP_ST20 | KAUFMAN | GAS | NORTH | 2003 | 417
FREESTONE ENERGY CENTER CTG 1 | 01INR0009 | FREC_GT1 | FREESTONE | GAS | NORTH | 2002 | 160.7
FREESTONE ENERGY CENTER CTG 2 | 01INR0009 | FREC_GT2 | FREESTONE | GAS | NORTH | 2002 | 160.7
FREESTONE ENERGY CENTER STG 3 | 01INR0009 | FREC_ST3 | FREESTONE | GAS | NORTH | 2002 | 179.8
FREESTONE ENERGY CENTER CTG 4 | 01INR0009 | FREC_GT4 | FREESTONE | GAS | NORTH | 2002 | 161.1
FREESTONE ENERGY CENTER CTG 5 | 01INR0009 | FREC_GT5 | FREESTONE | GAS | NORTH | 2002 | 161.1
FREESTONE ENERGY CENTER STG 6 | 01INR0009 | FREC_ST6 | FREESTONE | GAS | NORTH | 2002 | 179.7
GUADALUPE GEN STN CTG 1 | 01INR0004 | GUADG_GAS1 | GUADALUPE | GAS | SOUTH | 2000 | 167
GUADALUPE GEN STN CTG 2 | 01INR0004 | GUADG_GAS2 | GUADALUPE | GAS | SOUTH | 2000 | 167
GUADALUPE GEN STN CTG 3 | 01INR0004 | GUADG_GAS3 | GUADALUPE | GAS | SOUTH | 2000 | 167
GUADALUPE GEN STN CTG 4 | 01INR0004 | GUADG_GAS4 | GUADALUPE | GAS | SOUTH | 2000 | 167
GUADALUPE GEN STN STG 5 | 01INR0004 | GUADG_STM5 | GUADALUPE | GAS | SOUTH | 2000 | 203
GUADALUPE GEN STN STG 6 | 01INR0004 | GUADG_STM6 | GUADALUPE | GAS | SOUTH | 2000 | 203
HAYS ENERGY FACILITY CSG 1 | 01INR0003 | HAYSEN_HAYSENG1 | HAYS | GAS | SOUTH | 2002 | 237
HAYS ENERGY FACILITY CSG 2 | 01INR0003 | HAYSEN_HAYSENG2 | HAYS | GAS | SOUTH | 2002 | 237
HAYS ENERGY FACILITY CSG 3 | 01INR0003 | HAYSEN_HAYSENG3 | HAYS | GAS | SOUTH | 2002 | 247
HAYS ENERGY FACILITY CSG 4 | 01INR0003 | HAYSEN_HAYSENG4 | HAYS | GAS | SOUTH | 2002 | 247
HIDALGO CTG 1 | 00INR0006 | DUKE_DUKE_GT1 | HIDALGO | GAS | SOUTH | 2000 | 150
HIDALGO CTG 2 | 00INR0006 | DUKE_DUKE_GT2 | HIDALGO | GAS | SOUTH | 2000 | 150
HIDALGO STG | 00INR0006 | DUKE_DUKE_ST1 | HIDALGO | GAS | SOUTH | 2000 | 176
JACK COUNTY GEN FACILITY CTG 1 | 05INR0010 | JACKCNTY_CT1 | JACK | GAS | NORTH | 2005 | 165
JACK COUNTY GEN FACILITY CTG 2 | 05INR0010 | JACKCNTY_CT2 | JACK | GAS | NORTH | 2005 | 165
JACK COUNTY GEN FACILITY STG 1 | 05INR0010 | JACKCNTY_STG | JACK | GAS | NORTH | 2005 | 310
JACK COUNTY GEN FACILITY CTG 3 | 10INR0010 | JCKCNTY2_CT3 | JACK | GAS | NORTH | 2011 | 165
JACK COUNTY GEN FACILITY CTG 4 | 10INR0010 | JCKCNTY2_CT4 | JACK | GAS | NORTH | 2011 | 165
JACK COUNTY GEN FACILITY STG 2 | 10INR0010 | JCKCNTY2_ST2 | JACK | GAS | NORTH | 2011 | 310
JOHNSON COUNTY GEN FACILITY CTG |  | TEN_CT1 | JOHNSON | GAS | NORTH | 1997 | 177
JOHNSON COUNTY GEN FACILITY STG |  | TEN_STG | JOHNSON | GAS | NORTH | 1997 | 106
LAMAR POWER PROJECT CTG 11 | 00INR0008 | LPCCS_CT11 | LAMAR | GAS | NORTH | 2000 | 186
LAMAR POWER PROJECT CTG 12 | 00INR0008 | LPCCS_CT12 | LAMAR | GAS | NORTH | 2000 | 176
LAMAR POWER PROJECT CTG 21 | 00INR0008 | LPCCS_CT21 | LAMAR | GAS | NORTH | 2000 | 176
LAMAR POWER PROJECT CTG 22 | 00INR0008 | LPCCS_CT22 | LAMAR | GAS | NORTH | 2000 | 186
LAMAR POWER PROJECT STG 1 | 00INR0008 | LPCCS_UNIT1 | LAMAR | GAS | NORTH | 2000 | 204
LAMAR POWER PROJECT STG 2 | 00INR0008 | LPCCS_UNIT2 | LAMAR | GAS | NORTH | 2000 | 204
LOST PINES CTG 1 | 02INR0005 | LOSTPI_LOSTPGT1 | BASTROP | GAS | SOUTH | 2001 | 183
LOST PINES CTG 2 | 02INR0005 | LOSTPI_LOSTPGT2 | BASTROP | GAS | SOUTH | 2001 | 183
LOST PINES STG | 02INR0005 | LOSTPI_LOSTPST1 | BASTROP | GAS | SOUTH | 2001 | 192
MAGIC VALLEY CTG 1 | 00INR0009 | NEDIN_NEDIN_G1 | HIDALGO | GAS | SOUTH | 2001 | 218.6
MAGIC VALLEY CTG 2 | 00INR0009 | NEDIN_NEDIN_G2 | HIDALGO | GAS | SOUTH | 2001 | 218.6
MAGIC VALLEY STG | 00INR0009 | NEDIN_NEDIN_G3 | HIDALGO | GAS | SOUTH | 2001 | 257.9
MIDLOTHIAN CS 1 | 00INR0012 | MDANP_CT1 | ELLIS | GAS | NORTH | 2001 | 240
MIDLOTHIAN CS 2 | 00INR0012 | MDANP_CT2 | ELLIS | GAS | NORTH | 2001 | 240
MIDLOTHIAN CS 3 | 00INR0012 | MDANP_CT3 | ELLIS | GAS | NORTH | 2001 | 240
MIDLOTHIAN CS 4 | 00INR0012 | MDANP_CT4 | ELLIS | GAS | NORTH | 2001 | 240
MIDLOTHIAN CS 5 | 02INR0008 | MDANP_CT5 | ELLIS | GAS | NORTH | 2002 | 257
MIDLOTHIAN CS 6 | 02INR0008 | MDANP_CT6 | ELLIS | GAS | NORTH | 2002 | 257
NUECES BAY CTG 8 | 09INR0039 | NUECES_B_NUECESG8 | NUECES | GAS | SOUTH | 2010 | 165
NUECES BAY CTG 9 | 09INR0039 | NUECES_B_NUECESG9 | NUECES | GAS | SOUTH | 2010 | 165
NUECES BAY STG 7 |  | NUECES_B_NUECESG7 | NUECES | GAS | SOUTH | 1972 | 320
ODESSA-ECTOR GEN STN CTG 11 | 01INR0026 | OECCS_CT11 | ECTOR | GAS | WEST | 2001 | 162.6
ODESSA-ECTOR GEN STN CTG 12 | 01INR0026 | OECCS_CT12 | ECTOR | GAS | WEST | 2001 | 151.2
ODESSA-ECTOR GEN STN CTG 21 | 01INR0026 | OECCS_CT21 | ECTOR | GAS | WEST | 2001 | 155.8
ODESSA-ECTOR GEN STN CTG 22 | 01INR0026 | OECCS_CT22 | ECTOR | GAS | WEST | 2001 | 153.3
ODESSA-ECTOR GEN STN STG 1 | 01INR0026 | OECCS_UNIT1 | ECTOR | GAS | WEST | 2001 | 216
ODESSA-ECTOR GEN STN STG 2 | 01INR0026 | OECCS_UNIT2 | ECTOR | GAS | WEST | 2001 | 216
PANDA SHERMAN CTG1 | 10INR0021 | PANDA_S_SHER1CT1 | GRAYSON | GAS | NORTH | 2014 | 202
PANDA SHERMAN CTG2 | 10INR0021 | PANDA_S_SHER1CT2 | GRAYSON | GAS | NORTH | 2014 | 202
PANDA SHERMAN STG | 10INR0021 | PANDA_S_SHER1ST1 | GRAYSON | GAS | NORTH | 2014 | 336
PANDA TEMPLE CTG1 | 10INR0020a | PANDA_T1_TMPL1CT1 | BELL | GAS | NORTH | 2014 | 218.5
PANDA TEMPLE CTG2 | 10INR0020a | PANDA_T1_TMPL1CT2 | BELL | GAS | NORTH | 2014 | 218.5
PANDA TEMPLE STG | 10INR0020a | PANDA_T1_TMPL1ST1 | BELL | GAS | NORTH | 2014 | 333.6
PARIS ENERGY CENTER CTG 1 |  | TNSKA_GT1 | LAMAR | GAS | NORTH | 1989 | 87
PARIS ENERGY CENTER CTG 2 |  | TNSKA_GT2 | LAMAR | GAS | NORTH | 1989 | 87
PARIS ENERGY CENTER STG |  | TNSKA_STG | LAMAR | GAS | NORTH | 1990 | 89
PASGEN CTG 2 |  | PSG_PSG_GT2 | HARRIS | GAS | HOUSTON | 2000 | 176
PASGEN CTG 3 |  | PSG_PSG_GT3 | HARRIS | GAS | HOUSTON | 2000 | 176
PASGEN STG 2 |  | PSG_PSG_ST2 | HARRIS | GAS | HOUSTON | 2000 | 169
QUAIL RUN ENERGY CTG 1 | 06INR0036 | QALSW_GT2 | ECTOR | GAS | WEST | 2007 | 86
QUAIL RUN ENERGY CTG 2 | 06INR0036 | QALSW_GT3 | ECTOR | GAS | WEST | 2008 | 81
QUAIL RUN ENERGY CTG 3 | 06INR0036 | QALSW_STG1 | ECTOR | GAS | WEST | 2007 | 98
QUAIL RUN ENERGY CTG 4 | 06INR0036 | QALSW_STG2 | ECTOR | GAS | WEST | 2008 | 98
QUAIL RUN ENERGY STG 1 | 06INR0036 | QALSW_GT1 | ECTOR | GAS | WEST | 2007 | 84
QUAIL RUN ENERGY STG 2 | 06INR0036 | QALSW_GT4 | ECTOR | GAS | WEST | 2008 | 81
SAM RAYBURN CTG 7 | 03INR0014 | RAYBURN_RAYBURG7 | VICTORIA | GAS | SOUTH | 2003 | 50
RIO NOGALES CTG 1 | 02INR0001 | RIONOG_CT1 | GUADALUPE | GAS | SOUTH | 2002 | 175
RIO NOGALES CTG 2 | 02INR0001 | RIONOG_CT2 | GUADALUPE | GAS | SOUTH | 2002 | 175
RIO NOGALES CTG 3 | 02INR0001 | RIONOG_CT3 | GUADALUPE | GAS | SOUTH | 2002 | 175
RIO NOGALES STG 4 | 02INR0001 | RIONOG_ST1 | GUADALUPE | GAS | SOUTH | 2002 | 323
SAM RAYBURN CTG 8 | 03INR0014 | RAYBURN_RAYBURG8 | VICTORIA | GAS | SOUTH | 2003 | 51
SAM RAYBURN CTG 9 | 03INR0014 | RAYBURN_RAYBURG9 | VICTORIA | GAS | SOUTH | 2003 | 50
SAM RAYBURN STG 10 | 03INR0014 | RAYBURN_RAYBURG10 | VICTORIA | GAS | SOUTH | 2003 | 40
SANDHILL ENERGY CENTER CTG 5A | 03INR0033 | SANDHSYD_SH_5A | TRAVIS | GAS | SOUTH | 2004 | 170
SANDHILL ENERGY CENTER STG 5C | 03INR0033 | SANDHSYD_SH_5C | TRAVIS | GAS | SOUTH | 2004 | 160
SILAS RAY STG 6 |  | SILASRAY_SILAS_6 | CAMERON | GAS | SOUTH | 1962 | 21
SILAS RAY CTG 9 |  | SILASRAY_SILAS_9 | CAMERON | GAS | SOUTH | 1996 | 49
T H WHARTON CTG 31 |  | THW_THWGT31 | HARRIS | GAS | HOUSTON | 1972 | 57
T H WHARTON CTG 32 |  | THW_THWGT32 | HARRIS | GAS | HOUSTON | 1972 | 57
T H WHARTON CTG 33 |  | THW_THWGT33 | HARRIS | GAS | HOUSTON | 1972 | 57
T H WHARTON CTG 34 |  | THW_THWGT34 | HARRIS | GAS | HOUSTON | 1972 | 57
T H WHARTON STG 3 |  | THW_THWST_3 | HARRIS | GAS | HOUSTON | 1974 | 104
T H WHARTON CTG 41 |  | THW_THWGT41 | HARRIS | GAS | HOUSTON | 1972 | 57
T H WHARTON CTG 42 |  | THW_THWGT42 | HARRIS | GAS | HOUSTON | 1972 | 57
T H WHARTON CTG 43 |  | THW_THWGT43 | HARRIS | GAS | HOUSTON | 1974 | 57
T H WHARTON CTG 44 |  | THW_THWGT44 | HARRIS | GAS | HOUSTON | 1974 | 57
T H WHARTON STG 4 |  | THW_THWST_4 | HARRIS | GAS | HOUSTON | 1974 | 104
TEXAS CITY CTG A |  | TXCTY_CTA | GALVESTON | GAS | HOUSTON | 2000 | 102.4
TEXAS CITY CTG B |  | TXCTY_CTB | GALVESTON | GAS | HOUSTON | 2000 | 102.4
TEXAS CITY CTG C |  | TXCTY_CTC | GALVESTON | GAS | HOUSTON | 2000 | 102.4
TEXAS CITY STG |  | TXCTY_ST | GALVESTON | GAS | HOUSTON | 2000 | 131.5
VICTORIA POWER STATION CTG 6 | 08INR0050 | VICTORIA_VICTORG6 | VICTORIA | GAS | SOUTH | 2009 | 168
VICTORIA POWER STATION STG 5 | 08INR0050 | VICTORIA_VICTORG5 | VICTORIA | GAS | SOUTH | 1963 | 132
WICHITA FALLS CTG 1 |  | WFCOGEN_UNIT1 | WICHITA | GAS | WEST | 1987 | 21
WICHITA FALLS CTG 2 |  | WFCOGEN_UNIT2 | WICHITA | GAS | WEST | 1987 | 21
WICHITA FALLS CTG 3 |  | WFCOGEN_UNIT3 | WICHITA | GAS | WEST | 1987 | 21
WICHITA FALLS STG 4 |  | WFCOGEN_UNIT4 | WICHITA | GAS | WEST | 1987 | 16
WISE-TRACTEBEL POWER CTG 1 | 02INR0009 | WCPP_CT1 | WISE | GAS | NORTH | 2004 | 275
WISE-TRACTEBEL POWER CTG 2 | 02INR0009 | WCPP_CT2 | WISE | GAS | NORTH | 2004 | 275
WISE-TRACTEBEL POWER STG 1 | 02INR0009 | WCPP_ST1 | WISE | GAS | NORTH | 2004 | 290
WOLF HOLLOW POWER CTG 1 | 01INR0015 | WHCCS_CT1 | HOOD | GAS | NORTH | 2002 | 249
WOLF HOLLOW POWER CTG 2 | 01INR0015 | WHCCS_CT2 | HOOD | GAS | NORTH | 2002 | 249
WOLF HOLLOW POWER STG | 01INR0015 | WHCCS_STG | HOOD | GAS | NORTH | 2002 | 293
ATKINS 7 |  | ATKINS_ATKINSG7 | BRAZOS | GAS | NORTH | 1973 | 20
DANSBY CTG 2 |  | DANSBY_DANSBYG2 | BRAZOS | GAS | NORTH | 2004 | 48
DANSBY CTG 3 | 09INR0072 | DANSBY_DANSBYG3 | BRAZOS | GAS | NORTH | 2010 | 50
DECKER CREEK CTG 1 |  | DECKER_DPGT_1 | TRAVIS | GAS | SOUTH | 1989 | 54
DECKER CREEK CTG 2 |  | DECKER_DPGT_2 | TRAVIS | GAS | SOUTH | 1989 | 54
DECKER CREEK CTG 3 |  | DECKER_DPGT_3 | TRAVIS | GAS | SOUTH | 1989 | 54
DECKER CREEK CTG 4 |  | DECKER_DPGT_4 | TRAVIS | GAS | SOUTH | 1989 | 54
DECORDOVA CTG 1 |  | DCSES_CT10 | HOOD | GAS | NORTH | 1990 | 80
DECORDOVA CTG 2 |  | DCSES_CT20 | HOOD | GAS | NORTH | 1990 | 79
DECORDOVA CTG 3 |  | DCSES_CT30 | HOOD | GAS | NORTH | 1990 | 78
DECORDOVA CTG 4 |  | DCSES_CT40 | HOOD | GAS | NORTH | 1990 | 77
EXTEX LAPORTE GEN STN CTG 1 | 01INR0044 | AZ_AZ_G1 | HARRIS | GAS | HOUSTON | 2009 | 45
EXTEX LAPORTE GEN STN CTG 2 | 01INR0044 | AZ_AZ_G2 | HARRIS | GAS | HOUSTON | 2009 | 45
EXTEX LAPORTE GEN STN CTG 3 | 01INR0044 | AZ_AZ_G3 | HARRIS | GAS | HOUSTON | 2009 | 45
EXTEX LAPORTE GEN STN CTG 4 | 01INR0044 | AZ_AZ_G4 | HARRIS | GAS | HOUSTON | 2009 | 45
GREENS BAYOU CTG 73 |  | GBY_GBYGT73 | HARRIS | GAS | HOUSTON | 1976 | 54
GREENS BAYOU CTG 74 |  | GBY_GBYGT74 | HARRIS | GAS | HOUSTON | 1976 | 54
GREENS BAYOU CTG 81 |  | GBY_GBYGT81 | HARRIS | GAS | HOUSTON | 1976 | 54
GREENS BAYOU CTG 83 |  | GBY_GBYGT83 | HARRIS | GAS | HOUSTON | 1976 | 64
GREENS BAYOU CTG 84 |  | GBY_GBYGT84 | HARRIS | GAS | HOUSTON | 1976 | 54
GREENVILLE ENGINE PLANT | 10INR0070 | STEAM_ENGINE_1 | HUNT | GAS | NORTH | 2010 | 8.4
GREENVILLE ENGINE PLANT | 10INR0070 | STEAM_ENGINE_2 | HUNT | GAS | NORTH | 2010 | 8.4
GREENVILLE ENGINE PLANT | 10INR0070 | STEAM_ENGINE_3 | HUNT | GAS | NORTH | 2010 | 8.4
LAREDO CTG 4 | 08INR0064 | LARDVFTN_G4 | WEBB | GAS | SOUTH | 2008 | 98.5
LAREDO CTG 5 | 08INR0064 | LARDVFTN_G5 | WEBB | GAS | SOUTH | 2008 | 98.5
LEON CREEK PEAKER CTG 1 | 04INR0009 | LEON_CRK_LCPCT1 | BEXAR | GAS | SOUTH | 2004 | 48
LEON CREEK PEAKER CTG 2 | 04INR0009 | LEON_CRK_LCPCT2 | BEXAR | GAS | SOUTH | 2004 | 48
LEON CREEK PEAKER CTG 3 | 04INR0009 | LEON_CRK_LCPCT3 | BEXAR | GAS | SOUTH | 2004 | 48
LEON CREEK PEAKER CTG 4 | 04INR0009 | LEON_CRK_LCPCT4 | BEXAR | GAS | SOUTH | 2004 | 48
MORGAN CREEK CTG 1 |  | MGSES_CT1 | MITCHELL | GAS | WEST | 1988 | 81
MORGAN CREEK CTG 2 |  | MGSES_CT2 | MITCHELL | GAS | WEST | 1988 | 81
MORGAN CREEK CTG 3 |  | MGSES_CT3 | MITCHELL | GAS | WEST | 1988 | 81
MORGAN CREEK CTG 4 |  | MGSES_CT4 | MITCHELL | GAS | WEST | 1988 | 81
MORGAN CREEK CTG 5 |  | MGSES_CT5 | MITCHELL | GAS | WEST | 1988 | 81
MORGAN CREEK CTG 6 |  | MGSES_CT6 | MITCHELL | GAS | WEST | 1988 | 81
PEARSALL IC ENGINE PLANT A | 09INR0079a | PEARSAL2_AGR_A | FRIO | GAS | SOUTH | 2012 | 50.6
PEARSALL IC ENGINE PLANT B | 09INR0079a | PEARSAL2_AGR_B | FRIO | GAS | SOUTH | 2012 | 50.6
PEARSALL IC ENGINE PLANT C | 09INR0079b | PEARSAL2_AGR_C | FRIO | GAS | SOUTH | 2012 | 50.6
PEARSALL IC ENGINE PLANT D | 09INR0079b | PEARSAL2_AGR_D | FRIO | GAS | SOUTH | 2012 | 50.6
PERMIAN BASIN CTG 1 |  | PB2SES_CT1 | WARD | GAS | WEST | 1988 | 71
PERMIAN BASIN CTG 2 |  | PB2SES_CT2 | WARD | GAS | WEST | 1988 | 71
PERMIAN BASIN CTG 3 |  | PB2SES_CT3 | WARD | GAS | WEST | 1988 | 74
PERMIAN BASIN CTG 4 |  | PB2SES_CT4 | WARD | GAS | WEST | 1990 | 75
PERMIAN BASIN CTG 5 |  | PB2SES_CT5 | WARD | GAS | WEST | 1990 | 75
R W MILLER CTG 4 |  | MIL_MILLERG4 | PALO PINTO | GAS | NORTH | 2000 | 115
R W MILLER CTG 5 |  | MIL_MILLERG5 | PALO PINTO | GAS | NORTH | 2000 | 115
RAY OLINGER CTG 4 | 00INR0024 | OLINGR_OLING_4 | COLLIN | GAS | NORTH | 2001 | 84
SAM RAYBURN CTG 1 |  | RAYBURN_RAYBURG1 | VICTORIA | GAS | SOUTH | 1963 | 13.5
SAM RAYBURN CTG 2 |  | RAYBURN_RAYBURG2 | VICTORIA | GAS | SOUTH | 1963 | 13.5
SAN JACINTO SES CTG 1 |  | SJS_SJS_G1 | HARRIS | GAS | HOUSTON | 1995 | 81
SAN JACINTO SES CTG 2 |  | SJS_SJS_G2 | HARRIS | GAS | HOUSTON | 1995 | 81
SANDHILL ENERGY CENTER CTG 1 | 01INR0041 | SANDHSYD_SH1 | TRAVIS | GAS | SOUTH | 2001 | 48
SANDHILL ENERGY CENTER CTG 2 | 01INR0041 | SANDHSYD_SH2 | TRAVIS | GAS | SOUTH | 2001 | 48
SANDHILL ENERGY CENTER CTG 3 | 01INR0041 | SANDHSYD_SH3 | TRAVIS | GAS | SOUTH | 2001 | 48
SANDHILL ENERGY CENTER CTG 4 | 01INR0041 | SANDHSYD_SH4 | TRAVIS | GAS | SOUTH | 2001 | 48
SANDHILL ENERGY CENTER CTG 6 | 09INR0045 | SANDHSYD_SH6 | TRAVIS | GAS | SOUTH | 2010 | 48
SANDHILL ENERGY CENTER CTG 7 | 09INR0045 | SANDHSYD_SH7 | TRAVIS | GAS | SOUTH | 2010 | 48
SILAS RAY CTG 10 | 04INR0014 | SILASRAY_SILAS_10 | CAMERON | GAS | SOUTH | 2004 | 46
T H WHARTON CTG 51 |  | THW_THWGT51 | HARRIS | GAS | HOUSTON | 1975 | 57
T H WHARTON CTG 52 |  | THW_THWGT52 | HARRIS | GAS | HOUSTON | 1975 | 57
T H WHARTON CTG 53 |  | THW_THWGT53 | HARRIS | GAS | HOUSTON | 1975 | 57
T H WHARTON CTG 54 |  | THW_THWGT54 | HARRIS | GAS | HOUSTON | 1975 | 57
T H WHARTON CTG 55 |  | THW_THWGT55 | HARRIS | GAS | HOUSTON | 1975 | 57
T H WHARTON CTG 56 |  | THW_THWGT56 | HARRIS | GAS | HOUSTON | 1975 | 57
T H WHARTON CTG G1 |  | THW_THWGT_1 | HARRIS | GAS | HOUSTON | 1967 | 13
TEXAS GULF SULPHUR |  | TGF_TGFGT_1 | WHARTON | GAS | HOUSTON | 1985 | 89
V H BRAUNIG CTG 5 | 09INR0028 | BRAUNIG_VHB6CT5 | BEXAR | GAS | SOUTH | 2009 | 48
V H BRAUNIG CTG 6 | 09INR0028 | BRAUNIG_VHB6CT6 | BEXAR | GAS | SOUTH | 2009 | 48
V H BRAUNIG CTG 7 | 09INR0028 | BRAUNIG_VHB6CT7 | BEXAR | GAS | SOUTH | 2009 | 48
V H BRAUNIG CTG 8 | 09INR0028 | BRAUNIG_VHB6CT8 | BEXAR | GAS | SOUTH | 2009 | 48
W A PARISH CTG 1 |  | WAP_WAPGT_1 | FT. BEND | GAS | HOUSTON | 1967 | 13
W A PARISH - PETRA NOVA CTG | 12INR0086 | PNPI_GT2 | FORT BEND | GAS | HOUSTON | 2013 | 88
WINCHESTER POWER PARK CTG 1 | 09INR0027 | WIPOPA_WPP_G1 | FAYETTE | GAS | SOUTH | 2009 | 46
WINCHESTER POWER PARK CTG 2 | 09INR0027 | WIPOPA_WPP_G2 | FAYETTE | GAS | SOUTH | 2009 | 46
WINCHESTER POWER PARK CTG 3 | 09INR0027 | WIPOPA_WPP_G3 | FAYETTE | GAS | SOUTH | 2009 | 46
WINCHESTER POWER PARK CTG 4 | 09INR0027 | WIPOPA_WPP_G4 | FAYETTE | GAS | SOUTH | 2009 | 46
B M DAVIS STG U1 |  | B_DAVIS_B_DAVIG1 | NUECES | GAS | SOUTH | 1974 | 335
CEDAR BAYOU STG U1 |  | CBY_CBY_G1 | CHAMBERS | GAS | HOUSTON | 1970 | 745
CEDAR BAYOU STG U2 |  | CBY_CBY_G2 | CHAMBERS | GAS | HOUSTON | 1972 | 749
DANSBY STG U1 |  | DANSBY_DANSBYG1 | BRAZOS | GAS | NORTH | 1978 | 110
DECKER CREEK STG U1 |  | DECKER_DPG1 | TRAVIS | GAS | SOUTH | 1971 | 320
DECKER CREEK STG U2 |  | DECKER_DPG2 | TRAVIS | GAS | SOUTH | 1978 | 428
GRAHAM STG U1 |  | GRSES_UNIT1 | YOUNG | GAS | WEST | 1960 | 225
GRAHAM STG U2 |  | GRSES_UNIT2 | YOUNG | GAS | WEST | 1969 | 390
GREENS BAYOU STG U5 |  | GBY_GBY_5 | HARRIS | GAS | HOUSTON | 1973 | 371
HANDLEY STG U3 |  | HLSES_UNIT3 | TARRANT | GAS | NORTH | 1963 | 395
HANDLEY STG U4 |  | HLSES_UNIT4 | TARRANT | GAS | NORTH | 1976 | 435
HANDLEY STG U5 |  | HLSES_UNIT5 | TARRANT | GAS | NORTH | 1977 | 435
LAKE HUBBARD STG U1 |  | LHSES_UNIT1 | DALLAS | GAS | NORTH | 1970 | 392
LAKE HUBBARD STG U2 |  | LHSES_UNIT2A | DALLAS | GAS | NORTH | 1973 | 515
MOUNTAIN CREEK STG U6 |  | MCSES_UNIT6 | DALLAS | GAS | NORTH | 1956 | 122
MOUNTAIN CREEK STG U7 |  | MCSES_UNIT7 | DALLAS | GAS | NORTH | 1958 | 118
MOUNTAIN CREEK STG U8 |  | MCSES_UNIT8 | DALLAS | GAS | NORTH | 1967 | 568
O W SOMMERS STG U1 |  | CALAVERS_OWS1 | BEXAR | GAS | SOUTH | 1972 | 420
O W SOMMERS STG U2 |  | CALAVERS_OWS2 | BEXAR | GAS | SOUTH | 1974 | 420
PEARSALL STG U1 |  | PEARSALL_PEARS_1 | FRIO | GAS | SOUTH | 1961 | 25
PEARSALL STG U2 |  | PEARSALL_PEARS_2 | FRIO | GAS | SOUTH | 1961 | 25
PEARSALL STG U3 |  | PEARSALL_PEARS_3 | FRIO | GAS | SOUTH | 1961 | 25
POWERLANE PLANT STG U1 |  | STEAM1A_STEAM_1 | HUNT | GAS | NORTH | 1966 | 20
POWERLANE PLANT STG U2 |  | STEAM_STEAM_2 | HUNT | GAS | NORTH | 1967 | 26
POWERLANE PLANT STG U3 |  | STEAM_STEAM_3 | HUNT | GAS | NORTH | 1978 | 41
R W MILLER STG U1 |  | MIL_MILLERG1 | PALO PINTO | GAS | NORTH | 2000 | 75
R W MILLER STG U2 |  | MIL_MILLERG2 | PALO PINTO | GAS | NORTH | 2000 | 120
R W MILLER STG U3 |  | MIL_MILLERG3 | PALO PINTO | GAS | NORTH | 2000 | 208
RAY OLINGER STG U1 |  | OLINGR_OLING_1 | COLLIN | GAS | NORTH | 1967 | 78
RAY OLINGER STG U2 |  | OLINGR_OLING_2 | COLLIN | GAS | NORTH | 1971 | 107
RAY OLINGER STG U3 |  | OLINGR_OLING_3 | COLLIN | GAS | NORTH | 1975 | 146
SIM GIDEON STG U1 |  | GIDEON_GIDEONG1 | BASTROP | GAS | SOUTH | 1965 | 130
SIM GIDEON STG U2 |  | GIDEON_GIDEONG2 | BASTROP | GAS | SOUTH | 1968 | 135
SIM GIDEON STG U3 |  | GIDEON_GIDEONG3 | BASTROP | GAS | SOUTH | 1972 | 340
SPENCER STG U4 |  | SPNCER_SPNCE_4 | DENTON | GAS | NORTH | 1966 | 61
SPENCER STG U5 |  | SPNCER_SPNCE_5 | DENTON | GAS | NORTH | 1973 | 61
STRYKER CREEK STG U1 |  | SCSES_UNIT1A | CHEROKEE | GAS | NORTH | 1958 | 167
STRYKER CREEK STG U2 |  | SCSES_UNIT2 | CHEROKEE | GAS | NORTH | 1965 | 502
TRINIDAD STG U6 |  | TRSES_UNIT6 | HENDERSON | GAS | NORTH | 1965 | 226
V H BRAUNIG STG U1 |  | BRAUNIG_VHB1 | BEXAR | GAS | SOUTH | 1966 | 220
V H BRAUNIG STG U2 |  | BRAUNIG_VHB2 | BEXAR | GAS | SOUTH | 1968 | 230
V H BRAUNIG STG U3 |  | BRAUNIG_VHB3 | BEXAR | GAS | SOUTH | 1970 | 412
W A PARISH STG U1 |  | WAP_WAP_G1 | FT. BEND | GAS | HOUSTON | 1958 | 169
W A PARISH STG U2 |  | WAP_WAP_G2 | FT. BEND | GAS | HOUSTON | 1958 | 169
W A PARISH STG U3 |  | WAP_WAP_G3 | FT. BEND | GAS | HOUSTON | 1961 | 258
W A PARISH STG U4 |  | WAP_WAP_G4 | FT. BEND | GAS | HOUSTON | 1968 | 552
NOTREES BATTERY | 12INR0076 | NWF_NBS | WINKLER/ECTOR | STORAGE | WEST | 2012 | 33.7
ACACIA SOLAR |  | ACACIA_UNIT_1 | PRESIDIO | SOLAR | WEST | 2012 | 10
BRACKETVILLE SOLAR - OCI ALAMO 4 | 14INR0024 | ECLIPSE_UNIT1 | KINNEY | SOLAR | SOUTH | 2014 | 37.6
OCI ALAMO 1 SOLAR | 13INR0058 | OCI_ALM1_UNIT1 | BEXAR | SOLAR | SOUTH | 2013 | 39.2
WEBBERVILLE SOLAR | 10INR0082 | WEBBER_S_WSP1 | TRAVIS | SOLAR | SOUTH | 2011 | 26.7
BLUE WING 1 |  | DG_BROOK_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.6
BLUE WING 2 |  | DG_ELMEN_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.3
SOMERSET 1 |  | DG_SOME1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5.6
SOMERSET 2 |  | DG_SOME2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5
SUNEDISON RABEL ROAD |  | DG_VALL1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9
SUNEDISON VALLEY ROAD |  | DG_VALL2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9
NACOGDOCHES POWER | 09INR0007 | NACPW_UNIT1 | NACOGDOCHES | BIOMASS | NORTH | 2012 | 105
LUFKIN BIOMASS | 08INR0033 | LFBIO_UNIT1 | ANGELINA | BIOMASS | NORTH | 2012 | 45
ALVIN |  | AV_DG1 | GALVESTON | BIOMASS | HOUSTON | 2002 | 6.7
AUSTIN LANDFILL GAS |  | DG_SPRIN_4UNITS | TRAVIS | BIOMASS | SOUTH | 2007 | 6.4
COVEL GARDENS POWER STATION |  | DG_MEDIN_1UNIT | BEXAR | BIOMASS | SOUTH | 2005 | 9.6
DFW GAS RECOVERY |  | DG_BIO2_4UNITS | DENTON | BIOMASS | NORTH | 2009 | 6.4
DG_BIOENERGY PARTNERS |  | DG_BIOE_2UNITS | DENTON | BIOMASS | NORTH | 1988 | 6.2
FW REGION GEN FACILITY |  | DG_RDLML_1UNIT | TARRANT | BIOMASS | NORTH | 2011 | 1.6
HUMBLE |  | HB_DG1 | HARRIS | BIOMASS | HOUSTON | 2002 | 10
LIBERTY |  | LB_DG1 | HARRIS | BIOMASS | HOUSTON | 2002 | 3.9
MCKINNEY LANDFILL |  | DG_MKNSW_2UNITS | COLLIN | BIOMASS | NORTH | 2011 | 3.2
MESQUITE CREEK ENERGY |  | DG_FREIH_2UNITS | COMAL | BIOMASS | SOUTH | 2011 | 3.2
SKYLINE LANDFILL GAS |  | DG_FERIS_4_UNITS | DALLAS | BIOMASS | NORTH | 2007 | 6.4
TRINITY BAY |  | TRN_DG1 | CHAMBERS | BIOMASS | HOUSTON | 2002 | 3.9
TRINITY OAKS LFG |  | DG_KLBRG_1UNIT | DALLAS | BIOMASS | NORTH | 2011 | 3.2
WALZEM ROAD |  | DG_WALZE_4UNITS | BEXAR | BIOMASS | SOUTH | 2002 | 9.8
WESTSIDE |  | DG_WSTHL_3UNITS | PARKER | BIOMASS | NORTH | 2010 | 4.8
Operational Capacity Total (Coal, Gas, Nuclear, Biomass, Solar) | [6 empty] | 66557.5
Operational Resources (Hydro)
AMISTAD HYDRO 1 |  | AMISTAD_AMISTAG1 | VAL VERDE |  | SOUTH | 1983 | 37.9
AMISTAD HYDRO 2 |  | AMISTAD_AMISTAG2 | VAL VERDE |  | SOUTH | 1983 | 37.9
AUSTIN HYDRO 1 |  | AUSTPL_AUSTING1 | TRAVIS |  | SOUTH | 1940 | 8
AUSTIN HYDRO 2 |  | AUSTPL_AUSTING2 | TRAVIS |  | SOUTH | 1940 | 9
BUCHANAN HYDRO 1 |  | BUCHAN_BUCHANG1 | LLANO |  | SOUTH | 1938 | 16
BUCHANAN HYDRO 2 |  | BUCHAN_BUCHANG2 | LLANO |  | SOUTH | 1938 | 16
BUCHANAN HYDRO 3 |  | BUCHAN_BUCHANG3 | LLANO |  | SOUTH | 1950 | 17
DENISON DAM 1 |  | DNDAM_DENISOG1 | GRAYSON |  | NORTH | 1944 | 40
DENISON DAM 2 |  | DNDAM_DENISOG2 | GRAYSON |  | NORTH | 1948 | 40
FALCON HYDRO 1 |  | FALCON_FALCONG1 | STARR |  | SOUTH | 1954 | 12
FALCON HYDRO 2 |  | FALCON_FALCONG2 | STARR |  | SOUTH | 1954 | 12
FALCON HYDRO 3 |  | FALCON_FALCONG3 | STARR |  | SOUTH | 1954 | 12
GRANITE SHOALS HYDRO 1 |  | WIRTZ_WIRTZ_G1 | BURNET |  | SOUTH | 1951 | 29
GRANITE SHOALS HYDRO 2 |  | WIRTZ_WIRTZ_G2 | BURNET |  | SOUTH | 1951 | 29
INKS HYDRO 1 |  | INKSDA_INKS_G1 | LLANO |  | SOUTH | 1938 | 14
MARBLE FALLS HYDRO 1 |  | MARBFA_MARBFAG1 | BURNET |  | SOUTH | 1951 | 21
MARBLE FALLS HYDRO 2 |  | MARBFA_MARBFAG2 | BURNET |  | SOUTH | 1951 | 20
MARSHALL FORD HYDRO 1 |  | MARSFO_MARSFOG1 | TRAVIS |  | SOUTH | 1941 | 36
MARSHALL FORD HYDRO 2 |  | MARSFO_MARSFOG2 | TRAVIS |  | SOUTH | 1941 | 36
MARSHALL FORD HYDRO 3 |  | MARSFO_MARSFOG3 | TRAVIS |  | SOUTH | 1941 | 29
WHITNEY DAM HYDRO |  | WND_WHITNEY1 | BOSQUE |  | NORTH | 1953 | 20
WHITNEY DAM HYDRO 2 |  | WND_WHITNEY2 | BOSQUE |  | NORTH | 1953 | 15
CANYON |  | CANYHY_CANYHYG1 | COMAL |  | SOUTH | 1989 | 6
EAGLE PASS HYDRO |  | EAGLE_HY_EAGLE_HY1 | MAVERICK |  | SOUTH | 2005 | 9.6
LAKEWOOD TAP |  | DG_LKWDT_2UNITS | GONZALES |  | SOUTH | 1931 | 4.8
LEWISVILLE |  | DG_LWSVL_1UNIT | DENTON |  | NORTH | 1991 | 2.2
MCQUEENEY |  | DG_MCQUE_5UNITS | GUADALUPE |  | SOUTH | 1928 | 7.7
SCHUMANSVILLE |  | DG_SCHUM_2UNITS | GUADALUPE |  | SOUTH | 1928 | 3.6
Operational Capacity Total (Hydro) | [6 empty] | 540.7
Hydro Capacity Contribution (Top 20 Hours) |  | HYDRO_CAP_CONT |  | HYDRO |  |  | 63.6
Operational Capacity Total (Including Hydro) | [6 empty] | 66621.1
Private-Use Network Capacity Contribution (Top 20 Hours) |  | PUN_CAP_CONT |  | GAS |  |  | 4318
Wind Resources
ANACACHO WIND | 12INR0072 | ANACACHO_ANA | KINNEY | WIND | SOUTH | 2012 | 99.8
BARTON CHAPEL WIND | 06INR0021 | BRTSW_BCW1 | JACK | WIND | WEST | 2007 | 120
BLUE SUMMIT WIND 5 | 12INR0075 | BLSUMMIT_BLSMT1_5 | WILBARGER | WIND | WEST | 2013 | 9
BLUE SUMMIT WIND 6 | 12INR0075 | BLSUMMIT_BLSMT1_6 | WILBARGER | WIND | WEST | 2013 | 126.4
BOBCAT BLUFF WIND | 08INR0049 | BCATWIND_WIND_1 | ARCHER | WIND | NORTH | 2012 | 150
BUFFALO GAP WIND FARM 1 | 04INR0015 | BUFF_GAP_UNIT1 | TAYLOR | WIND | WEST | 2006 | 120.6
BUFFALO GAP WIND FARM 2_1 | 06INR0037 | BUFF_GAP_UNIT2_1 | TAYLOR | WIND | WEST | 2007 | 115.5
BUFFALO GAP WIND FARM 2_2 | 06INR0037 | BUFF_GAP_UNIT2_2 | TAYLOR | WIND | WEST | 2007 | 117
BUFFALO GAP WIND FARM 3 | 07INR0030 | BUFF_GAP_UNIT3 | TAYLOR | WIND | WEST | 2008 | 170.2
BULL CREEK WIND PLANT U1 | 07INR0037 | BULLCRK_WND1 | BORDEN | WIND | WEST | 2009 | 88
BULL CREEK WIND PLANT U2 | 07INR0037 | BULLCRK_WND2 | BORDEN | WIND | WEST | 2009 | 90
CALLAHAN WIND | 04INR0013 | CALLAHAN_WND1 | CALLAHAN | WIND | WEST | 2004 | 114
CAMP SPRINGS WIND 1 | 06INR0038 | CSEC_CSECG1 | SCURRY | WIND | WEST | 2007 | 130.5
CAMP SPRINGS WIND 2 | 07INR0040 | CSEC_CSECG2 | SCURRY | WIND | WEST | 2007 | 120
CAPRICORN RIDGE WIND 1 | 07INR0018 | CAPRIDGE_CR1 | STERLING | WIND | WEST | 2007 | 214.5
CAPRICORN RIDGE WIND 2 | 07INR0041 | CAPRIDGE_CR3 | STERLING | WIND | WEST | 2008 | 186
CAPRICORN RIDGE WIND 3 | 07INR0041 | CAPRIDGE_CR2 | STERLING | WIND | WEST | 2007 | 149.5
CAPRICORN RIDGE WIND 4 | 08INR0063 | CAPRIDG4_CR4 | COKE/STERLING | WIND | WEST | 2008 | 112.5
CEDRO HILL WIND 1 | 09INR0082 | CEDROHIL_CHW1 | WEBB | WIND | SOUTH | 2010 | 75
CEDRO HILL WIND 2 | 09INR0083 | CEDROHIL_CHW2 | WEBB | WIND | SOUTH | 2010 | 75
CHAMPION WIND FARM | 07INR0045d | CHAMPION_UNIT1 | NOLAN AND MITCHELL | WIND | WEST | 2008 | 126.5
DESERT SKY WIND FARM 1 |  | INDNENR_INDNENR | PECOS | WIND | WEST | 2002 | 84
DESERT SKY WIND FARM 2 |  | INDNENR_INDNENR_2 | PECOS | WIND | WEST | 2002 | 76.5
ELBOW CREEK WIND PROJECT | 08INR0053 | ELB_ELBCREEK | HOWARD | WIND | WEST | 2008 | 118.7
FOREST CREEK WIND FARM | 05INR0019 | MCDLD_FCW1 | GLASSCOCK | WIND | WEST | 2007 | 124.2
GOAT WIND | 07INR0028 | GOAT_GOATWIND | STERLING | WIND | WEST | 2008 | 80
GOAT WIND 2 | 07INR0028b | GOAT_GOATWIN2 | STERLING | WIND | WEST | 2010 | 69.6
GOLDTHWAITE WIND 1 | 11INR0013 | GWEC_GWEC_G1 | MILLS | WIND | NORTH | 2014 | 148.6
GREEN MOUNTAIN WIND (BRAZOS) U1 | 03INR0020 | BRAZ_WND_WND1 | SCURRY/BORDEN | WIND | WEST | 2003 | 99
GREEN MOUNTAIN WIND (BRAZOS) U2 | 03INR0020 | BRAZ_WND_WND2 | SCURRY/BORDEN | WIND | WEST | 2003 | 61
HACKBERRY WIND FARM | 04INR0011e | HWF_HWFG1 | SHACKELFORD | WIND | WEST | 2008 | 163.5
HORSE HOLLOW WIND 1 | 05INR0015 | H_HOLLOW_WND1 | TAYLOR | WIND | WEST | 2005 | 206.6
HORSE HOLLOW WIND 2 | 05INR0018 | HHOLLOW2_WIND1 | TAYLOR | WIND | WEST | 2006 | 184
HORSE HOLLOW WIND 3 | 06INR0040 | HHOLLOW3_WND_1 | TAYLOR | WIND | WEST | 2006 | 223.5
HORSE HOLLOW WIND 4 | 06INR0040 | HHOLLOW4_WND1 | TAYLOR | WIND | WEST | 2006 | 108
INADALE WIND | 07INR0045b | INDL_INADALE1 | NOLAN | WIND | WEST | 2008 | 196.6
INDIAN MESA WIND FARM | 00INR0022 | INDNNWP_INDNNWP | PECOS COUNTY | WIND | WEST | 2001 | 82.5
KING MOUNTAIN NE | 00INR0025 | KING_NE_KINGNE | UPTON | WIND | WEST | 2001 | 79.3
KING MOUNTAIN NW | 00INR0025 | KING_NW_KINGNW | UPTON | WIND | WEST | 2001 | 79.3
KING MOUNTAIN SE | 00INR0025 | KING_SE_KINGSE | UPTON | WIND | WEST | 2001 | 40.3
KING MOUNTAIN SW | 00INR0025 | KING_SW_KINGSW | UPTON | WIND | WEST | 2001 | 79.3
LANGFORD WIND POWER | 10INR0026 | LGD_LANGFORD | TOM GREEN | WIND | WEST | 2009 | 155
LONE STAR WIND 1 (MESQUITE) | 04INR0011 | LNCRK_G83 | SHACKELFORD | WIND | WEST | 2006 | 200
LONE STAR WIND 2 (POST OAK) U1 | 04INR0011a | LNCRK2_G871 | SHACKELFORD | WIND | WEST | 2007 | 100
LONE STAR WIND 2 (POST OAK) U2 | 04INR0011a | LNCRK2_G872 | SHACKELFORD | WIND | WEST | 2007 | 100
LORAINE WINDPARK I | 09INR0047 | LONEWOLF_G1 | MITCHELL | WIND | WEST | 2009 | 49.5
LORAINE WINDPARK II | 09INR0047 | LONEWOLF_G2 | MITCHELL | WIND | WEST | 2009 | 51
LORAINE WINDPARK III | 09INR0047 | LONEWOLF_G3 | MITCHELL | WIND | WEST | 2011 | 25.5
LORAINE WINDPARK IV | 09INR0047 | LONEWOLF_G4 | MITCHELL | WIND | WEST | 2011 | 24
MCADOO WIND FARM | 08INR0028 | MWEC_G1 | DICKENS | WIND | WEST | 2008 | 150
NOTREES WIND FARM 1 AND 3 | 07INR0005 | NWF_NWF1 | WINKLER/ECTOR | WIND | WEST | 2009 | 92.6
NOTREES WIND FARM 2 | 07INR0005 | NWF_NWF2 | WINKLER/ECTOR | WIND | WEST | 2009 | 60
OCOTILLO WIND FARM | 04INR0017 | OWF_OWF | HOWARD | WIND | WEST | 2008 | 58.8
PANHANDLE WIND 1 U1 | 14INR0030a_2 | PH1_UNIT1 | CARSON | WIND | PANHANDLE | 2014 | 109.2
PANHANDLE WIND 1 U2 | 14INR0030a_2 | PH1_UNIT2 | CARSON | WIND | PANHANDLE | 2014 | 109.2
PANTHER CREEK 1 | 07INR0022 | PC_NORTH_PANTHER1 | HOWARD | WIND | WEST | 2008 | 142.5
PANTHER CREEK 2 | 08INR0037 | PC_SOUTH_PANTHER2 | HOWARD | WIND | WEST | 2008 | 115.5
PANTHER CREEK 3 | 11INR0015 | PC_SOUTH_PANTHER3 | HOWARD | WIND | WEST | 2009 | 199.5
PECOS WIND (WOODWARD 1) | 01INR0035 | WOODWRD1_WOODWRD1 | PECOS | WIND | WEST | 2001 | 82.5
PECOS WIND (WOODWARD 2) | 01INR0035 | WOODWRD2_WOODWRD2 | PECOS | WIND | WEST | 2001 | 77.2
PYRON WIND FARM | 07INR0045a | PYR_PYRON1 | SCURRY AND FISHER | WIND | WEST | 2008 | 249
RED CANYON WIND | 05INR0017 | RDCANYON_RDCNY1 | BORDEN | WIND | WEST | 2006 | 84
ROSCOE WIND FARM | 07INR0045e | TKWSW1_ROSCOE | NOLAN | WIND | WEST | 2008 | 209
SAND BLUFF WIND FARM | 05INR0019 | MCDLD_SBW1 | GLASSCOCK | WIND | WEST | 2008 | 90
SENATE WIND PROJECT | 08INR0011 | SENATEWD_UNIT1 | JACK | WIND | WEST | 2012 | 150
SHERBINO I WIND | 06INR0012a | KEO_KEO_SM1 | PECOS | WIND | WEST | 2008 | 150
SHERBINO 2 WIND | 06INR0012b | KEO_SHRBINO2 | PECOS | WIND | WEST | 2011 | 150
SILVER STAR WIND | 03INR0034 | FLTCK_SSI | EASTLAND | WIND | NORTH | 2008 | 60
SNYDER WIND FARM | 04INR0020 | ENAS_ENA1 | SCURRY | WIND | WEST | 2007 | 63
SOUTH TRENT WIND FARM | 07INR0029 | STWF_T1 | NOLAN & TAYLOR | WIND | WEST | 2008 | 101.2
SPINNING SPUR WIND TWO | 13INR0048 | SSPURTWO_WIND_1 | OLDHAM | WIND | PANHANDLE | 2014 | 161
STANTON WIND ENERGY | 07INR0010 | SWEC_G1 | MARTIN | WIND | WEST | 2008 | 120
SWEETWATER WIND 1 | 01INR0036 | SWEETWND_WND1 | NOLAN | WIND | WEST | 2003 | 36.6
SWEETWATER WIND 2A | 01INR0036 | SWEETWN2_WND24 | NOLAN | WIND | WEST | 2006 | 15.9
SWEETWATER WIND 2B | 01INR0036 | SWEETWN2_WND2 | NOLAN | WIND | WEST | 2004 | 97.5
SWEETWATER WIND 3A | 01INR0036 | SWEETWN3_WND3A | NOLAN | WIND | WEST | 2011 | 28.5
SWEETWATER WIND 3B | 01INR0036 | SWEETWN3_WND3B | NOLAN | WIND | WEST | 2011 | 100.5
SWEETWATER WIND 4-5 | 07INR0023 | SWEETWN4_WND5 | NOLAN | WIND | WEST | 2007 | 79.2
SWEETWATER WIND 4-4B | 07INR0023 | SWEETWN4_WND4B | NOLAN | WIND | WEST | 2007 | 103.7
SWEETWATER WIND 4-4A | 07INR0023 | SWEETWN4_WND4A | NOLAN | WIND | WEST | 2007 | 117.8
TEXAS BIG SPRING WIND a |  | SGMTN_SIGNALMT | HOWARD | WIND | WEST | 1999 | 27.7
TEXAS BIG SPRING WIND b |  | SGMTN_SIGNALM2 | HOWARD | WIND | WEST | 1999 | 6.6
TRENT WIND FARM | 01INR0038 | TRENT_TRENT | NOLAN | WIND | WEST | 2001 | 150
TRINITY HILLS WIND 1 | 08INR0062 | TRINITY_TH1_BUS1 | YOUNG | WIND | NORTH | 2012 | 117.5
TRINITY HILLS WIND 2 | 08INR0062 | TRINITY_TH1_BUS2 | YOUNG | WIND | NORTH | 2012 | 107.5
TURKEY TRACK WIND ENERGY CENTER | 07INR0011 | TTWEC_G1 | NOLAN | WIND | WEST | 2008 | 169.5
WEST TEXAS WIND ENERGY |  | SW_MESA_SW_MESA | UPTON/CROCKETT COUNTIES | WIND | WEST | 1999 | 74.2
WHIRLWIND ENERGY | 07INR0003 | WEC_WECG1 | FLOYD | WIND | NORTH | 2007 | 57
WHITETAIL WIND ENERGY PROJECT | 11INR0091 | EXGNWTL_WIND_1 | WEBB AND DUVAL | WIND | SOUTH | 2012 | 90
WKN MOZART WIND | 09INR0061 | MOZART_WIND_1 | KENT & STONEWALL COUNTY | WIND | WEST | 2012 | 30
WOLF RIDGE WIND | 07INR0034 | WHTTAIL_WR1 | COOKE | WIND | NORTH | 2008 | 112.5
TSTC WEST TEXAS WIND |  | DG_ROSC2_1UNIT | NOLAN | WIND | WEST | 2008 | 2
Wind Capacity Total (Non-Coastal Counties) | [6 empty] | 9827.9
GULF WIND I | 05INR0015a | TGW_T1 | KENEDY | WIND | SOUTH | 2010 | 141.6
GULF WIND II | 05INR0015a | TGW_T2 | KENEDY | WIND | SOUTH | 2010 | 141.6
LOS VIENTOS WIND I | 11INR0033 | LV1_LV1A | WILLACY/CAMERON | WIND | SOUTH | 2013 | 200.1
LOS VIENTOS WIND II | 11INR0033 | LV1_LV1B | WILLACY/CAMERON | WIND | SOUTH | 2013 | 201.6
MAGIC VALLEY WIND (REDFISH) 1A | 10INR0060 | REDFISH_MV1A | WILLACY | WIND | SOUTH | 2012 | 99.8
MAGIC VALLEY WIND (REDFISH) 1B | 10INR0060 | REDFISH_MV1B | WILLACY | WIND | SOUTH | 2012 | 103.5
PAPALOTE CREEK WIND FARM | 08INR0012a | PAP1_PAP1 | SAN PATRICIO | WIND | SOUTH | 2009 | 179.9
PAPALOTE CREEK WIND FARM II | 08INR0012b | COTTON_PAP2 | SAN PATRICIO | WIND | SOUTH | 2010 | 200.1
PENASCAL WIND 1 | 06INR0022a | PENA_UNIT1 | KENEDY | WIND | SOUTH | 2009 | 160.8
PENASCAL WIND 2 | 06INR0022b | PENA_UNIT2 | KENEDY | WIND | SOUTH | 2009 | 141.6
PENASCAL WIND 3 | 06INR0022b | PENA3_UNIT3 | KENEDY | WIND | SOUTH | 2011 | 100.8
HARBOR WIND |  | DG_NUECE_6UNITS | NUECES | WIND | SOUTH | 2012 | 9
Wind Capacity Total (Coastal Counties) | [6 empty] | 1680.4
Wind Capacity Total Total | [6 empty] | 11508.3
Reliability Must-Run (RMR) Capacity |  | RMR_CAP_CONT |  | GAS |  |  | -0.001
DC-Tie Resources
EAGLE PASS TIE |  | DC_S | MAVERICK |  | SOUTH |  | 30
EAST TIE |  | DC_E | FANNIN |  | NORTH |  | 600
LAREDO VFT TIE |  | DC_L | WEBB |  | SOUTH |  | 100
NORTH TIE |  | DC_N | WILBARGER |  | WEST |  | 220
SHARYLAND RAILROAD TIE |  | DC_R | HIDALGO |  | SOUTH |  | 150
SHARYLAND RAILROAD TIE (FUTURE) |  | DC_R2 | HIDALGO |  | SOUTH |  | 20
DC-Ties Total | [6 empty] | 1120
DC-Ties Capacity Contribution (Top 20 Hours) |  | DCTIE_CAP_CONT |  | OTHER |  |  | 494.8
Switchable Resources
KIAMICHI ENERGY FACILITY 1CT101 | 03INR0012 | KMCHI_1CT101 | PITTSBURG | GAS | NORTH | 2003 | 178
KIAMICHI ENERGY FACILITY 1CT201 | 03INR0012 | KMCHI_1CT201 | PITTSBURG | GAS | NORTH | 2003 | 180
KIAMICHI ENERGY FACILITY 1ST | 03INR0012 | KMCHI_1ST | PITTSBURG | GAS | NORTH | 2003 | 307
KIAMICHI ENERGY FACILITY 2CT101 | 03INR0012 | KMCHI_2CT101 | PITTSBURG | GAS | NORTH | 2003 | 178
KIAMICHI ENERGY FACILITY 2CT201 | 03INR0012 | KMCHI_2CT201 | PITTSBURG | GAS | NORTH | 2003 | 180
KIAMICHI ENERGY FACILITY 2ST | 03INR0012 | KMCHI_2ST | PITTSBURG | GAS | NORTH | 2003 | 307
TENASKA-FRONTIER CTG 1 | 00PSR4 | FTR_FTR_G1 | GRIMES | GAS | HOUSTON | 2000 | 180
TENASKA-FRONTIER CTG 2 | 00PSR4 | FTR_FTR_G2 | GRIMES | GAS | HOUSTON | 2000 | 180
TENASKA-FRONTIER CTG 3 | 00PSR4 | FTR_FTR_G3 | GRIMES | GAS | HOUSTON | 2000 | 180
TENASKA-FRONTIER STG 4 | 00PSR4 | FTR_FTR_G4 | GRIMES | GAS | HOUSTON | 2000 | 400
TENASKA-GATEWAY CTG 1 | 01INR0019 | TGCCS_CT1 | RUSK | GAS | NORTH | 2001 | 162
TENASKA-GATEWAY CTG 2 | 01INR0019 | TGCCS_CT2 | RUSK | GAS | NORTH | 2001 | 179
TENASKA-GATEWAY CTG 3 | 01INR0019 | TGCCS_CT3 | RUSK | GAS | NORTH | 2001 | 178
TENASKA-GATEWAY STG 4 | 01INR0019 | TGCCS_UNIT4 | RUSK | GAS | NORTH | 2001 | 389
FRONTERA GENERATION CTG 1 |  | FRONTERA_FRONTEG1 | HIDALGO | GAS | SOUTH | 1999 | 170
FRONTERA GENERATION CTG 2 |  | FRONTERA_FRONTEG2 | HIDALGO | GAS | SOUTH | 1999 | 170
FRONTERA GENERATION STG |  | FRONTERA_FRONTEG3 | HIDALGO | GAS | SOUTH | 2000 | 184
Switchable Capacity Total | [6 empty] | 3702
Switchable Capacity Unavailable to ERCOT |  | SWITCH_UNAVAIL |  | GAS |  |  | -470
Available Mothball Capacity based on Owner's Return Probability |  | MOTH_AVAIL |  | GAS |  |  | 0
Planned Resources with Executed SGIA, Air Permit, GHG Permit and Water Rights
PECOS BARILLA SOLAR (HOVEY_UNIT1) | 12INR0059 |  | PECOS | SOLAR | WEST | 2014 | 30
Planned Capacity Total (Not Wind) | [6 empty] | 30
Planned Wind Resources with Executed SGIA
STEPHENS RANCH WIND 1 (SRWE1_UNIT1) | 12INR0034a |  | BORDEN | WIND | WEST | 2014 | 211
PANHANDLE WIND 2 (PH2_UNIT1-2) | 14INR0030b |  | CARSON | WIND | PANHANDLE | 2014 | 182
MIAMI WIND 1 (MIAM1_G1-2) | 14INR0012a |  | GRAY | WIND | PANHANDLE | 2014 | 289
GRANDVIEW (CONWAY) 1 (GRANDVW1_GV1A-B) | 13INR0005a | GRANDVW1_GV1A | CARSON | WIND | PANHANDLE | 2014 | 211
WINDTHORST 2 (WNDTHST2_UNIT1) | 13INR0057 |  | ARCHER | WIND | WEST | 2014 | 65
Planned Wind Capacity Total | [6 empty] | 958
Planned Wind Capacity Sub-total (Non-Coastal Counties) | [6 empty] | 958
Planned Wind Capacity Sub-total (Coastal Counties) | [6 empty] | 0
Mothballed Capacity
GREENS BAYOU CTG 82 |  | GBY_GBYGT82 | HARRIS | GAS | HOUSTON | 1976 | 58
NORTH TEXAS CTG 1 |  | NTX_NTX_1 | PARKER | GAS | NORTH | 1958 | 18
NORTH TEXAS CTG 2 |  | NTX_NTX_2 | PARKER | GAS | NORTH | 1958 | 18
NORTH TEXAS CTG 3 |  | NTX_NTX_3 | PARKER | GAS | NORTH | 1963 | 39
PERMIAN BASIN SES U6 |  | PBSES_UNIT6 | WARD | GAS | WEST | 1973 | 530
SILAS RAY CTG 5 |  | SILASRAY_SILAS_5 | CAMERON | GAS | SOUTH | 1953 | 10
VALLEY SES U1 |  | VLSES_UNIT1 | FANNIN | GAS | NORTH | 1962 | 174
VALLEY SES U2 |  | VLSES_UNIT2 | FANNIN | GAS | NORTH | 1967 | 520
VALLEY SES U3 |  | VLSES_UNIT3 | FANNIN | GAS | NORTH | 1971 | 375
S R BERTRON CTG 2 |  | SRB_SRBGT_2 | HARRIS | GAS | HOUSTON | 1967 | 13
S R BERTRON U1 |  | SRB_SRB_G1 | HARRIS | GAS | HOUSTON | 1958 | 118
S R BERTRON U2 |  | SRB_SRB_G2 | HARRIS | GAS | HOUSTON | 1956 | 174
S R BERTRON U3 |  | SRB_SRB_G3 | HARRIS | GAS | HOUSTON | 1959 | 211
S R BERTRON U4 |  | SRB_SRB_G4 | HARRIS | GAS | HOUSTON | 1960 | 211
Total Mothballed Capacity | [6 empty] | 2469
Seasonal Mothballed Capacity
MARTIN LAKE U3 |  | MLSES_UNIT3 | RUSK | COAL | NORTH | 1979 | 820
MONTICELLO U1 |  | MNSES_UNIT1 | TITUS | COAL | NORTH | 1974 | 580
MONTICELLO U2 |  | MNSES_UNIT2 | TITUS | COAL | NORTH | 1975 | 580
Total Seasonal Mothballed Capacity | [6 empty] | 1980
Retiring Capacity Unavailable to ERCOT
APPLIED ENERGY |  | APD_APD_G1 | HARRIS | COAL | HOUSTON | 1986 | 140
ATKINS CTG 3 |  | ATKINS_ATKINSG3 | BRAZOS | GAS | NORTH | 1954 | 12
ATKINS CTG 4 |  | ATKINS_ATKINSG4 | BRAZOS | GAS | NORTH | 1958 | 22
ATKINS CTG 5 |  | ATKINS_ATKINSG5 | BRAZOS | GAS | NORTH | 1965 | 25
ATKINS CTG 6 |  | ATKINS_ATKINSG6 | BRAZOS | GAS | NORTH | 1969 | 50
DELAWARE MOUNTAIN WIND FARM | 99INR0004 | KUNITZ_WIND_NWP | CULBERSON COUNTY | WIND | WEST | 1999 | 28.5
KUNITZ WIND - WINDPOWER PARTNERS 1994 |  | KUNITZ_WIND_LGE | CULBERSON COUNTY | WIND | WEST | 1995 | 39.8
Total Retiring Capacity Unavailable to ERCOT | [6 empty] | 317.3

## Background
Release Date: October 31, 2014
Seasonal Assessment of Resource Adequacy for the ERCOT Region Background The Seasonal Assessment of Resource Adequacy (SARA) report is a deterministic approach to considering the impact of potential variables that may affect the sufficiency of installed resources to meet the peak electrical demand on the ERCOT System during a particular season. The standard approach to assessing resource adequacy for one or more years into the future is to account for projected load and resources on a normalized basis and to require sufficient reserves (resources in excess of peak demand, on this normalized basis) to cover the uncertainty in peak demand and resource availability to meet a one-in-ten-years loss-of-load event criteria on a probabilistic basis. For seasonal assessments that look ahead less than a year, specific information may be available (such as seasonal climate forecasts or anticipated common-mode events such as drought) which can be used to consider the range of resource adequacy in a more deterministic manner. In contrast to the Capacity, Demand and Reserves (CDR) report, which addresses the sufficiency of planning reserves on an annual basis as described above, the SARA report focuses on the availability of sufficient operating reserves to avoid emergency actions such as deployment of voluntary load reduction resources. Consequently, load reduction resources included in the CDR report, such as Emergency Response Service (ERS) and Load Resources that provide operating reserves (LRs), are excluded from the SARA. The SARA report is intended to illustrate the range of resource adequacy outcomes that might occur, and thus help fulfill the reporting requirement per Public Utility Commission of Texas rule 25.362(i)(2)(H). Several sensitivity analyses are developed by varying the value of certain parameters that affect resource adequacy. The variation in these parameters is either based on historic values of these parameters, adjusted by any known or expected change.