## Sheet1
Requirement |  | Resource Registration Glossary | [10 empty] | Data Validation Rules
Groups that use data element | Purpose of data element | RARF Tab | Wind | Conventional Generation (Gen) | Combined Cycle (CC) | Load Resources | Notes | Field Name | Definition / Detailed Description | Screening Study (SS) (R, C, O, A) | Full Interconnect Study (FIS) (R, C, O, A) | Full Registration (R, C, O, A) | RARF DATA FIELD | Business Rules/Basic UI validations | Field/ Tab Type | Data type | Validation Type | Source | Destination Application | Required for Screening Study (SS) | Required for Full Interconnect Study (FIS) | Required for Planning
|  | Planning |  | X | X |  | List | Unit Name | Unit Code as provided on the Unit Info tab. |  | R | R | Unit Name | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS | N | Y
|  | Planning | X | X | X |  | Automatic | Resource Name (Unit Code/Mnemonic) | Concatenated mnemonic of Resource Site Code and Unit name (e.g. CBY_CBYG1). |  |  | A | Resource Name (Unit Code/Mnemonic) | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS | N | Y
| Goes into SSWG Case | Planning |  | X | X |  | MVA | What is the MVA base that the following data is based on? | The MVA Base for stated impedances. This must match the MVA Base used for the dynamic models. |  | R | R | What Is The Mva Base That The Following Data Is Based On? | 1) This field is required 2) Value must be Float 3) Generate a Warning if MVABASE > 2500 4)[ If MVABASE value is within +/- 25% range of Unit Name Plate Rating] OR [MVABASE value = 100, then it is OK.If MVABASE value is outside the +/- 25% range of Unit Name Plate Rating, then Generate a Warning that the MVABSE is outside the typical +/- 25% variation of unit name plate rating | R | Float | B | Planning Team |  | N | Y
|  | Planning |  | X | X |  | KV | What is the kV base that the following data is based on? | The KV Base for stated impedances. |  | R | R | What Is The Kv Base That The Following Data Is Based On? | 1) This field is required 2) Value must be >0 and <1000 3) Generate a Warning if KVBASE > 40 4) If KVBASE value is within +/- 25% range of Unit KV value in the unit-information tab then it is OK.If If KVBASE value is outside the typical +/- 25% variation of Unit KV value in the unit-information tab then Generate a Warning that the KVBASE is outside the typical +/- 25% variation of Unit KV value | R | Float | B,DVB | Planning Team |  | N | Y
|  | Planning |  | X | X |  | p.u. | Direct Axis Subtransient reactance, X"di (unsaturated) | Enter the direct axis subtransient reactance (unsaturated) for the fault. This must match data in the dynamic model. |  | R | R | Direct Axis Subtransient Reactance, X"di (unsaturated) | 1) This field is required and Data type is float 2) Value must be between 0.0 and 1.0 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) 4) Generate a Warning if X"di (unsaturated) < X"dv (saturated) | R | Float | B | Planning Team |  | N | Y
|  | Planning |  | X | X |  | p.u. | Direct Axis Transient reactance, X'di (unsaturated) | Enter the direct axis transient reactance (unsaturated) for the first 2-3 cycles of the fault. |  | R | R | Direct Axis Transient Reactance, X'di (unsaturated) | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) 4) Generate a Warning if X’di (unsaturated) < X’dv (saturated) | R | Float | B | Planning Team |  | N | Y
|  | Planning |  | X | X |  | R in p.u. | Positive Sequence (Synchronous) Z (unsaturated) | Enter the positive sequence resistance (unsaturated) for system models. |  | R | R | Positive Sequence Z (unsaturated) | 1) This field is required and Data type is float 2) Value must be between 0 and 1 |  |  |  | Planning Team |  | N | Y
|  | Planning |  | X | X |  | X in p.u. | Positive Sequence (Synchronous) Z (unsaturated) | Enter the positive sequence reactance (unsaturated) for system models. |  | R | R | Positive Sequence Z (unsaturated) | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) |  |  |  | Planning Team |  | N | Y
|  | Planning |  | X | X |  | R in p.u. | Negative Sequence Z (unsaturated) | Enter the negative sequence resistance (unsaturated) for system models. |  | R | R | Negative Sequence Z (unsaturated) | 1) This field is required and Data type is float 2) Value must be between 0 and 1 |  |  |  | Planning Team |  | N | Y
|  | Planning |  | X | X |  | X in p.u. | Negative Sequence Z (unsaturated) | Enter the negative sequence reactance (unsaturated) for system models. |  | R | R | Negative Sequence Z (unsaturated) | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] |  |  |  | Planning Team |  | N | Y
|  | Planning |  | X | X |  | Y/N | Does Zero Sequence Z exist? | Select whether the generator has Zero Sequence Z data. If no, then the zero sequence data fields will not be required. |  | R | R | Does Zero Sequence Z exist? | Drop down list select Y/N | R | Dropdown List |  | Planning Team |  | N | Y
|  | Planning |  | X | X |  | R in p.u. | Zero Sequence Z (unsaturated) | Enter the zero sequence resistance (unsaturated) for system models. |  | R | R | Zero Sequence Z (unsaturated) | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning ONLY when value is > 1.0 P.U |  |  |  | Planning Team |  | N | Y
|  | Planning |  | X | X |  | X in p.u. | Zero Sequence Z (unsaturated) | Enter the zero sequence reactance (unsaturated) for system models. |  | R | R | Zero Sequence Z (unsaturated) | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] |  |  |  | Planning Team |  | N | Y
|  | Planning |  | X | X |  | p.u. | Direct Axis Subtransient reactance, X"dvi (saturated) | Enter the direct axis subtransient reactance (saturated) for the fault. |  | R | R | Direct Axis Subtransient Reactance, X"dv (saturated) | 1) This field is required and Data type is float 2) Value must be between -1 and 1 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value.(* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team |  | N | Y
|  | Planning |  | X | X |  | p.u. | Direct Axis Transient reactance, X''dvi (saturated) | Enter the direct axis transient reactance (saturated) for the first 2-3 cycles of the fault. |  | R | R | Direct Axis Transient Reactance, X'dv (saturated) | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team |  | N | Y
|  | Planning |  | X | X |  | R in p.u. | Positive Sequence (Synchronous) Z (saturated) | Enter the positive sequence resistance (saturated) for system models. |  | R | R | Positive Sequence Z (saturated) | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | R | Float | B | Planning Team | NMMS | N | Y
|  | Planning |  | X | X |  | X in p.u. | Positive Sequence (Synchronous) Z (saturated) | Enter the positive sequence reactance (saturated) for system models. |  | R | R | Positive Sequence Z (saturated) | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | R | Float | B | Planning Team | NMMS | N | Y
|  | Planning |  | X | X |  | R in p.u. | Negative Sequence Z (saturated) | Enter the negative sequence resistance (saturated) for system models. |  | R | R | Negative Sequence Z (saturated) | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | R | Float | B | Planning Team |  | N | Y
|  | Planning |  | X | X |  | X in p.u. | Negative Sequence Z (saturated) | Enter the negative sequence reactance (saturated) for system models. |  | R | R | Negative Sequence Z (saturated) | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team |  | N | Y
|  | Planning |  | X | X |  | R in p.u. | Zero Sequence Z (saturated) | Enter the zero sequence resistance (saturated) for system models. |  | R | R | Zero Sequence Z (saturated) | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning ONLY when value is > 1.0 P.U | R | Float | B | Planning Team | NMMS | N | Y
|  | Planning |  | X | X |  | X in p.u. | Zero Sequence Z (saturated) | Enter the zero sequence reactance (saturated) for system models. |  | R | R | Zero Sequence Z (saturated) | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team | NMMS | N | Y
|  | Planning |  | X | X |  | p.u. | Zero Sequence Grounding Resistance For An Impedance Grounded Generator in p.u. (100 MVA Base) | Zero Sequence Grounding Resistance value of the Generator Grounding Inpedance is required. The value must be specified on a 100 MVA base. |  | R | R | Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 Value must be greater than or equal to 0.0 and less than or equal to 99999.0 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Model Adminstration |  | N | Y
|  | Planning |  | X | X |  | p.u. | Zero Sequence Grounding Reactance For An Impedance Grounded Generator in p.u. (100 MVA Base) | Zero Sequence Grounding Reactance value of the Generator Grounding Inpedance is required. The value must be specified on a 100 MVA base. |  | R | R | Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 Value must be greater than or equal to 0.0 and less than or equal to 99999.0 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Model Adminstration |  | N | Y
|  | Planning | X | X | X |  | MW | Average Amount of Auxiliary Real Power at full MW output | Enter average MW for auxiliary Load at full MW output of the unit | R | R | R | Average Amount of Auxiliary Real Power | 1) This field is required 2) Data type is float 3) Value must be < Parameters - GEN - High Reasonability Limit 4) Warn if value > (High Reasonability Limit) * .20 5) Error if value > (High Reasonability Limit) * .50 | R | Float | B | Planning Team |  | Y | Y
|  | Planning | X | X | X |  | MVAr | Average Amount of Auxiliary Reactive Power at full MW output | Enter average MVAr for auxiliary Load at full MW output of the unit | C | C | C | Average Amount of Auxiliary Reactive Power | 1) This field is conditionally required (see below) 2) Data type is Float 3) Value must be <= Reactive Capability - GEN - Maximum Lagging Operating Capability (MVAR) 4) Warn if value > ( Maximum Lagging Operating Capability) * .20 5) Error if value > ( Maximum Lagging Operating Capability) * .50 Either Auxiliary Reactive Power or Power Factor is required | C | Float | B | Planning Team |  | Y | Y
|  | Planning | X | X | X |  |  | Auxiliary Load Power Factor | Enter power factor for auxiliary Load | C | C | C | Auxiliary Load Power Factor | Between .6 and 1.0 conditionally required (see below) Either Auxiliary Reactive Power or Power Factor is required | C |  |  | Planning Team |  | Y | Y
|  | Planning | X | X | X |  | % | Large Motor, percent of total MW Load | Enter estimated % of total MW Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  | C | Large Motor, Percent Of Total Mw Load | 1)This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at >= 2400V / 4160V are large motors | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS | N | N
|  | Planning | X | X | X |  | % | Small Motor, percent of total MW Load | Enter estimated % of total MW Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  | C | Small Motor, Percent Of Total Mw Load | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at < 2400V / 4160V are small motors | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS | N | N
|  | Planning | X | X | X |  | % | Resistive (Heating) Load, percent of total MW Load | Enter estimated % of total MW Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  | C | Resistive (heating) Load, Percent Of Total Mw Load | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS | N | N
|  | Planning | X | X | X |  | % | Discharge Lighting, percent of total MW Load | Enter estimated % of total MW Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  | C | Discharge Lighting, Percent Of Total Mw Load | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS | N | N
|  | Planning | X | X | X |  | % | Other, percent of total MW Load | Enter estimated % of total MW Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  | C | Other, Percent Of Total Mw Load | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS | N | N
|  | Planning | X | X | X |  | % | Large Motor, percent of total MVAr Load | Enter estimated % of total MVAr Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  | C | Large Motor, Percent Of Total Mvar Load | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% 4) Motors connected at >= 2400V / 4160V are large motors | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS | N | N
|  | Planning | X | X | X |  | % | Small Motor, percent of total MVAr Load | Enter estimated % of total MVAr Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  | C | Small Motor, Percent Of Total Mvar Load | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at < 2400V / 4160V are small motors | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS | N | N
|  | Planning | X | X | X |  | % | Discharge Lighting, percent of total MVAr Load | Enter estimated % of total MVAr Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  | C | Discharge Lighting, Percent Of Total Mvar Load | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS | N | N
|  | Planning | X | X | X |  | % | Other, percent of total MVAr Load | Enter estimated % of total MVAr Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. Ensure that Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. |  |  | C | Other, Percent Of Total Mvar Load | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS | N | N
|  | Protection | X | X | X |  | List | Unit Name | Unit Code as provided on the Unit Info tab. |  | R | R | Unit Name | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS | N | Y
|  | Protection | X | X | X |  | Automatic | Resource Name (Unit Code/Mnemonic) | Concatenated mnemonic of Resource Site Code and Unit name (e.g. CBY_CBYG1). |  |  | A | Resource Name (Unit Code/Mnemonic) | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS | N | Y
|  | Protection | X | X | X |  | cycles | Breaker Interruption Time | Time taken (in cycles) between the breaker receiving the trip signal, and the breaker contacts opening to interrupt the flow of current. |  | R | R | Breaker Interruption Time | 1) this field is required 2) Data type must be Integer | R | Integer | B | Planning Team |  | N | Y
|  | Protection | X | X | X |  | p.u. | Instantaneous Undervoltage Trip | The per unit value (below nominal) of the undervoltage relay instantaneous set point. |  | O | O | Instantaneous Undervoltage Trip | 1) This field is optional 2) Data type must be Float 3)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | O | Float | B | Planning Team |  | N | Y
|  | Protection | X | X | X |  | p.u. | Undervoltage 1 | Enter the first level undervoltage relay set point in per unit. |  | C | C | Instantaneous Under voltage Trip - Undervoltage 1 Undervoltage 2 Undervoltage 3 Undervoltage 4 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Under voltage 1 is required, Under voltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | C | Float | B | Planning Team |  | N | Y
|  | Protection | X | X | X |  | sec | Time 1 | Enter the first level undervoltage time delay set point. |  | C | C | Instantaneous Under voltage Trip - Time 1 Time 2 Time 3 Time 4 | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | C | Float |  | Planning Team |  | N | Y
|  | Protection | X | X | X |  | p.u. | Undervoltage 2 | Enter the second level undervoltage relay set point in per unit. |  | C | C
|  | Protection | X | X | X |  | sec | Time 2 | Enter the second level undervoltage time delay set point. |  | C | C
|  | Protection | X | X | X |  | p.u. | Undervoltage 3 | Enter the third level undervoltage relay set point in per unit. |  | C | C
|  | Protection | X | X | X |  | sec | Time 3 | Enter the third level undervoltage time delay set point. |  | C | C
|  | Protection | X | X | X |  | p.u. | Undervoltage 4 | Enter the fourth level undervoltage relay set point in per unit. |  | C | C
|  | Protection | X | X | X |  | sec | Time 4 | Enter the fourth level undervoltage time delay set point. |  | C | C
|  | Protection | X | X | X |  | p.u. | Instantaneous Overvoltage Trip | The per unit value (above nominal) of the overvoltage relay instantaneous set point. |  | O | O | Instantaneous Overvoltage Trip | 1) This field is optional 2) Data type must be Float 3)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | O | Float | B | Planning Team |  | N | Y
|  | Protection | X | X | X |  | p.u. | Overvoltage 1 | Enter the first level overvoltage relay set point in per unit. |  | C | C | Instantaneous Overvoltage Trip - Overvoltage 1 Overvoltage 2 Overvoltage 3 Overvoltage 4 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Under voltage 1 is required, Under voltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | C | Float | B | Planning Team |  | N | Y
|  | Protection | X | X | X |  | sec | Time 1 | Enter the first level overvoltage relay time delay set point. |  | C | C | Instantaneous Overvoltage Trip Time 1 Time 2 Time 3 Time 4 | 11) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | C | Float | B | Planning Team |  | N | Y
|  | Protection | X | X | X |  | p.u. | Overvoltage 2 | Enter the second level overvoltage relay set point in per unit. |  | C | C
|  | Protection | X | X | X |  | sec | Time 2 | Enter the second level overvoltage relay time delay set point. |  | C | C
|  | Protection | X | X | X |  | p.u. | Ovrvoltage 3 | Enter the third level overvoltage relay set point in per unit. |  | C | C
|  | Protection | X | X | X |  | sec | Time 3 | Enter the third level overvoltage relay time delay set point. |  | C | C
|  | Protection | X | X | X |  | p.u. | Overvoltage 4 | Enter the fourth level overvoltage relay set point in per unit. |  | C | C
|  | Protection | X | X | X |  | sec | Time 4 | Enter the fourth level overvoltage relay time delay set point. |  | C | C
|  | Protection | X | X | X |  | Hz | Instantaneous Underfrequency Trip | The per unit value (below 60Hz) of the underfrequency relay instantaneous set point. |  | O | O | Instantaneous Underfrequency Trip | 1) This field is optional 2) Data type must be Float | O | Float | B | Planning Team |  | N | Y
|  | Protection | X | X | X |  | Hz | Underfrequency 1 | Enter the first level underfrequency relay set point in Hz. |  | C | C | Instantaneous Underfrequency Trip - Underfrequency 1 Underfrequency 2 Underfrequency 3 Underfrequency 4 | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Under frequency 1 is required, Under frequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab | C | Float | B | Planning Team |  | N | Y
|  | Protection | X | X | X |  | sec | Time 1 | Enter the first level underfrequency relay time delay set point. |  | C | C | Instantaneous Underfrequency Trip Time 1 Time 2 Time 3 Time 4 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | C | Float | B | Planning Team |  | N | Y
|  | Protection | X | X | X |  | Hz | Underfrequency 2 | Enter the second level underfrequency relay set point in Hz. |  | C | C
|  | Protection | X | X | X |  | sec | Time 2 | Enter the second level underfrequency relay time delay set point. |  | C | C
|  | Protection | X | X | X |  | Hz | Underfrequency 3 | Enter the third level underfrequency relay set point in Hz. |  | C | C
|  | Protection | X | X | X |  | sec | Time 3 | Enter the third level underfrequency relay time delay set point. |  | C | C
|  | Protection | X | X | X |  | Hz | Underfrequency 4 | Enter the fourth level underfrequency relay set point in Hz. |  | C | C
|  | Protection | X | X | X |  | sec | Time 4 | Enter the fourth level underfrequency relay time delay set point. |  | C | C
|  | Protection | X | X | X |  | Hz | Instantaneous Overfrequency Trip | The per unit value (above 60Hz) of the overfrequency relay instantaneous set point. |  | O | O | Instantaneous Overfrequency Trip | 1) This field is optional 2) Data type must be Float | O | Float | B | Planning Team |  | N | Y
|  | Protection | X | X | X |  | Hz | Overfrequency 1 | Enter the first level overfrequency relay set point in Hz. |  | C | C | Instantaneous Overfrequency Trip - Overfrequency 1 Overfrequency 2 Overfrequency 3 Overfrequency 4 | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Over frequency 1 is required, Over frequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab | C | Float | B | Planning Team |  | N | Y
|  | Protection | X | X | X |  | sec | Time 1 | Enter the first level overfrequency relay time delay set point. |  | C | C | Instantaneous Overfrequency Trip Time 1 Time 2 Time 3 Time 4 | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | C | Float | B | Planning Team |  | N | Y
|  | Protection | X | X | X |  | Hz | Overfrequency 2 | Enter the second level overfrequency relay set point in Hz. |  | C | C
|  | Protection | X | X | X |  | sec | Time 2 | Enter the second level overfrequency relay time delay set point. |  | C | C
|  | Protection | X | X | X |  | Hz | Overfrequency 3 | Enter the third level overfrequency relay set point in Hz. |  | C | C
|  | Protection | X | X | X |  | sec | Time 3 | Enter the third level overfrequency relay time delay set point. |  | C | C
|  | Protection | X | X | X |  | Hz | Overfrequency 4 | Enter the fourth level overfrequency relay set point in Hz. |  | C | C
|  | Protection | X | X | X |  | sec | Time 4 | Enter the fourth level overfrequency relay time delay set point. |  | C | C
|  | Subsync |  | X | X |  | List | Unit Name | Unit Code as provided on the Unit Info tab. |  | R | R | Unit Name | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS | N | Y
|  | Subsync |  | X | X |  | Automatic | Resource Name (Unit Code/Mnemonic) | Concatenated mnemonic of Resource Site Code and Unit name (e.g. CBY_CBYG1). |  |  | A | Resource Name (Unit Code/Mnemonic) | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS | N | Y
|  | Subsync |  | X | X |  | List | Mass Number | Select a unique number for each mass. |  | C | C | Mass # | [6 empty] | N | Y
|  | Subsync |  | X | X |  | Automatic | Mass Code | Concatenated code automatically provided of the Resource Name and Mass Number |  |  | A | Mass Code | CONCATENATE Unit_CODE_MASS | [5 empty] | N | Y
|  | Subsync |  | X | X |  | Automatic | Name | Identification of the masses- HP, IP, LP1, LP2, EXC, etc. |  |  | A | Name | [6 empty] | N | Y
|  | Subsync |  | X | X |  |  | Mass Inertia | H-value. The inertia constant of each mass, either in MW's, MVA, or lbm.ft² |  | C | C | Mass Inertia | [6 empty] | N | Y
|  | Subsync |  | X | X |  |  | Inertia units | MW's, MVA, or lbm.ft² |  | C | C | Inertia Units | [6 empty] | N | Y
|  | Subsync |  | X | X |  |  | Associated damping | The damping associated with each mass either in p.u. torque/p.u. speed deviation, or lbf.ft.sec/rad |  | C | C | Associated Damping | [6 empty] | N | Y
|  | Subsync |  | X | X |  |  | Damping units | p.u. torque/p.u. speed or lbf.ft.sec/rad |  | C | C | Damping Units | [6 empty] | N | Y
|  | Subsync |  | X | X |  |  | Stiffness between Masses | The stiffness (spring constant) between each two mass, either in p.u. torque/rad, or lbf.ft/rad (coupling). |  | C | C | Stiffness Between Masses Previous and Current Masses | [6 empty] | N | Y
|  | Subsync |  | X | X |  |  | Stiffness units | p.u. torque/rad or lbf.ft/rad |  | C | C | Stiffness Units | [6 empty] | N | Y
|  | Line Data | X | X | X |  | List | Description of Change | Select: description of change from drop down list: Add, Change or Delete |  |  | C | DESCRIPTION OF CHANGE | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | T | Alpha | B | Joel Koepke |  | N | N
|  | Line Data | X | X | X |  | All Caps | Line Name | Line names as listed in the ERCOT model, which must meet the character limitation of the system. |  |  | R | Line Name | 1) This field is required 2) This field may not have any special characters, except an underscore "_" and a dash "-" 3) Warn if > 14 characters. Warning! ERCOT Line Name () should not be > 14 characters long or the name will be truncated in the model which requires uniqueness. 4) Line Name can not be duplicated in a Station | T | Alpha | B | Joel Koepke |  | N | N
|  | Line Data | X | X | X |  | kV | Line Voltage Level | Line Voltage Level |  | R | R | Line Voltage Level | 1) This field is required. 2) If the value >= 69kv it must be 69,138, or 345 3) The value must be < 345 4) The value must be > 1 | T | Float | B/DVE | Joel Koepke |  | N | Y
|  | Line Data | X | X | X |  | p.u. | Resistance in p.u. (100 MVA Base) | Resistance in p.u. (100 MVA Base) |  | R | R | Resistance in P.U. (100 MVA Base) | 1) Field is required If value is < 0.0001 and Internal Line = 'Y' then Warning! Resistance should be less than 0.0001 If value is < 0.0001 and Internal Line = 'N' then Warning! Resistance should be less than 0.0001 3) If Line Data - Line Voltage Level = 69kV, value must be <= 1.5 If Line Data - Line Voltage Level = 138kV or 345kV, value must be <= 0.5 WARN if value is outside of these conditions 4) If the Zero Impedance Lines are contained within a single substation, then they should be removed from the Line tab and the updated connections should be shown in the Breaker/Switch tab. "ERROR! Internal zero impedance lines should be modeled on the breaker/switch tab" If Zero Impedance Lines are between two substations, produce a warning if line ratings are entered as 9999. "ERROR! Invalid MVA Rating between substations" | T | Float | B | Joel Koepke |  | N | Y
|  | Line Data | X | X | X |  | p.u. | Reactance in p.u. (100 MVA Base) | Reactance in p.u. (100 MVA Base) |  | R | R | Reactance in P.U. (100 MVA Base) | 1) Field is required If value is < 0.0001 and Internal Line = 'Y' then Warning! Reactance should be less than 0.0001 If value is < 0.0001 and Internal Line = 'N' then Warning! Reactance should be less than 0.0001 If Line Data - Line Voltage Level = 69kV, value must be <=1.0 If Line Data - Line Voltage Level = 138kV, value must be <=0.1 If Line Data - Line Voltage Level = 345kV, value must be <=.05 WARN if value is outside of these conditions 3)Error if Reactance value is > 1. Error! Reactance (value) > 1.0. Reactance should be expressed in terms of per unit (e.g. not percentage). 4) If the Zero Impedance Lines are contained within a single substation, then they should be removed from the Line tab and the updated connections should be shown in the Breaker/Switch tab. "ERROR! Internal zero impedance lines should be modeled on the breaker/switch tab" | T | Float | B | Joel Koepke |  | N | Y
|  | Line Data | X | X | X |  | p.u. | Charging Susceptance in p.u. (100 MVA Base) | Charging Susceptance in p.u. (100 MVA Base) |  | R | R | Charging Susceptance in PU (100 MVA Base) | 1) Field is required 2) Value must be >= 0 If Line Data - Line Voltage Level = 69kV, value must be >=.00001<=0.3 If Line Data - Line Voltage Level = 138kV, value must be >=.00001<=0.5 If Line Data - Line Voltage Level = 345kV, value must be >=.00001<=2.2. Generate a Warning if Rule fails 3) If the Zero Impedance Lines are contained within a single substation, then they should be removed from the Line tab and the updated connections should be shown in the Breaker/Switch tab. ERROR! Internal zero impedance lines should be modeled on the breaker/switch tab. | T | Float | B | Joel Koepke |  | N | Y
|  | Line Data | X | X | X |  | p.u. | Zero Sequence Line Resistance in p.u. (100 MVA Base) | Zero Sequence Line Resistance in p.u. (100 MVA Base) |  | R | R | Zero Sequence Line Resistance In P.u. (100mva Base) | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 Generate a Warning if the per unit value entered is not >= 0.0 and <= 100.0 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  |  |  | N | Y
|  | Line Data | X | X | X |  | p.u. | Zero Sequence Line Reactance in p.u. (100 MVA Base) | Zero Sequence Line Reactance in p.u. (100 MVA Base) |  | R | R | Zero Sequence Line Reactance In P.u. (100mva Base) | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 Generate a Warning if the per unit value entered is not >= 0.0 and <= 100.0 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  |  |  | N | Y
|  | Line Data | X | X | X |  | p.u. | Zero Sequence Charging Susceptance in p.u. (100 MVA Base) | Zero Sequence Charging Susceptance in p.u. (100 MVA Base) |  | R | R | Zero Sequence Charging Susceptance In P.u. (100mva Base) | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 Generate a Warning if the per unit value entered is not >= 0.0 and <= 100.0 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  |  |  | N | Y
|  | Line Data | X | X | X |  | List | Type | Select line type from drop down list: Overhead, Underground or Both |  |  | R | Type (overhead / underground) | 1) Field is required 2) Value must be at from the following list: OVERHEAD, UNDERGROUND, BOTH | T | Alpha | B | Joel Koepke |  | N | N
|  | Line Data | X | X | X |  | miles | Segment Length | Length of this line segment between the TO station and the FROM station (circuit miles) |  | R | R | Segment Length | 1) Field is required 2) Value must > 0 3) Formula on Line Data - Segment Length: The formula to determine the length of a line based on the Reactance (X) and the Charging Susceptance (Chg) is 486 * SQRT(X_pu * Chg_pu). Generate a Warning when Segment length is not within the 25% variation of the calculated value. 4) Update the Warning message to include the text " This is applicable for Overhead lines only" | T | Float | B | Joel Koepke |  | N | Y
|  | Line Data | X | X | X |  | All Caps | ERCOT TO Station Code Mnemonic | Enter the station code mnemonic of the TO station for this Line |  |  | R | EROCT STATION TO - Station Code Mnemonic | 1) This field is Optional 2) Warn if left blank 3) This field must match ERCOT records (unless new) .Substation Code invalid message should be warning only if the PUN flag is 'yes'. 4.If the Internal Line Flag is 'Y', then the TO STATION - ERCOT Station Code Mnemonic and FROM STATION - ERCOT Station Code Mnemonic can be same. If the internal Line Flag is 'N', TO STATION - ERCOT Station Code Mnemonic and FROM STATION - ERCOT Station Code Mnemonic should be distinct . Error message should be "'Error! TO and FROM Station Code ( ) should not be duplicated if Internal Line Flag = "N". 5) If the internal Line Flag is 'N', ,FROM Station Code Mnemonic cannot be listed as a TO Station Code Mnemonic on any other lines. The Warning would occur on the secondary side (eg: they had DIESEL on the FROM station on the first line, and DIESEL on the TO Station on the second line then the TO station would produce the Warning) or (eg: DIESEL is on the TO station on the 3rd line and DIESEL on the FROM station on the 4th line then the FROM station would produce the Warning). | T | Alpha | B/DVE | Joel Koepke |  | N | N
|  | Line Data | X | X | X |  | Y/N | Internal Line? | Is this line internal to the station (i.e. not directly connected to the TDSP or both ends are within the same station)? |  |  | C | Internal Line | 1) This field is required 2) Value must be of the following: 'Y', 'N' | T | Alpha | B |  |  | N | Y
|  | Line Data | X | X | X |  | List | TSP Name | Select TSP Name from the drop down list |  |  | C | TSP Name | 1) This field is conditionally required if TO STATION - Internal Line - 'N' 2) This field must match ERCOT records (drop down in RARF) | T | Alpha | B/DVE | Joel Koepke |  | N | N
|  | Line Data | X | X | X |  | All Caps | Connected Device 1 | Enter device connected to this line in the TO station (can provide up to 10). Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | R | Connected Device 1 thru 10 | 1) This field is required 2) May not be >= than 17 characters. Warning! Device Name () should not be > 17 characters long or the name will be truncated in the model which requires uniqueness. 3) May not have duplicates within the TO or FROM Station 4) May not contain special characters except for an underscore "_" and a dash "-" | T | Alpha | B/DVE | Joel Koepke |  | N | N
|  | Line Data | X | X | X |  | All Caps | Connected Device 2 | Enter device connected to this line in the TO station (can provide up to 10). Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Line Data | X | X | X |  | All Caps | Connected Device 3 | Enter device connected to this line in the TO station (can provide up to 10). Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Line Data | X | X | X |  | All Caps | Connected Device 4 | Enter device connected to this line in the TO station (can provide up to 10). Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Line Data | X | X | X |  | All Caps | Connected Device 5 | Enter device connected to this line in the TO station (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Line Data | X | X | X |  | All Caps | Connected Device 6 | Enter device connected to this line in the TO station (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Line Data | X | X | X |  | All Caps | Connected Device 7 | Enter device connected to this line in the TO station (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Line Data | X | X | X |  | All Caps | Connected Device 8 | Enter device connected to this line in the TO station (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Line Data | X | X | X |  | All Caps | Connected Device 9 | Enter device connected to this line in the TO station (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Line Data | X | X | X |  | All Caps | Connected Device 10 | Enter device connected to this line in the TO station (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Line Data | X | X | X |  | Number | Bus Number (PTI Bus Number) | Enter PTI Bus number connecting this line in the TO station |  |  | O | Bus Number (PTI Bus Number) | 1) This field is optional 2) This field must be between 1 - 999,999 | T | Integer | B/DVE | Joel Koepke |  | N | N
|  | Line Data | X | X | X |  | List | Weather Zone / Weather Station (used for Dynamic Ratings) | Select Weather zone or station from the drop down list |  |  | C | Weather Zone / Weather Station (used for Dynamic Ratings) | 1) This field is conditionally required if "Line Rating (Static or Dynamic)" = 'DYNAMIC' 2) Value must be from the following list: COAST, EAST, FAR_WEST, NORTH, NORTH_C, SOUTH_C, SOUTHERN, WEST, KABI, KAUS, KBRO, KCRP, KDFW, KGLS, KIAH, KJCT, KLRD, KLFK, KMAF, KMWL, KSJT, KSAT, KTYR, KVCT, KACT, KSPS, KINK, KPRX | T | Alpha | B/DVE | Joel Koepke |  | N | N
|  | Line Data | X | X | X |  | All Caps | ERCOT FROM Station Code Mnemonic | Enter the station code mnemonic of the FROM station for this Line |  |  | R | ERCOT FROM Station Code Mnemonic | 1) This field is required 2) Must match ERCOT records (unless new) 3) Value must be <= 8 characters .Warning! Station Code () should not be > 8 characters long or the name will be truncated in the model which requires uniqueness. 4. If the Internal Line Flag is 'Y', then the TO STATION - ERCOT Station Code Mnemonic and FROM STATION - ERCOT Station Code Mnemonic can be same. If the internal Line Flag is 'N', TO STATION - ERCOT Station Code Mnemonic and FROM STATION - ERCOT Station Code Mnemonic should be distinct. Error message should be "'Error! TO and FROM Station Code ( ) should not be duplicated if Internal Line Flag = "N". 5) If the internal Line Flag is 'N', ,FROM Station Code Mnemonic cannot be listed as a TO Station Code Mnemonic on any other lines. The Warning would occur on the secondary side (eg: they had DIESEL on the FROM station on the first line, and DIESEL on the TO Station on the second line then the TO station would produce the Warning) or (eg: DIESEL is on the TO station on the 3rd line and DIESEL on the FROM station on the 4th line then the FROM station would produce the Warning). | T | Alpha | B/DVE |  |  | N | N
|  | Line Data | X | X | X |  | All Caps | Connected Device 1 | Enter device connected to this line in the FROM station (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | R | Connected Device 1 thru 10 | 1) This field is required 2) May not have duplicates within the TO or FROM Station 3) May not contain special characters except for an underscore "_" and a dash "-" 4) May not be > than 17 characters. Warning! Device Name () should not be > 17 characters long or the name will be truncated in the model which requires uniqueness. | T | Alpha | B/DVE | Joel Koepke |  | N | N
|  | Line Data | X | X | X |  | All Caps | Connected Device 2 | Enter device connected to this line in the FROM station (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Line Data | X | X | X |  | All Caps | Connected Device 3 | Enter device connected to this line in the FROM station (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Line Data | X | X | X |  | All Caps | Connected Device 4 | Enter device connected to this line in the FROM station (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Line Data | X | X | X |  | All Caps | Connected Device 5 | Enter device connected to this line in the FROM station (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Line Data | X | X | X |  | All Caps | Connected Device 6 | Enter device connected to this line in the FROM station (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Line Data | X | X | X |  | All Caps | Connected Device 7 | Enter device connected to this line in the FROM station (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Line Data | X | X | X |  | All Caps | Connected Device 8 | Enter device connected to this line in the FROM station (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Line Data | X | X | X |  | All Caps | Connected Device 9 | Enter device connected to this line in the FROM station (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Line Data | X | X | X |  | All Caps | Connected Device 10 | Enter device connected to this line in the FROM station (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Line Data | X | X | X |  | Number | Bus Number (PTI Bus Number) | Enter PTI Bus number connecting this line in the FROM station |  |  | O | Bus Number (PTI Bus Number) | 1) This field is optional 2) This field must be between 1 - 999,999 3) Warn if left blank | T | Integer | B/DVE | Joel Koepke |  | N | N
|  | Line Data | X | X | X |  | List | Weather Zone / Weather Station (used for Dynamic Ratings) | Select Weather zone or station from the drop down list |  |  | C | Weather Zone / Weather Station (used for Dynamic Ratings) | 1) This field is conditionally required if "Line Rating (Static or Dynamic)" = 'DYNAMIC' 2) Value must be from the following list: COAST, EAST, FAR_WEST, NORTH, NORTH_C, SOUTH_C, SOUTHERN, WEST, KABI, KAUS, KBRO, KCRP, KDFW, KGLS, KIAH, KJCT, KLRD, KLFK, KMAF, KMWL, KSJT, KSAT, KTYR, KVCT, KACT, KSPS, KINK, KPRX | T | Alpha | B/DVE | Joel Koepke |  | N | N
|  | Line Data | X | X | X |  | Automatic | Line Code | Concatenated code automatically provided |  |  | A | Line Code | Concantenate (Site Code_Substation Code_ERCOT_LINE_NAME) | R |  |  |  |  | N | N
|  | Line Data | X | X | X |  |  | Comments | Enter any comments regarding this Line data |  |  | O | COMMENTS | [6 empty] | N | N
|  | Line Data | X | X | X |  | mm/dd/yyyy | Effective Date | Date this line was added, removed or updated in the model |  |  | R | EFFECTIVE DATE: | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | T | Date | B/DVB | Scott/Woody/Angie |  | N | N
|  | Line Temperature | X | X | X |  | Automatic | Line Name | Automatically provided based on lines listed in the Line data tab |  |  | A | Line Name | 1) This field is required 2) This field may not have any special characters, except an underscore "_" and a dash "-" 3) Warn if > 14 characters. Warning! ERCOT Line Name () should not be > 14 characters long or the name will be truncated in the model which requires uniqueness. 4) Line Name can not be duplicated in a Station | [5 empty] | N | Y
|  | Line Temperature | X | X | X |  | Automatic | Line Code | Automatically provided based on line codes listed in the Line data tab |  |  | A | Line Code | Concantenate (Site Code_Substation Code_ERCOT_LINE_NAME) | [5 empty] | N | N
|  | Line Temperature | X | X | X |  | List | Line Rating | Select Static or Dynamic line rating |  |  | R | Line Rating | 1) Field is required 2) Field must be from the following list: STATIC, DYNAMIC | T | Alpha | B | Joel Koepke |  | N | N
|  | Line Temperature | X | X | X |  | MVA | Continuous Rating | Rating that line can operate at indefinitely without damage, or violation fof NESC clearances. Per definition of "Normal Rating" in Section 2 of the ERCOT protocols, the continuous MVA rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature. The Transmission Element can operate at this rating indefinitely without damage, or violation of NESC clearances. |  | R | R | Continuous Rating | 1) This field is required regardless of STATIC or DYNAMIC 2) Value must be <= Nominal (Static) - 2-hr Emergency Rating 3) Value must be <= Nominal (Static) - 15-min Rating 4) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - Continuous Rating AND value must be >= 115 °F Continuous Rating 5) Produce an error when invalid MVA ratings are entered as 9999. ERROR! Invalid MVA Rating between substations. | T | Integer | B/DVE | Joel Koepke |  | N | Y
|  | Line Temperature | X | X | X |  | MVA | 2-hr Emergency Rating | Rating that line can operate at this rating for two hours without violation of NESC clearances or equipment failure Per definition of "Emergency Rating" in Section 2 of the ERCOT protocols, the two-hour MVA rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature. The Transmission Element can operate at this rating for two hours without violation of NESC clearances or equipment failure. |  | R | R | 2-hr Emergency Rating | 1) This field is required regardless of STATIC or DYNAMIC 2) Value must be >= Nominal (Static) - Continuous Rating 3) Value must be <= Nominal (Static) - 15-min Rating 4) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - 2-hr Emergency Rating AND value must be >= 115 °F 2-hr Emergency Rating 5) Produce an error when invalid MVA ratings are entered as 9999. ERROR! Invalid MVA Rating between substations. | T | Integer | B/DVE | Joel Koepke |  | N | Y
|  | Line Temperature | X | X | X |  | MVA | 15-min Rating | Rating that line can operate at this rating for fifteen minutes without violation of NESC clearances or equipment failure Per definition of "15 Minute Rating" in Section 2 of the ERCOT protocols, The 15-minute MVA rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature and with a step increase from a prior loading up to 90% of the Normal Rating. The Transmission Element can operate at this rating for 15 minutes, assuming its pre-contingency loading up to 90% of the Normal Rating limit at the applicable ambient temperature, without violation of NESC clearances or equipment failure. This rating takes advantage of the time delay associated with heating of a conductor or transformer following a sudden increase in current. |  | R | R | 15-min Rating | 1) This field is required regardless of STATIC or DYNAMIC 2) Value must be >= Nominal (Static) - Continuous Rating 3) Value must be >= Nominal (Static) - 2-hr Emergency Rating 4) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - 15-min Rating AND value must be >= 115 °F 15-min Rating 5) Produce an error when invalid MVA ratings are entered as 9999. ERROR! Invalid MVA Rating between substations. | T | Integer | B/DVE | Joel Koepke |  | N | Y
|  | Line Temperature | X | X | X |  | MVA | Planning Rate C | Represents the two hour MVA rating of the conductor or transformer only,excluding substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature without violation of NESC clearances or equipment failure. Per definition of "Conductor/Transformer 2-hour Rating" in Section 2 of the ERCOT protocols, The two-hour MVA rating of the conductor or transformer only, excluding substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature. The conductor or transformer can operate at this rating for two hours without violation of National Electrical Safety Code (NESC) clearances or equipment failure. |  | R | R | Planning Rate C | This field is required Numeric value Must be >= Nominal Emergency Rating (2HR Rating) | R | Model Adminstration |  |  |  | N | Y
|  | Line Temperature | X | X | X |  | MVA | 20 °F - Continuous Rating - 115 °F Continuous Rating | Rating that line can operate at indefinitely without damage, or violation fo NESC clearances at the stated temperature. Per definition of "Normal Rating" in Section 2 of the ERCOT protocols, the continuous MVA rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the stated ambient temperature. The Transmission Element can operate at this rating indefinitely without damage, or violation of NESC clearances. |  |  | C | 20 °F - Continuous Rating - 115 °F Continuous Rating | 1) These field are conditionally required. If Line Rating (Static or Dynamic) = Dynamic this field is required 2) Line Rating (Static or Dynamic) = Static, this field must be blank 3) If required, these values must be <= the subsequent dynamic rating. For example: 20 °F - Continuous Rating >= 25 °F - Continuous Rating 25 °F - Continuous Rating >= 30 °F - Continuous Rating 4) If required, within each temp rating, the following must apply Continuous Rating <= 2-hr Emergency Rating <= 15-min rating | T | Integer | B/DVE | Joel Koepke |  | N | N
|  | Line Temperature | X | X | X |  | MVA | 20 °F - 2-hr Emergency Rating - 115 °F 2-hr Emergency Rating | Rating that line can operate at this rating for two hours without violation of NESC clearances or equipment failure at the stated temperature. Per definition of "Emergency Rating" in Section 2 of the ERCOT protocols, the two-hour MVA rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the stated ambient temperature. The Transmission Element can operate at this rating for two hours without violation of NESC clearances or equipment failure. |  |  | C | 20 °F - 2-hr Emergency Rating - 115 °F 2-hr Emergency Rating | 1) These field are conditionally required. If Line Rating (Static or Dynamic) = Dynamic this field is required 2) Line Rating (Static or Dynamic) = Static, this field must be blank 3) If required, these values must be >= the subsequent dynamic rating. For example: 20 °F - 2-hr Emergency Rating >= 25 °F - 2-hr Emergency Rating 25 °F - 2-hr Emergency Rating >= 30 °F - 2-hr Emergency Rating 4) If required, within each temp rating, the following must apply Continuous Rating <= 2-hr Emergency Rating <= 15-min rating | T | Integer | B/DVE | Joel Koepke |  | N | N
|  | Line Temperature | X | X | X |  | MVA | 20 °F - 15-min Rating - 115 °F 15-min Rating | Rating that line can operate at this rating for fifteen minutes without violation of NESC clearances or equipment failure at the stated temperature. Per definition of "15 Minute Rating" in Section 2 of the ERCOT protocols, The 15-minute MVA rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the stated ambient temperature and with a step increase from a prior loading up to 90% of the Normal Rating. The Transmission Element can operate at this rating for 15 minutes, assuming its pre-contingency loading up to 90% of the Normal Rating limit at the stated ambient temperature, without violation of NESC clearances or equipment failure. This rating takes advantage of the time delay associated with heating of a conductor or transformer following a sudden increase in current. |  |  | C | 20 °F - 15-min Rating - 115 °F 15-min Rating | 1) These field are conditionally required. If Line Rating (Static or Dynamic) = Dynamic this field is required 2) Line Rating (Static or Dynamic) = Static, this field must be blank 3) If required, these values must be >= the subsequent dynamic rating. For example: 20 °F - 2-hr 15-min Rating >= 25 °F - 15-min Rating 25 °F - 2-hr 15-min Rating >= 30 °F - 15-min Rating 4) If required, within each temp rating, the following must apply Continuous Rating <= 2-hr Emergency Rating <= 15-min rating | T | Integer | B/DVE | Joel Koepke |  | N | N
|  | Line Temperature | X | X | X |  | MVA | 20 °F - Planning Rate C - 115 °F - Planning Rate C | Represents the two hour MVA rating of the conductor or transformer only,excluding substation terminal equipment in series with a conductor or transformer, at the stated ambient temperature without violation of NESC clearances or equipment failure. Per definition of "Conductor/Transformer 2-hour Rating" in Section 2 of the ERCOT protocols, The two-hour MVA rating of the conductor or transformer only, excluding substation terminal equipment in series with a conductor or transformer, at the stated ambient temperature. The conductor or transformer can operate at this rating for two hours without violation of National Electrical Safety Code (NESC) clearances or equipment failure. |  |  | C | Planning Rate C | 1)Numeric value 2) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be >=Tempature Emergency Rating (2HR Rating) else (if Line Rating (Static or Dynamic) = Static, this field must be blank). | R | Float |  | Planning Team |  | N | N
|  | Breaker Switch Data | X | X | X |  | List | Description of Change | Select: description of change from drop down list: Add, Change or Delete |  |  | C | DESCRIPTION OF CHANGE | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | T | Alpha | B | Joel Koepke |  | N | N
|  | Breaker Switch Data | X | X | X |  | All Caps | Switch Name | Breaker or Switch name as provided in the ERCOT model, which must meet the character limitation of the system. Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | R | Switch Name | 1) This field is required 2) Value may contain no special characters except an underscore "_" and a dash "-" 3) Must be <=14 characters. Warning! Switch Name () should not be >14 characters long or the name will be truncated in the model which requires uniqueness. 4) Switch Name can not be duplicated in a station | T | Alpha | B | Joel Koepke |  | N | N
|  | Breaker Switch Data | X | X | X |  | All Caps | ERCOT Station Name (Station Code or Station Mnemonic) | ERCOT Station Code Mnemonic thatwhere the breaker or switch is located, as listed in the model |  |  | R | ERCOT Station Code Mnemonic | 1) This field is required 2) Must match ERCOT records (unless new). Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) This field may not have any special characters, except an underscore "_" and a dash "-" 4) Must be <= 8 characters. Warning! Station Code () should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 5) substation code should be in Upper case letters. Generate an error if the rule fails | T | Alpha | B | Joel Koepke |  | N | N
|  | Breaker Switch Data | X | X | X |  | Automatic | Switch Code | Concatenated code automatically provided |  |  | A | Switch Code | Concantenate (Site Code_Substation Code_Switch Name) | [5 empty] | N | N
|  | Breaker Switch Data | X | X | X |  | Y/N | Is This A Fault Isolating Device (e.g. Circuit Breaker) | Select Y if device is Breaker, or N if device is a Switch Select Y or N |  | R | R | Is this a Fault Isolating Device (e.g. Circuit Breaker) | 1) This is a required field 2) Values must from the following list: 'Y', 'N' | T | Alpha | B | Joel Koepke |  | N | Y
|  | Breaker Switch Data | X | X | X |  | List | Normal Operating Status (when in service) | Select whether Open or Closed during normal operations |  | R | R | Normal Operating Status (when in-service) | 1) This field is required 2) Value must be from the following list: 'OPEN', 'CLOSED' 3) Generate a warning when the Normal Operating Status is 'OPEN' | T | Alpha | B | Joel Koepke |  | N | Y
|  | Breaker Switch Data | X | X | X |  | kV | Voltage Level | Enter voltage level of this breaker or switch |  | R | R | Voltage Level | 1) This field is required. 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 | T | Float | B/DVE | Joel Koepke |  | N | Y
|  | Breaker Switch Data | X | X | X |  | MVA | Continuous Rating | Rating that device can operate at indefinitely without damage, or violation fo NESC clearances. Per definition of "Normal Rating" in Section 2 of the ERCOT protocols, the continuous MVA rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature. The Transmission Element can operate at this rating indefinitely without damage, or violation of NESC clearances. |  | R | R | Continuous Rating | 1) This field is required regardless of STATIC or DYNAMIC 2) Value must be <= Nominal (Static) - 2-hr Emergency Rating 3) Value must be <= Nominal (Static) - 15-min Rating 4) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - Continuous Rating AND value must be >= 115 °F Continuous Rating 5) Produce an warning when invalid MVA ratings are entered as 9999. WARNING! Invalid MVA Rating between substations. | T | Integer | B/DVE | Planning Team |  | N | Y
|  | Breaker Switch Data | X | X | X |  | MVA | 2-hr Emergency Rating | Rating that device can operate at this rating for two hours without violation of NESC clearances or equipment failure Per definition of "Emergency Rating" in Section 2 of the ERCOT protocols, the two-hour MVA rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature. The Transmission Element can operate at this rating for two hours without violation of NESC clearances or equipment failure. |  | R | R | 2-hr Emergency Rating | 1) This field is required regardless of STATIC or DYNAMIC 2) Value must be >= Nominal (Static) - Continuous Rating 3) Value must be <= Nominal (Static) - 15-min Rating 4) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - 2-hr Emergency Rating AND value must be >= 115 °F 2-hr Emergency Rating 5) Produce an warning when invalid MVA ratings are entered as 9999. WARNING! Invalid MVA Rating between substations. | T | Integer | B/DVE | Planning Team |  | N | Y
|  | Breaker Switch Data | X | X | X |  | MVA | 15-min Rating | Rating that device can operate at this rating for fifteen minutes without violation of NESC clearances or equipment failure Per definition of "15 Minute Rating" in Section 2 of the ERCOT protocols, The 15-minute MVA rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature and with a step increase from a prior loading up to 90% of the Normal Rating. The Transmission Element can operate at this rating for 15 minutes, assuming its pre-contingency loading up to 90% of the Normal Rating limit at the applicable ambient temperature, without violation of NESC clearances or equipment failure. This rating takes advantage of the time delay associated with heating of a conductor or transformer following a sudden increase in current. |  | R | R | 15 Min Rating | 1) This field is required regardless of STATIC or DYNAMIC 2) Value must be >= Nominal (Static) - Continuous Rating 3) Value must be >= Nominal (Static) - 2-hr Emergency Rating 4) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - 15-min Rating AND value must be >= 115 °F 15-min Rating 5) Produce an Warning when invalid MVA ratings are entered as 9999. WARNING! Invalid MVA Rating between substations. | T | Integer | B/DVE | Planning Team |  | N | Y
|  | Breaker Switch Data | X | X | X |  | All Caps | Connected Device 1 | Enter device connected to this breaker or switch on Side 1 (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | R | Side 1 / Side 2 - Directly connected device name(s) | 1) This field is required 2) Value may contain no special characters except an underscore "_" and a dash "-" 3) Must be <=17 characters. Must be <=17 characters. Warning! Device Names () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. 4) At least one connected device is required on each side of the Breaker/Switch. Generate an error if at least one connected device is missing on both sides Generate a Warning when at least one connected device is missing on any one side. | T | Alpha | B | Joel Koepke |  | N | N
|  | Breaker Switch Data | X | X | X |  | All Caps | Connected Device 2 | Enter device connected to this breaker or switch on Side 1 (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Breaker Switch Data | X | X | X |  | All Caps | Connected Device 3 | Enter device connected to this breaker or switch on Side 1 (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Breaker Switch Data | X | X | X |  | All Caps | Connected Device 4 | Enter device connected to this breaker or switch on Side 1 (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Breaker Switch Data | X | X | X |  | All Caps | Connected Device 5 | Enter device connected to this breaker or switch on Side 1 (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Breaker Switch Data | X | X | X |  | All Caps | Connected Device 6 | Enter device connected to this breaker or switch on Side 1 (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Breaker Switch Data | X | X | X |  | All Caps | Connected Device 7 | Enter device connected to this breaker or switch on Side 1 (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Breaker Switch Data | X | X | X |  | All Caps | Connected Device 8 | Enter device connected to this breaker or switch on Side 1 (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Breaker Switch Data | X | X | X |  | All Caps | Connected Device 9 | Enter device connected to this breaker or switch on Side 1 (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Breaker Switch Data | X | X | X |  | All Caps | Connected Device 10 | Enter device connected to this breaker or switch on Side 1 (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Breaker Switch Data | X | X | X |  | All Caps | Connected Device 1 | Enter device connected to this breaker or switch on Side 2 (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | R
|  | Breaker Switch Data | X | X | X |  | All Caps | Connected Device 2 | Enter device connected to this breaker or switch on Side 2 (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Breaker Switch Data | X | X | X |  | All Caps | Connected Device 3 | Enter device connected to this breaker or switch on Side 2 (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Breaker Switch Data | X | X | X |  | All Caps | Connected Device 4 | Enter device connected to this breaker or switch on Side 2 (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Breaker Switch Data | X | X | X |  | All Caps | Connected Device 5 | Enter device connected to this breaker or switch on Side 2 (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Breaker Switch Data | X | X | X |  | All Caps | Connected Device 6 | Enter device connected to this breaker or switch on Side 2 (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Breaker Switch Data | X | X | X |  | All Caps | Connected Device 7 | Enter device connected to this breaker or switch on Side 2 (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Breaker Switch Data | X | X | X |  | All Caps | Connected Device 8 | Enter device connected to this breaker or switch on Side 2 (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Breaker Switch Data | X | X | X |  | All Caps | Connected Device 9 | Enter device connected to this breaker or switch on Side 2 (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Breaker Switch Data | X | X | X |  | All Caps | Connected Device 10 | Enter device connected to this breaker or switch on Side 2 (can provide up to 10) Ensure device name is consistent throughout all RARF tabs and one-line diagram. |  |  | C
|  | Breaker Switch Data | X | X | X |  |  | Comments | Enter any comments regarding this breaker-switch data |  |  | O | COMMENTS | [6 empty] | N | N
|  | Breaker Switch Data | X | X | X |  | mm/dd/yyyy | Effective Date | Date this breaker or switch was added, removed or updated in the model |  |  | R | EFFECTIVE DATE: | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | T | Date | Scott/Woody/Angie |  |  | N | N
|  | Capacitor and Reactor Data | X | X | X |  | List | Description of Change | Select: description of change from drop down list: Add, Change or Delete |  |  | C | DESCRIPTION OF CHANGE | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | T | Alpha | B | Joel Koepke |  | N | N
|  | Capacitor and Reactor Data | X | X | X |  | All Caps | Device Name | Capacitor or Reactor name as provided in the ERCOT model, which must meet the character limitation of the system. |  |  | R | Device Name | 1) This field is required 2) Value may contain no special characters except an underscore "_" and a dash "-" 3) Must be <=14 characters. Warning! Device Name () should not be >14 characters long or the name will be truncated in the model which requires uniqueness. 4) Device Name can not be duplicated in a Station | T | Alpha | B | Joel Koepke |  | N | N
|  | Capacitor and Reactor Data | X | X | X |  | All Caps | ERCOT Station Name (Station Code or Station Mnemonic) | ERCOT Station Code Mnemonic that the breaker or switch is located, as listed in the model |  |  | R | ERCOT Station Code Mnemonic | 1) This field is required 2) Must match ERCOT records (unless new).Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3)This field may not have any special characters, except an underscore "_" and a dash "-" 4) Value must be <= 8 characters. Warning! Station Code () should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 5) substation code should be in Upper case letters. Generate an error if the rule fails | T | Alpha | B | Joel Koepke |  | N | N
|  | Capacitor and Reactor Data | X | X | X |  | Automatic | Device Code | Concatenated code automatically provided |  |  | A | Device Code | Concantenate (Site Code_Substation Code_Device Code) | [5 empty] | N | N
|  | Capacitor and Reactor Data | X | X | X |  | List | Capacitor or Reactor | Select whether this device is a capacitor or reactor |  | R | R | Capacitor or Reactor | 1) This field is required 2) Value must be from the following list: 'C', 'R' | T | Alpha | B | Joel Koepke |  | N | Y
|  | Capacitor and Reactor Data | X | X | X |  | MVAr | Nominal MVAr | Rated MVAr rating of a capacitor or reactor (name plate data) |  | R | R | Nominal MvAR | 1) This field is required 2) If the Capacitor or Reactor field is 'C' , the value should be > 0 , if it is 'R', value should be < 0 | T | Float | B | Joel Koepke |  | N | Y
|  | Capacitor and Reactor Data | X | X | X |  | kV | Voltage Level kV | Enter voltage level of this capacitor or reactor |  | R | R | Voltage Level Kv | 1) This field is required. 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 | T | Float | B/DVE | Joel Koepke |  | N | Y
|  | Capacitor and Reactor Data | X | X | X |  | Number | Bus Number (PTI Bus Number) | Enter PTI Bus Number for this device |  |  | O | Bus Number (PTI Bus Number) | 1) This field is optional 2) This field must be between 1 - 999,999 | T | Float | B | Joel Koepke |  | N | N
|  | Capacitor and Reactor Data | X | X | X |  | Y/N | Automatic Voltage Regulation | Select Y or N whether this device has automatic voltage regulation |  | R | R | Automatic Voltage Regulation | 1) This field is required 2) Value must be from the following list: 'Y', 'N' | T | Alpha | B | Joel Koepke |  | N | Y
|  | Capacitor and Reactor Data | X | X | X |  | kV | Voltage Level of Busbar being regulated | Enter voltage of busbar where device is located |  | C | C | Voltage Level of Busbar being regulated | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 | T | Float | B/DVE | Joel Koepke |  | N | Y
|  | Capacitor and Reactor Data | X | X | X |  | kV | Desired Regulating Voltage | Desired Regulating Voltage |  | C | C | Desired Regulating voltage | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) The value may not exceed 345. (REMOVED) 3) The value must be > 0 4) The value must >= Minimum Regulating Voltage 5) The value must <=Maximum Regulating Voltage 6) Value should be within the range of 10% of the base kV..anything beyond should be a Warning. | T | Float | B/DVE | Joel Koepke |  | N | Y
|  | Capacitor and Reactor Data | X | X | X |  | kV | Minimum Regulating Voltage | Lower limit of voltage specified in the Protocols |  | C | C | Minimum Regulating Voltage | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) The value may not exceed 345(REMOVED) 3) The value must be > 0 4) The value must be <= Maximum Regulating Voltage 5) Warning if value exceeds 50% from Maximum Regulating Voltage 6) Value should be within the range of 10% of the base kV..anything beyond should be a Warning. | T | Float | B/DVE | Joel Koepke |  | N | Y
|  | Capacitor and Reactor Data | X | X | X |  | kV | Maximum Regulating Voltage | Higher limit of voltage specified in the Protocols |  | C | C | Maximum Regulating Voltage | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 3) The value must be > 0 4) The value must be >= Minimum Regulating Voltage 5) Warning if value exceeds 50% from Minimum Regulating Voltage 6) Value should be within the range of 10% of the base kV..anything beyond should be a Warning. | T | Float | B/DVE | Joel Koepke |  | N | Y
|  | Capacitor and Reactor Data | X | X | X |  | p.u. | Zero Sequence Reactance Increment in p.u. | Zero Sequence Reactance Increment in p.u. |  | R | R | Zero Sequence Reactance Increment In p.u. | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 | R |  |  | Model Adminstration |  | N | Y
|  | Capacitor and Reactor Data | X | X | X |  | All Caps | Directly Connected Device 1 | Enter device connected to this capacitor or reactor (can provide up to 10) |  |  | R | Device Name(s) - that this reactive device is directly connected to | 1) This field is optional 2) May not contain special characters except for an underscore "_" and a dash "-" 3) ) May not be > than 17 characters. Warning! Device Name () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. 4)This field should be unique. Every Device entry needs to have a unique “Device Name(s) – that this reactive device is directly connected to". No two capacitors should have the same controlling breaker or switch. 4) 'Connected Device in Capacitor Reactor should have a Controlling Breaker/Switch in Breaker/switch Tab. Audit report should generate an error if the rule fails. For all other equipment that is not a Capacitor/Reactor, they can have connectivity references to transformers, lines, etc. However, for the Capacitor/Reactors, the EMS needs to have a controlling switch modeled, else they would always be "On | T | Alpha | B/DVE | Joel Koepke |  | N | N
|  | Capacitor and Reactor Data | X | X | X |  | All Caps | Directly Connected Device 2 | Enter device connected to this capacitor or reactor (can provide up to 10) |  |  | C
|  | Capacitor and Reactor Data | X | X | X |  | All Caps | Directly Connected Device 3 | Enter device connected to this capacitor or reactor (can provide up to 10) |  |  | C
|  | Capacitor and Reactor Data | X | X | X |  | All Caps | Directly Connected Device 4 | Enter device connected to this capacitor or reactor (can provide up to 10) |  |  | C
|  | Capacitor and Reactor Data | X | X | X |  | All Caps | Directly Connected Device 5 | Enter device connected to this capacitor or reactor (can provide up to 10) |  |  | C
|  | Capacitor and Reactor Data | X | X | X |  | All Caps | Directly Connected Device 6 | Enter device connected to this capacitor or reactor (can provide up to 10) |  |  | C
|  | Capacitor and Reactor Data | X | X | X |  | All Caps | Directly Connected Device 7 | Enter device connected to this capacitor or reactor (can provide up to 10) |  |  | C
|  | Capacitor and Reactor Data | X | X | X |  | All Caps | Directly Connected Device 8 | Enter device connected to this capacitor or reactor (can provide up to 10) |  |  | C
|  | Capacitor and Reactor Data | X | X | X |  | All Caps | Directly Connected Device 9 | Enter device connected to this capacitor or reactor (can provide up to 10) |  |  | C
|  | Capacitor and Reactor Data | X | X | X |  | All Caps | Directly Connected Device 10 | Enter device connected to this capacitor or reactor (can provide up to 10) |  |  | C
|  | Capacitor and Reactor Data | X | X | X |  |  | Comments | Enter any comments regarding this breaker-switch data |  |  | C | COMMENTS | [6 empty] | N | N
|  | Capacitor and Reactor Data | X | X | X |  | mm/dd/yyyy | Effective Date | Date this breaker or switch was added, removed or updated in the model |  |  | R | EFFECTIVE DATE: | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | T | Date | B/DVB | Scott/Woody/Angie |  | N | N