ERCOT System Protection Working Group

Meeting Minutes – July 16, 2014

Austin, TX

- 1:15 pm: SPWG chair Andrew Mattei read the ERCOT Antitrust admonition.  He then passed around the sign-in sheet, email list / roster, and the SPWG contact information list.

- 1:20 pm: Discussion of SPWG calendar

  - Andrew Mattei discussed short circuit case-building dates

  - DME equipment review RFI – October 2014

  - Will ERCOT always put out list of PRC-023-2 circuits with end of May market notice – Andrew to check with Jeff Billo

- 1:27 pm: Review Previous Meeting Minutes – Discussions or carry-over topics included:

  - No comments.

  - Meeting minutes were approved.

- 1:30 pm: System Strength Workshop Discussion

  - No action items for SPWG

  - Generator interconnection process may be affected by issues from workshop

  - Can SPWG provide guidance on a Weighted SCR number (1.5?)

    - Inaccuracy of wind turbine generator model in Aspen

    - Modeling of generator dispatch in short circuit case is not required

    - Aspen isn’t the correct tool for dynamic studies

- 1:42 pm: David Penney TRE Update

  - 1st quarter 2014 Misoperations data review

    - Removed prior quarter’s failure to reclose for accurate data comparison

  - Tertiary connected shunt devices – BES Element

    - Misoperations reportable when guide changed for next full quarter

  - PRC-10,20,21,22 – UVLS

  - Dispersed Generation/Resources

    - PRC-004,005

    - BES Definition change I4

      - >75MVA aggregated at BES interconnection point

  - SDT proposed renaming of SPS to RAS (Remedial Action Scheme)

    - May drive changes to ERCOT guides or protocols

- 2:00 pm: Ed Geer ERCOT Update

  - RARF project with Siemens PTI

    - Wind Turbine type III & IV data

    - Upon Request - Siemens PTI Report ERCOT to provide

    - For equipment ratings and similar studies modeling wind turbine as synchronous machine maybe preferable to get highest fault current.

    - For relay settings studies modeling wind turbines as current limited sources may be preferable to get minimum fault currents.

    - Crowbar circuit operating is individual to the machine and happens during most faults, possible coming in and out during the fault.

    - Short, instantaneous peak of current, up to 5 times nominal, happens within first cycle only - is valuable information in model.

    - Ed Geer, ERCOT to update the System Operations & Planning website that has access to RARF data

    - ERCOT proposes ‘warnings’ in RARF data submittal process when fault currents from wind resource are outside of thresholds. The ‘warnings’ are intended to prompt further investigation.

    - 2-3 cycle values or 4+ cycle values for fault current are both useful pieces of data. For now Aspen is limited to selecting one of two (A or B) current limits at a time.

    - Aspen software program limitation for sub-transient reactance required to be .02 for current limited data. ERCOT will get more info from vendors, more accurate numbers for this data.

- 3:25pm: Kris Koellner Temporary Switching / Temporary Settings

  - Breaker Bypass / Double-Bus Single-Breaker w/ Tie Breaker / Line Tie – 3 Terminal Line

  - Setting changes & timing of changes are a challenge

- 3:50pm: Kris Koellner Phasor Measurement Task Force

  - Key Deliverable report - ERCOT Synchrophasor Technology Assessment

    - Generator Oscillation Detection & Alarming, Generator Model Validation, Post Disturbance Analysis

  - ERCOT Synchrophasor Communication Handbook

- 4:00pm: Bill Blevins ERCOT Updates

  - DME Survey Results –

    - ERCOT created a PowerWorld map to show coverage

    - ERCOT has acceptable coverage everywhere except want to verify CREZ lines in October 2014 DME RFI

- 4:25pm: Andrew Mattei Brazos Electric Event Discussion

- 4:40pm: Bret Burford AEP Event Discussion

  - GE Relay – wiring lugs were arcing during faults only, not steady state

- At 5:00 pm, meeting adjourned.

Day 1 Attendees:

| Andrew Mattei Brazos Electric Danny Ee Austin Energy Kristian Koellner LCRA Peter Belkin AEP Stan Ginsburg Brazos Electric Glenn Hargrave CPS Energy Manjula Datta-Barua CenterPoint Energy Xia Gao Austin Energy Bill Tucker AEP | Dung Nguyen STEC David Penney TRE Brian Clowe CenterPoint Energy Keith Calle CPS Energy Ivan Ivanov Garland Power-Light Genardo Corpuz LCRA Ed Geer ERCOT | WebEx: Bret Burford Derek Merta Eddie Filat Mark Chronister Perry Brown Bill Blevins Armin Klusman Sam Francis |
| --- | --- | --- |