TXU Electric Delivery

Distribution Loss Factor Data

### ERCOT Protocols

Section 13: Transmission and Distribution Losses

October 24, 2006

Section 13.3 Distribution Losses

Excerpt from ERCOT Protocol Section 13.3:

13.3	Distribution Losses

By October 30th of each year for the next calendar year, or two (2) months prior to the posting of any update to the approved Distribution Loss Factor (DLF) codes and calculation each Distribution Service Provider (DSP), except NOIEs, shall calculate and provide ERCOT the Annual DLFs to be applied to distribution voltage level Loads in its area of certification.  ERCOT shall review and approve the DLF calculation methodology used by each DSP prior to use of the loss factors for settlement purposes.  If the DLF calculation methodology does not conform with ERCOT’s interpretation of the Protocol criteria in this subsection, ERCOT will work with the DSP to correct the deficiency.  Until deficiencies are resolved, the last approved  DLF and the calculation methodology will be posted, and the last approved DLFs shall be used for settlement.  A DSP may only submit a change to the DLF calculation methodology annually or when a change in a DSP service area warrants an update to the approved DLF based on the DSP internal evaluation.

The TDSP shall assign a DLF code to each ESI ID.  A maximum of five (5) DLFs may be submitted for each DSP based upon ERCOT approved parameters, such as service voltages or number of transformations.

The following coding standards will be used to identify the DLF applicable to each ESI ID:

- T = Transmission connected Customers (no Distribution Loss Factor applied)

- A through E = TDSP defined Customer segment(s)

The DSPs, except NOIEs, are obligated to provide DLFs to ERCOT.  ERCOT will post the DLF and calculation methodology, including any equations and constants, for each DSP.

Loss factor variables submitted by the DSP shall include:

(1)	The annual DLF for each DLF code;

(2)	The methodology upon which the calculation was made;

(3)	The annual interval average Load for the entire DSP service area used to calculate the annual loss factor for each DLF code;

(4)	The portion of the loss factor that is not sensitive to Load for each DLF code;

[PRR668: Replace the above (1), (2), (3), and (4) with the following upon system implementation:] (1) The annual DLF coefficients (F1, F2, and F3) for each DLF code; and (2) The methodology upon which the calculation of the coefficients (F1, F2, and F3) was made.

13.3.1	Loss Factor Calculation

ERCOT shall use the DLFs submitted by the DSP to calculate the Settlement Interval DLFs.  DLFs will be calculated from the data provided by DSPs as follows using the following equation:

SILFi = ADLF * [ K+(1-K)*(SIELi/AAL)]

Where:

i =	interval

SILFi =	Settlement Interval DLF

ADLF =	Annual DLF

K =	a factor provided by DSP between 0.0 and 1.2

SIELi =	Settlement Interval ERCOT System Load (forecasted or actual)

AAL =	Annual Interval Average ERCOT System Load

And where:

AAL =	Annual Total System MWh / (Number of Settlement Intervals in the year)

[PRR668: Replace the above Section 13.3.1 with the following upon system implementation:] ERCOT shall use the DLFs submitted by the DSP to calculate the Settlement Interval DLFs. DLFs will be calculated from the data provided by DSPs as follows using the following equation: SILFi = F1 * (SIELi/AAL) + F2 + F3 / (SIELi/AAL) Where: i = interval SILFi = Settlement Interval DLF SIELi = Settlement Interval ERCOT System Load (forecasted or actual) AAL = Annual Interval Average ERCOT System Load (forecasted or actual) F1 , F2 , F3 = Coefficients determined by the DSP to allow calculation of its SILF from ERCOT System Load

ERCOT shall use the DLFs calculated for each Settlement Interval of the Operating Day for settlement purposes.

[PRR565: Replace the above sentence with the following on system implementation:] ERCOT shall use the deemed actual DLFs calculated for each Settlement Interval of the Operating Day for settlement purposes.

# Results

- The Annual Distribution Loss Factor Coefficients

Annual Distribution Loss Factors by voltage level, are:

F1(A) = Secondary-voltage coefficient = 0.018458

F2(A) = Secondary-voltage coefficient = 0.000000

F3(A) = Secondary-voltage coefficient = 0.019166

F1(B) = Primary-voltage coefficient = 0.011464

F2(B) = Primary-voltage coefficient = 0.000000

F3(B) = Primary-voltage coefficient = 0.002531

# (2)	The Methodology Upon Which The Calculation Was Made;

- The above annual distribution loss factor coefficients were calculated from data filed in TXU Electric Fuel Factor Docket 23640.

- “Annual” calculations were based on the twelve-month period ending December 31, 2000.

- Attachment 1 contains the calculations for ERCOT Protocol Distribution Loss Factor Coefficients.

- Substation and feeder losses are allocated to secondary and primary classes proportionately as the ratio of the class AAL to the total AAL

|  |  |  |  |  | Attachment 1 |
| --- | --- | --- | --- | --- | --- |
| Calculation of TXU Electric Delivery DLF Coefficients |  |  |  |  |  |
| Docket 23640 |  |  |  |  |  |
| Exhibit DAW-FF-1 |  |  |  |  |  |
| from Table 9 |  |  |  |  |  |
| TXU Electric |  |  |  |  |  |
| Distribution System Components |  |  |  |  |  |
|  | Energy Losses, MWh |  |  | Average Annual Losses, MW |  |
| Component | Load | No-Load |  | Load | No-Load |
| Distribution Substation | 320,993 | 225,303 |  | 36.6 | 25.7 |
| Primary Feeders | 699,585 |  |  | 79.9 |  |
| Line Transformers | 231,169 | 1,289,755 |  | 26.4 | 147.2 |
| Residential Secondary Lines | 108,748 |  |  | 12.4 |  |
| Residential Services | 91,400 |  |  | 10.4 |  |
| Commercial Services | 110,930 |  |  | 12.7 |  |
| Booked kWh for the Year Ended December 31, 2000 |  |  |  | Average Annual Load, MW |  |
| Secondary Booked kWh | 77531467709 |  |  | 8851 |  |
| Primary Booked kWh | 11492407274 |  |  | 1312 |  |
| Losses Due to Secondary-voltage |  |  |  |  |  |
|  | Load | No-Load |  |  |  |
| Distribution Substation | 31.9 | 22.4 |  |  |  |
| Primary Feeders | 69.6 |  |  | F1(A) = | 0.018458 |
| Line Transformers | 26.4 | 147.2 |  |  |  |
| Residential Secondary Lines | 12.4 |  |  | F2(A) = | 0.000000 |
| Residential Services | 10.4 |  |  |  |  |
| Commercial Services | 12.7 |  |  | F3(A) = | 0.019166 |
| Seconday-voltage Losses | 163.4 | 169.6 |  |  |  |
| Losses Due to Primary-voltage |  |  |  |  |  |
|  | Load | No-Load |  | F1(B) = | 0.011464 |
| Distribution Substation | 4.7 | 3.3 |  | F2(B) = | 0.000000 |
| Primary Feeders | 10.3 |  |  |  |  |
|  |  |  |  | F3(B) = | 0.002531 |
| Primary-voltage Losses | 15.0 | 3.3 |  |  |  |