## 1) General Information
Sharyland Utilities, L.P. Distribution Loss Factor for 2014 posting
General Information on Distribution Loss Factor:
The Distribution Loss Factor is a percent that ERCOT will use to determine distribution losses for each Distribution Service Provider.
See ERCOT Protocols Section 13: Transmission and Distribution Losses, which was revised in December, 2010.
This Distribution Loss Factor analysis was conducted by GDS as part of the SU Rate Case test year and filed with the Public Utility Commission of Texas.
Additionally, Sharyland Utilities,L.P. will utilize 3 codes for mapping purposes (A, B, C) all three will map to the attached DL Factor.
The codes were setup to align with each of the EROCT Load Zones where SU has customers supporting the monitoring of loads during the transition to competition in Many 2014.
According to this protocol, ERCOT will calculate Distribution Loss Factors for each Settlement Interval of the Operating Day for
settlement purposes. Distribution Loss Factors will be calculated from the data provided by Distribution Service Providers using
the following equation
SILFi = F1 * (SIELi/AAL) + F2 + F3 / (SIELi / AAL)
Where:
i = interval (15 minutes)
SILFi = Settlement Interval Distribution Loss Factor
SIELi = Settlement Interval estimated ERCOT System Load
AAL = Annual Interval Average ERCOT System Load
F1, F2, F3 = Coefficients derived from regression analysis of the TDSP loss study results
AAL = Annual Total System MWh / (Number of settlement intervals in the year) Typically = 365 days * 24 hrs * 4 intervals
AAL value for use in 2013 =9,290 MWH
Customer Coding for 'Sharyland Utilities, L.P.:
Distribution customers that take service at secondary voltage are coded "A", "B", and "C"
Sharyland Utilities has no customers served from the transmission system.
For "A" Secondary Customers |  |  | For "B" Secondary Customers |  |  | For "C" Secondary Customers
F1 = | 0.0216 |  | F1 = | 0.0216 |  | F1 = | 0.0216
F2 = | 0.0026 |  | F2 = | 0.0026 |  | F2 = | 0.0026
F3 = | 0.0357 |  | F3 = | 0.0357 |  | F3 = | 0.0357
AAL for ERCOT (15 mins) = 9,290 |  |  | AAL for ERCOT (15 mins) = 9,290 |  |  | AAL for ERCOT (15 mins) = 9,290
Assumptions
ERCOT peak load and AAL for ERCOT are proportionately similar to 'Sharyland Utilities, L.P.
|  |  |  | For 15 Mins |  | For 1 Hour
|  |  |  | AAL | Peak | AAL | Peak
|  |  | ERCOT | 9290 | 67663 | 37160 | 270652
|  |  | Sharyland Utilities | 34.2934 | 62.4433 | 137.1734 | 249.773
ERCOT Peak was at 8/1/2012 at 17:00
SU Coincident Peak at 8/1/2012 at 16:30 was 249.77 MW.
For this analysis it is reasonable to assume ERCOT peak and the SU Peak are proportionate
Methodology upon which the calculation of loss factor was made:
Loss equations utilized to determine the loss for each component of the Sharyland Utilities,L.P. system including distribution
substation transformer losses, distribution primary conductor losses, distribution transformer losses and secondary conductor losses.
The following formula was solved for each component with B representing no load losses while A is a constant used to determine load losses
|  | Losses = | AX2 + B
A = Constant
B = Constant
X = Input to System (MW)
The constants (A & B) for each of the equations were updated as follows.
1. Substation Transformer Losses
Sharyland Utilities, L.P. presently has twenty nine distribution substations
The total estimated no-load losses for these units in 2012 is 520.0 kW
The full load losses for each transformer was used to determine the load losses.
The basis for the load losses was the actual 15 minute demands on each transformer.
The peak substation transformer load losses that occur at the system peak of 249 MW is 1.0987 MW.
This resulted in a total of 1.6187 MW of substation transformer losses at approximately 249 MW.
The constants in the system loss equations were adjusted to match this result. See Tab 3) Loss Analysis 2012.
2. Primary Conductor Losses
A computer model of the distribution system was loaded with the system kW demands and power factor
at the time of the ERCOT system peak. The resulting analysis provided the kW losses at that peak demand
value of 249 MW which was 8.058 MW.
The constants (A&B) were determined using the Tab 4) Loss Equations
3. Distribution Transformer Losses
An estimate of the number of distribution transformers was determined by using the number of customers served.
Single phase transformer loss calculations were determined using typical loss values for a 15 kVA transformer.
Three phase transformer bank loss calculations were determined using typical loss values for a 25 kVA transformer.
It was assumed that a three phase service would have (3) 25 kVA transformers.
The "Load" losses were calculated with a utilization factor which is the ratio of peak demand to total transformer capacity.
As the system load grows it anticipated that the utilization factor will increase in future years.
4. Secondary Conductor Losses
Secondary conductor losses were calculated based on an assumed average service length.
The load per consumer was estimated by dividing total load by the number of consumers.
Overall results:
2013
For "A","B",&"C" Secondary Customers |  |  | DLF at AAL | 5.994%
|  |  | DLF at ERCOT Peak | 6.132%
DLF Coefficients (F1, F2 and F3)
The F1, F2 and F3 coefficients were developed for secondary customers codes "A", "B", and "C".
These coefficients were selected to provide a curve fit with the loss equations that were
developed above. The graph in Tab 5) Graphs and in Tab 3 Loss Analysis 2012 depict the curve fitting.
| F1 = | 0.0216
| F2 = | 0.0026
| F3 = | 0.0357

## 2) ERCOT Load Comparison
ERCOT / Sharyland Utilities, L.P. Loading Comparison For 2013
Peak Load | 2013
ERCOT peak (MWh) = | 67663 | (on 8/07/2013 at 16:45)
Peak Interval = | 16915.75
SU peak (MWh) = | 249.773 | (on 8/01/2012 at 16:30)
Peak Interval = | 62.4433 | 0.3691% | = SU peak relative to ERCOT peak
Average Annual Load (AAL)
ERCOT Annual Total System MWH = | 325515268 | (for 01/01/2013 - 12/31/2013)
Intervals per year = | 35136
AAL value = | 9290 | for 15 mins | 37160 | for 1 hour
Assume AAL (Average Annual Load) for SU is proportional to peak in a manner that is similar to ERCOT. The calculation below confirms this simplifying assumption.
AAL for SU would correspond to | 34.2934 | for 15 mins | 137.1734 | for 1 hour
Sharyland Utilities, L.P. Annual Total System Purchases | 1548298.6197 | (1/1/2012-12/31/2012)
Intervals per year = | 35136
AAL value = | 44.0659 | for 15 mins | 176.2635 | for 1 hour
Note on B12: Matt Pamperin: 2012 was leap year.

## Loss Comparison (hidden)
Loss Comparison With Different A/B Constants |  |  |  |  | Loss Analysis 02.xls
|  | Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
|  | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| 1995 | 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07
| 2001 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 2001 Modified | #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF!
| Load |  | Sub Trf Losses |  | Primary Cond Losses |  | Dist Trf Losses |  | Sec Cond Losses |  | Total Losses | Total Losses
| (MW) |  | (MW) | (%) | (MW) | (%) | (MW) | (%) | (MW) | (%) | (MW) | (%)
1995 | 4000 |  | 22.7412 | 0.5685% | 16.6095 | 0.4152% | 106.3877 | 2.66% | 6.3214 | 0.158% | 152.0598 | 3.801%
2001 | 4000 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 4000 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1995 | 7600 |  | 37.0131 | 0.9253% | 60.0587 | 1.501% | 130.2566 | 3.256% | 23.1303 | 0.5783% | 250.4587 | 3.296%
2001 | 7600 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 7600 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1995 | 11200 |  | 60.1434 | 1.504% | 130.3012 | 3.258% | 168.4144 | 4.21% | 50.0129 | 1.25% | 408.8719 | 3.651%
2001 | 11200 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 11200 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Note: All % calculations are based on the total load which is shown in column 2.

## Loss Analysis 1995 (hidden)
HL&P Distribution Loss Analysis |  |  | 1995 |  | Loss Analysis 02.xls | [6 empty] | K = | 0 | K = | 0.8 | K = | 1
|  |  | PELCAR | [7 empty] | Difference |  | Tangent ? | Difference | K Formula | Difference | K Formula | Losses Based | Difference
| Input to Sub Trfs | Sub Trf Losses | Input to Dist Sys | Pri Cond Losses | Input to Dist Trfs | Dist Trf Losses | Input to Secondary | Secondary Losses | Total Losses | Tangent ? | Losses - Tangent | Total Losses | K = 0.0 | Loss - (K=0.0) | K = 0.8 | Loss - (K=0.8) | K = 1.0 | On K = 0.8 | Loss - (K=0.8)
| (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | (%) | (%) | (%) | (%) | (MW) | (MW)
1 | 2400 | 19.2415 | 2380.7585 | 5.9514 | 2374.8071 | 100.482 | 2274.325 | 2.2011 | 127.8761 | 79.0922 | 48.7838 | 5.328% | 1.041% | 4.287% | 2.845% | 2.484% | 3.296% | 68.2691 | 59.607
2 | 2800 | 19.9524 | 2780.0476 | 8.1151 | 2771.9325 | 101.6834 | 2670.2491 | 3.0341 | 132.7851 | 92.2743 | 40.5108 | 4.742% | 1.214% | 3.528% | 2.879% | 1.863% | 3.296% | 80.6186 | 52.1665
3 | 3200 | 20.7726 | 3179.2274 | 10.6129 | 3168.6145 | 103.0686 | 3065.5459 | 3.999 | 138.453 | 105.4563 | 32.9967 | 4.327% | 1.388% | 2.939% | 2.914% | 1.413% | 3.296% | 93.2456 | 45.2075
4 | 3600 | 21.7022 | 3578.2978 | 13.4444 | 3564.8534 | 104.6369 | 3460.2165 | 5.0949 | 144.8784 | 118.6383 | 26.2401 | 4.024% | 1.561% | 2.463% | 2.949% | 1.076% | 3.296% | 106.1501 | 38.7284
5 | 4000 | 22.7412 | 3977.2588 | 16.6095 | 3960.6493 | 106.3877 | 3854.2617 | 6.3214 | 152.0598 | 131.8204 | 20.2394 | 3.801% | 1.734% | 2.067% | 2.983% | 0.8182% | 3.296% | 119.3321 | 32.7277
6 | 4400 | 23.8895 | 4376.1105 | 20.1079 | 4356.0027 | 108.3204 | 4247.6823 | 7.6778 | 159.9955 | 145.0024 | 14.9931 | 3.636% | 1.908% | 1.728% | 3.018% | 0.6183% | 3.296% | 132.7917 | 27.2038
7 | 4800 | 25.1472 | 4774.8528 | 23.9392 | 4750.9137 | 110.4343 | 4640.4793 | 9.1634 | 168.6841 | 158.1844 | 10.4997 | 3.514% | 2.081% | 1.433% | 3.053% | 0.4616% | 3.296% | 146.5287 | 22.1554
8 | 5200 | 26.5142 | 5173.4858 | 28.1032 | 5145.3826 | 112.729 | 5032.6536 | 10.7777 | 178.1241 | 171.3665 | 6.7576 | 3.425% | 2.255% | 1.171% | 3.087% | 0.3381% | 3.296% | 160.5433 | 17.5808
9 | 5600 | 27.9906 | 5572.0094 | 32.5997 | 5539.4098 | 115.2037 | 5424.2061 | 12.52 | 188.3139 | 184.5485 | 3.7654 | 3.363% | 2.428% | 0.9345% | 3.122% | 0.2407% | 3.296% | 174.8354 | 13.4785
10 | 6000 | 29.5764 | 5970.4236 | 37.4283 | 5932.9954 | 117.8578 | 5815.1376 | 14.3897 | 199.2521 | 197.7305 | 1.5216 | 3.321% | 2.602% | 0.7192% | 3.157% | 0.1641% | 3.296% | 189.405 | 9.8471 | Highlighted Area Represents 96% Range
11 | 6400 | 31.2715 | 6368.7285 | 42.5887 | 6326.1398 | 120.6908 | 6205.449 | 16.3862 | 210.9372 | 210.9126 | 0.024651 | 3.296% | 2.775% | 0.5207% | 3.191% | 0.1045% | 3.296% | 204.2522 | 6.685
12 | 6800 | 33.076 | 6766.924 | 48.0808 | 6718.8432 | 123.702 | 6595.1412 | 18.5089 | 223.3677 | 224.0946 | -0.72694 | 3.285% | 2.949% | 0.3362% | 3.226% | 0.05869% | 3.296% | 219.3768 | 3.9908
13 | 7200 | 34.9898 | 7165.0102 | 53.9042 | 7111.1059 | 126.8908 | 6984.2152 | 20.7571 | 236.542 | 237.2766 | -0.73466 | 3.285% | 3.122% | 0.1632% | 3.261% | 0.02449% | 3.296% | 234.779 | 1.763
14 | 7600 | 37.0131 | 7562.9869 | 60.0587 | 7502.9282 | 130.2566 | 7372.6717 | 23.1303 | 250.4587 | 250.4587 | 0 | 3.296% | 3.296% | 0% | 3.296% | 0% | 3.296% | 250.4587 | 0
15 | 8000 | 39.1456 | 7960.8544 | 66.544 | 7894.3104 | 133.7988 | 7760.5116 | 25.6279 | 265.1163 | 263.6407 | 1.4756 | 3.314% | 3.469% | -0.155% | 3.33% | -0.01625% | 3.296% | 266.4159 | -1.2996
16 | 8400 | 41.3876 | 8358.6124 | 73.3597 | 8285.2527 | 137.5168 | 8147.7359 | 28.2492 | 280.5133 | 276.8228 | 3.6905 | 3.339% | 3.642% | -0.303% | 3.365% | -0.02544% | 3.296% | 282.6506 | -2.1373
17 | 8800 | 43.7389 | 8756.2611 | 80.5057 | 8675.7554 | 141.41 | 8534.3454 | 30.9936 | 296.6482 | 290.0048 | 6.6434 | 3.371% | 3.816% | -0.4449% | 3.4% | -0.02858% | 3.296% | 299.1628 | -2.5146
18 | 9200 | 46.1996 | 9153.8004 | 87.9817 | 9065.8188 | 145.4777 | 8920.341 | 33.8606 | 313.5196 | 303.1868 | 10.3328 | 3.408% | 3.989% | -0.5815% | 3.434% | -0.02645% | 3.296% | 315.9526 | -2.433
19 | 9600 | 48.7696 | 9551.2304 | 95.7873 | 9455.4431 | 149.7195 | 9305.7236 | 36.8496 | 331.126 | 316.3689 | 14.7571 | 3.449% | 4.163% | -0.7135% | 3.469% | -0.01973% | 3.296% | 333.0199 | -1.8939
20 | 10000 | 51.449 | 9948.551 | 103.9224 | 9844.6286 | 154.1346 | 9690.494 | 39.9599 | 349.4659 | 329.5509 | 19.915 | 3.495% | 4.336% | -0.8415% | 3.504% | -0.008988% | 3.296% | 350.3646 | -0.89877
21 | 10400 | 54.2378 | 10345.7622 | 112.3865 | 10233.3757 | 158.7226 | 10074.6531 | 43.1909 | 368.5378 | 342.7329 | 25.8049 | 3.544% | 4.51% | -0.966% | 3.538% | 0.005297% | 3.296% | 367.9869 | 0.55086
22 | 10800 | 57.1359 | 10742.8641 | 121.1796 | 10621.6845 | 163.4827 | 10458.2018 | 46.5421 | 388.3403 | 355.915 | 32.4253 | 3.596% | 4.683% | -1.087% | 3.573% | 0.02272% | 3.296% | 385.8868 | 2.4536
23 | 11200 | 60.1434 | 11139.8566 | 130.3012 | 11009.5554 | 168.4144 | 10841.141 | 50.0129 | 408.8719 | 369.097 | 39.7749 | 3.651% | 4.857% | -1.206% | 3.608% | 0.04293% | 3.296% | 404.0641 | 4.8079
24 | 11600 | 63.2602 | 11536.7398 | 139.7512 | 11396.9886 | 173.5171 | 11223.4715 | 53.6027 | 430.1312 | 382.279 | 47.8522 | 3.708% | 5.03% | -1.322% | 3.642% | 0.06562% | 3.296% | 422.5189 | 7.6123
25 | 12000 | 66.4864 | 11933.5136 | 149.5292 | 11783.9844 | 178.7903 | 11605.1941 | 57.3109 | 452.1168 | 395.4611 | 56.6557 | 3.768% | 5.203% | -1.436% | 3.677% | 0.09055% | 3.296% | 441.2513 | 10.8654
26 | 12400 | 69.822 | 12330.178 | 159.635 | 12170.543 | 184.2332 | 11986.3098 | 61.1369 | 474.827 | 408.6431 | 66.1839 | 3.829% | 5.377% | -1.548% | 3.712% | 0.1175% | 3.296% | 460.2612 | 14.5658
27 | 12800 | 73.267 | 12726.733 | 170.0682 | 12556.6648 | 189.8453 | 12366.8195 | 65.0801 | 498.2606 | 421.8251 | 76.4355 | 3.893% | 5.55% | -1.658% | 3.746% | 0.1462% | 3.296% | 479.5486 | 18.712
| % Losses at Peak = | 0.5724% |  | 1.336% |  | 1.512% |  | 0.5262%
400
| Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
| B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | 1995
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2001
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF! | 2001 Modified

## 3) Loss Analysis 2012
|  | Sharyland Utilities, L.P. Distribution Loss Factor For 2014 posting | [13 empty] | Using F1, F2 & F3 Coefficients
ERCOT | ERCOT |  | SU | SU |  |  | Primary | Total | Total |  |  |  | Secondary
Load (15 min) | Load (1 hr) |  | Load (15 min) | Input To Sub Trfs | Sub Trf Losses | Input to Dist Sys | Conductor Losses | Primary Losses | Primary Loss % | Input to Dist Trfs | Dist Trf Losses | Input To Secondary | Conductor Losses | Total Losses | Total Losses | DLF
|  |  |  | (MW) | (MW) | (MW) | (MW) |  |  | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | Secondary
SIEL
|  |  |  | -5.8736 | 0.52061 | -6.3942 | 0.005281 | 0.52589 | -8.953% | -6.3995 | 4.6283 | -11.0279 | 0.0012706 | 5.1555 | -87.77%
|  |  |  | 2.1264 | 0.52008 | 1.6063 | 0.00033326 | 0.52041 | 24.47% | 1.6059 | 4.628 | -3.022 | 9.5413e-05 | 5.1485 | 242.1%
|  |  |  | 10.1264 | 0.52181 | 9.6046 | 0.011915 | 0.53372 | 5.271% | 9.5926 | 4.6288 | 4.9638 | 0.00025742 | 5.1628 | 50.98%
1227.5984 | 4910.3937 |  | 4.5316 | 18.1264 | 0.52579 | 17.6006 | 0.040012 | 0.5658 | 3.121% | 17.5606 | 4.6308 | 12.9297 | 0.0017466 | 5.1984 | 28.68% | 27.56%
1769.3943 | 7077.5772 | 1 | 6.5316 | 26.1264 | 0.53202 | 25.5943 | 0.08461 | 0.61663 | 2.36% | 25.5097 | 4.634 | 20.8757 | 0.004553 | 5.2552 | 20.11% | 19.42%
2311.1902 | 9244.7608 | 2 | 8.5316 | 34.1264 | 0.54051 | 33.5859 | 0.1457 | 0.68621 | 2.011% | 33.4402 | 4.6384 | 28.8018 | 0.0086666 | 5.3333 | 15.63% | 15.15%
2852.9861 | 11411.9443 | 3 | 10.5316 | 42.1264 | 0.55125 | 41.5751 | 0.22326 | 0.77451 | 1.839% | 41.3519 | 4.6439 | 36.7079 | 0.014078 | 5.4325 | 12.9% | 12.55%
3394.782 | 13579.1279 | 4 | 12.5316 | 50.1264 | 0.56425 | 49.5621 | 0.31727 | 0.88153 | 1.759% | 49.2448 | 4.6506 | 44.5942 | 0.020776 | 5.5529 | 11.08% | 10.82%
3936.5779 | 15746.3115 | 5 | 14.5316 | 58.1264 | 0.5795 | 57.5469 | 0.42774 | 1.0072 | 1.733% | 57.1191 | 4.6584 | 52.4607 | 0.028753 | 5.6944 | 9.797% | 9.6%
4478.3738 | 17913.495 | 6 | 16.5316 | 66.1264 | 0.59701 | 65.5294 | 0.55464 | 1.1516 | 1.742% | 64.9747 | 4.6674 | 60.3073 | 0.037997 | 5.8571 | 8.857% | 8.707%
5020.1696 | 20080.6786 | 7 | 18.5316 | 74.1264 | 0.61677 | 73.5096 | 0.69795 | 1.3147 | 1.774% | 72.8116 | 4.6775 | 68.1341 | 0.0485 | 6.0407 | 8.149% | 8.034%
5561.9655 | 22247.8621 | 8 | 20.5316 | 82.1264 | 0.63878 | 81.4876 | 0.85767 | 1.4964 | 1.822% | 80.6299 | 4.6887 | 75.9412 | 0.060251 | 6.2454 | 7.605% | 7.516%
6103.7614 | 24415.0457 | 9 | 22.5316 | 90.1264 | 0.66305 | 89.4633 | 1.0338 | 1.6968 | 1.883% | 88.4295 | 4.701 | 83.7285 | 0.073242 | 6.4711 | 7.18% | 7.113%
6645.5573 | 26582.2292 | 10 | 24.5316 | 98.1264 | 0.68957 | 97.4368 | 1.2263 | 1.9158 | 1.952% | 96.2105 | 4.7145 | 91.496 | 0.087461 | 6.7178 | 6.846% | 6.796%
7187.3532 | 28749.4128 | 11 | 26.5316 | 106.1264 | 0.71835 | 105.408 | 1.4351 | 2.1535 | 2.029% | 103.9729 | 4.729 | 99.2439 | 0.1029 | 6.9854 | 6.582% | 6.546%
7729.1491 | 30916.5964 | 12 | 28.5316 | 114.1264 | 0.74938 | 113.377 | 1.6603 | 2.4097 | 2.111% | 111.7167 | 4.7446 | 106.9721 | 0.11955 | 7.2739 | 6.374% | 6.348%
8270.945 | 33083.7799 | 13 | 30.5316 | 122.1264 | 0.78266 | 121.3437 | 1.9018 | 2.6845 | 2.198% | 119.4419 | 4.7613 | 114.6806 | 0.1374 | 7.5832 | 6.209% | 6.193%
8812.7409 | 35250.9635 | 14 | 32.5316 | 130.1264 | 0.8182 | 129.3082 | 2.1597 | 2.9779 | 2.288% | 127.1485 | 4.7791 | 122.3694 | 0.15644 | 7.9134 | 6.081% | 6.072%
9354.5368 | 37418.147 | 15 | 34.5316 | 138.1264 | 0.856 | 137.2704 | 2.4338 | 3.2898 | 2.382% | 134.8365 | 4.7979 | 130.0386 | 0.17667 | 8.2644 | 5.983% | 5.98%
9896.3326 | 39585.3306 | 16 | 36.5316 | 146.1264 | 0.89604 | 145.2303 | 2.7243 | 3.6203 | 2.478% | 142.506 | 4.8178 | 137.6882 | 0.19806 | 8.6362 | 5.91% | 5.912%
10438.1285 | 41752.5141 | 17 | 38.5316 | 154.1264 | 0.93835 | 153.188 | 3.031 | 3.9693 | 2.575% | 150.157 | 4.8387 | 145.3183 | 0.22062 | 9.0287 | 5.858% | 5.864%
10979.9244 | 43919.6977 | 18 | 40.5316 | 162.1264 | 0.9829 | 161.1435 | 3.354 | 4.3369 | 2.675% | 157.7895 | 4.8607 | 152.9288 | 0.24434 | 9.4419 | 5.824% | 5.833%
11521.7203 | 46086.8813 | 19 | 42.5316 | 170.1264 | 1.0297 | 169.0966 | 3.6932 | 4.7229 | 2.776% | 165.4034 | 4.8837 | 160.5197 | 0.2692 | 9.8758 | 5.805% | 5.817%
12063.5162 | 48254.0648 | 20 | 44.5316 | 178.1264 | 1.0788 | 177.0476 | 4.0487 | 5.1275 | 2.879% | 172.9989 | 4.9077 | 168.0911 | 0.29519 | 10.3304 | 5.799% | 5.814%
12605.3121 | 50421.2484 | 21 | 46.5316 | 186.1264 | 1.1301 | 184.9963 | 4.4204 | 5.5505 | 2.982% | 180.5759 | 4.9328 | 175.6431 | 0.32231 | 10.8056 | 5.806% | 5.822%
13147.108 | 52588.4319 | 22 | 48.5316 | 194.1264 | 1.1837 | 192.9427 | 4.8083 | 5.992 | 3.087% | 188.1344 | 4.9588 | 183.1755 | 0.35055 | 11.3014 | 5.822% | 5.839%
13688.9039 | 54755.6155 | 23 | 50.5316 | 202.1264 | 1.2395 | 200.8869 | 5.2124 | 6.4519 | 3.192% | 195.6744 | 4.9859 | 190.6885 | 0.37989 | 11.8177 | 5.847% | 5.866%
14230.6998 | 56922.799 | 24 | 52.5316 | 210.1264 | 1.2976 | 208.8288 | 5.6327 | 6.9303 | 3.298% | 203.1961 | 5.0139 | 198.1821 | 0.41034 | 12.3546 | 5.88% | 5.899%
14772.4956 | 59089.9826 | 25 | 54.5316 | 218.1264 | 1.3579 | 216.7684 | 6.0692 | 7.4271 | 3.405% | 210.6993 | 5.043 | 205.6563 | 0.44187 | 12.9119 | 5.919% | 5.94%
15314.2915 | 61257.1662 | 26 | 56.5316 | 226.1264 | 1.4205 | 224.7059 | 6.5218 | 7.9423 | 3.512% | 218.1841 | 5.073 | 213.1111 | 0.47449 | 13.4897 | 5.966% | 5.986%
15856.0874 | 63424.3497 | 27 | 58.5316 | 234.1264 | 1.4853 | 232.641 | 6.9905 | 8.4759 | 3.62% | 225.6505 | 5.104 | 220.5465 | 0.50817 | 14.088 | 6.017% | 6.038%
16397.8833 | 65591.5333 | 28 | 60.5316 | 242.1264 | 1.5524 | 240.5739 | 7.4754 | 9.0278 | 3.729% | 233.0985 | 5.1359 | 227.9626 | 0.54292 | 14.7067 | 6.074% | 6.095%
16939.6792 | 67758.7168 | 29 | 62.5316 | 250.1264 | 1.6218 | 248.5046 | 7.9764 | 9.5982 | 3.837% | 240.5282 | 5.1688 | 235.3594 | 0.57873 | 15.3457 | 6.135% | 6.156%
17481.4751 | 69925.9004 | 30 | 64.5316 | 258.1264 | 1.6934 | 256.433 | 8.4934 | 10.1868 | 3.946% | 247.9395 | 5.2027 | 242.7369 | 0.61558 | 16.0051 | 6.2% | 6.222%
18023.271 | 72093.0839 | 31 | 66.5316 | 266.1264 | 1.7673 | 264.3591 | 9.0266 | 10.7939 | 4.056% | 255.3325 | 5.2374 | 250.095 | 0.65346 | 16.6848 | 6.269% | 6.291%
18565.0669 | 74260.2675 | 32 | 68.5316 | 274.1264 | 1.8434 | 272.283 | 9.5758 | 11.4192 | 4.166% | 262.7071 | 5.2732 | 257.434 | 0.69238 | 17.3848 | 6.342% | 6.363%
19106.8628 | 76427.4511 | 33 | 70.5316 | 282.1264 | 1.9217 | 280.2046 | 10.1411 | 12.0629 | 4.276% | 270.0635 | 5.3098 | 264.7537 | 0.73231 | 18.105 | 6.417% | 6.438%
19648.6587 | 78594.6346 | 34 | 72.5316 | 290.1264 | 2.0024 | 288.124 | 10.7225 | 12.7248 | 4.386% | 277.4015 | 5.3474 | 272.0542 | 0.77325 | 18.8454 | 6.496% | 6.516%
9290 | 37160 | AAL | 34.2934 | 137.1734 | 0.85138 | 136.3221 | 2.4003 | 3.2517 | 2.37% | 133.9217 | 4.7956 | 129.1261 | 0.1742 | 8.2215 | 5.994%
16915.75 | 67663 | Peak | 62.4433 | 249.773 | 1.6187 | 248.1543 | 7.9539 | 9.5726 | 3.833% | 240.2004 | 5.1673 | 235.0331 | 0.57712 | 15.317 | 6.132%
For Secondary Distribution Customers "A"
Secondary Constants
|  |  |  | Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
|  |  |  | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant |  |  |  |  | F1 = | 0.0216 | right
|  |  | 2012 Values ----> | 0.52 | 1.7611e-05 | 0 | 0.00012916 | 4.6279 | 9.3488e-06 | 0 | 1.0447e-05 | <--- 2012 Values |  |  |  | F2 = | 0.0026 | middle
[16 empty] | F3 = | 0.0357 | left
DLF = F1 * (SIEL/AAL) + F2 + F3 / (SIEL/AAL)
AAL for ERCOT (15 mins) = 9,308
Secondary Constants
F1 = | 0.0216 | right
F2 = | 0.0026 | middle
F3 = | 0.0357 | left
Note on C11: Kevin Mara: Ratio the Ercot Loading to the Assumed Loading in Col F by using the ratio of the AALs
Note on F48: Kevin Mara: AAL for 1 hour interval same ratio as 15 min AAL to Peak
Note on F49: Kevin Mara: Peak Demand, coincident with ERCOT Peak Demand-8-17-06, 1700 hours
Note on H11: Kevin Mara: Assumed Load (col F) less Sub Transf losses yields input into distrib system

## 4) Loss Equations
System Loss Equations For 'Sharyland Utilities, L.P.
Sharyland Utilities, L.P. Loss Values
| Losses = | AX2 + B
|  | A = Constant | [5 empty] | Coincident Peak Loading (MW) | Coincident Peak Loading (kW)
|  | B = Constant | [5 empty] | 249.773 | 249773.03
X = Input to System (MW)
Substation Transformers |  |  |  | Losses | A | B | X | No Load Losses (MW) | Load Losses (MW) | No Load Losses (kW) | Load Losses (kW) | Total Losses (kW)
| A = | 1.7611e-05 |  | 1.6187 | 1.7611e-05 | 0.52 | 249.773 | 0.52 | 1.0987 | 520 | 1098.6844 | 1618.6844 | 10.42%
| B = | 0.52 | Total No-Load Losses For Substation Transformers = 0.5200 MW
Primary Conductor |  |  |  | Losses | A | B | X | No Load Losses (MW) | Load Losses (MW) | No Load Losses (kW) | Load Losses (kW)
| A = | 0.00012916 |  | 8.058 | 0.00012916 | 0 | 249.773 | 0 | 8.058 | 0 | 8058 | 8058 | 51.85%
| B = | 0
Distribution Transformers |  |  |  | Losses | A | B | X | No Load Losses (MW) | Load Losses (MW) | No Load Losses (kW) | Load Losses (kW)
| A = | 9.3488e-06 |  | 5.2112 | 9.3488e-06 | 4.6279 | 249.773 | 4.6279 | 0.58324 | 4627.944 | 583.2422 | 5211.1862 | 33.53%
| B = | 4.6279 | Total No-Load Losses For Distribution Transformers = 4.6279 MW
Secondary Conductor |  |  |  | Losses | A | B | X | No Load Losses (MW) | Load Losses (MW) | No Load Losses (kW) | Load Losses (kW)
| A = | 1.0447e-05 |  | 0.65178 | 1.0447e-05 | 0 | 249.773 | 0 | 0.65178 | 0 | 651.7821 | 651.7821 | 4.194%
| B = | 0
[11 empty] | Total System Losses | 15539.6528
[11 empty] | Percent System Losses | 6.222%

## 6) power xfmr losses
Substation Power Transformer Losses
Count | Region | Station # | Station Name |  | HS Voltage | LS Voltage | Station Rating | No Load Losses | Full Load Losses | Primary Load Factor | No Load Losses | Load Losses | Total Substation Losses
[5 empty] | KV | KV | (MVA) | (KW) | (KW) | (%) | (KW) | (KW) | (KW) | MVA | NL | LL
1 | SPS | 0032 | Koch | 0032 Koch | 138 | 2.4 | 5 | 10 | 30 | 55.03% | 10 | 16.5095 | 26.5095 | 5 | 10 | 30
2 | SPS | 0162 | Brown | 0162 Brown | 138 | 12.47 | 7.5 | 13 | 48 | 58.76% | 13 | 28.203 | 41.203 | 10 | 13 | 48
3 | SPS | 0274 | Gardendale | 0274 Gardendale | 138 | 24.94 | 20 | 20 | 77 | 47.67% | 20 | 36.7076 | 56.7076 | 15 | 16 | 63
4 | SPS | 0566 | Midkiff | 0566 Midkiff | 138 | 24.94 | 20 | 20 | 77 | 84.44% | 20 | 65.0224 | 85.0224 | 20 | 20 | 77
5 | ERCOT | 1276 | Triangle | 1276 Triangle (ERCOT) | 138 | 12.47 | 20 | 20 | 77 | 76.62% | 20 | 58.9942 | 78.9942 | 25 | 24 | 90
6 | SPS | 1360 | East Midland | 1360 East Midland | 138 | 24.94 | 25 | 24 | 90 | 51.12% | 24 | 46.0052 | 70.0052 | *Loss values from Appendix A of CRN Power Loss Management Book
7 | SPS | 1440 | Salem | 1440 Salem | 138 | 12.47 | 16 | 20 | 77 | 41.77% | 20 | 32.1635 | 52.1635 | (project 01-28) for units with tap changers
8 | SPS | 1548 | Greenwood | 1548 Greenwood | 138 | 12.47 | 20 | 20 | 77 | 55.43% | 20 | 42.6796 | 62.6796
9 | SPS | 1646 | Grady | 1646 Grady | 138 | 24.94 | 20 | 20 | 77 | 75.55% | 20 | 58.1713 | 78.1713
10 | SPS | 1956 | SU 1956 | 1956 | 138 | 24.94 | 20 | 20 | 77 | 30.55% | 20 | 23.5249 | 43.5249
11 | SPS | 2058 | Pembrook | 2058 Pembrook | 138 | 24.94 | 20 | 20 | 77 | 67.59% | 20 | 52.0407 | 72.0407
12 | SPS | 2168 | Stiles | 2168 Stiles | 138 | 24.94 | 20 | 20 | 77 | 73.88% | 20 | 56.8854 | 76.8854
13 | SPS | 2254 | South Midland | 2254 South Midland | 138 | 24.94 | 20 | 20 | 77 | 53.45% | 20 | 41.1578 | 61.1578
14 | SPS | 2372 | St. Lawrence | 2372 St. Lawrence | 138 | 24.94 | 20 | 20 | 77 | 66.28% | 20 | 51.0367 | 71.0367
15 | SPS | 2478 | Vealmoor | 2478 Vealmoor | 138 | 24.94 | 20 | 20 | 77 | 82.42% | 20 | 63.4612 | 83.4612
16 | SPS | 2664 | Fairview | 2664 Fairview | 138 | 12.47 | 16 | 20 | 77 | 68.24% | 20 | 52.5468 | 72.5468
17 | SPS | 2757 | Eiland | 2757 Eiland | 138 | 24.94 | 20 | 20 | 77 | 79.84% | 20 | 61.4772 | 81.4772
18 | SPS | 2850 | Elbow | 2850 Elbow | 138 | 24.94 | 7.5 | 13 | 48 | 74.48% | 13 | 35.7489 | 48.7489
19 | SPS | 3852 | Colorado City | 3852 Colorado City | 138 | 24.94 | 16 | 20 | 77 | 39.87% | 20 | 30.6978 | 50.6978
20 | GP&L | 4084 | 4084 | 4084 | 138 | 24.94 | 25 | 24 | 90 | 27.79% | 24 | 25.0119 | 49.0119
21 | GP&L | 4780 | Floyd | 4780 Floyd | 138 | 24.94 | 25 | 24 | 90 | 39.73% | 24 | 35.7547 | 59.7547
22 | GP&L | 4882 | Farmersville | 4882 Farmersville | 69 | 24.94 | 15 | 16 | 63 | 43.75% | 16 | 27.5626 | 43.5626
23 | LCRA | 5100 | Dutton | 5100 Dutton | 69 | 12.47 | 10 | 13 | 48 | 46.75% | 13 | 22.4408 | 35.4408
24 | LCRA | 5200 | Terry | 5200 Terry | 69 | 12.47 | 5 | 10 | 30 | 32.26% | 10 | 9.6788 | 19.6788
25 | LCRA | 5300 | Eden | 5300 Eden | 69 | 12.47 | 5 | 10 | 30 | 49.39% | 10 | 14.8169 | 24.8169
26 | LCRA | 5500 | C. Bowie | 5500 C. Bowie | 138 | 24.94 | 12 | 20 | 77 | 36.38% | 20 | 28.0161 | 48.0161
27 | LCRA | 5600 | Camp S.S. | 5600 Camp S.S. | 69 | 24.94 | 20 | 20 | 77 | 71.65% | 20 | 55.1682 | 75.1682
28 | LCRA | 5700 | Hext | 5700 Hext | 69 | 12.47 | 7.5 | 13 | 48 | 37.42% | 13 | 17.9631 | 30.9631
29 | LCRA | 5800 | R. Springs | 5800 R. Springs | 69 | 24.94 | 5 | 10 | 30 | 30.79% | 10 | 9.2376 | 19.2376
[10 empty] | Totals | 520 | 1098.6844 | 1618.6844
[12 empty] | % System losses associated with substation transformers | 0.6471%
Note on C9: Matt Pamperin: Listed in the SPS file, but has a note indicating ERCOT.
Note on I3: Matt Pamperin: From McCord work plan for 2012.
Note on I5: Matt Pamperin: 2007 Transmission study shows both 5 and 12 MVA.
Note on J6: Matt Pamperin: Assume losses based on a 10MVA unit.
Note on J11: Matt Pamperin: Assume losses based on a 20 MVA unit.
Note on J20: Matt Pamperin: Assume losses based on a 20 MVA unit.
Note on J22: Matt Pamperin: Assume losses based on a 10MVA unit.
Note on J23: Matt Pamperin: Assume losses based on a 20 MVA unit.
Note on J30: Matt Pamperin: Assume losses based on a 20 MVA unit.
Note on J32: Matt Pamperin: Assume losses based on a 10MVA unit.
Note on L3: Matt Pamperin: See File Titled: Form 7 All Matt Myrick 2012 Cells E775:E815

## 7) distribution line losses
Sharyland Utilities, L.P. Coincident Peak with ERCOT: 249.77 MW on 8/1/2012 at 16:30
Region | DATE | TIME | Modeled System Demand (kW) | System KVAR | System PF | Modeled Distribution System Losses (kW) 1 | Modeled Dist. Losses (% of Actual Peak Demand)
Celeste | 2012-08-01 | 16:30 | 21664.72 | 1113.64 | 99.87% | 403 | 1.86%
Brady | 2012-08-01 | 16:30 | 21922.87 | 1039.4 | 99.89% | 661 | 3.015%
Stanton | 2012-08-01 | 16:30 | 206538.77 | 39509.56 | 98.22% | 6994 | 3.386%
|  | Totals | 250126.36 | 41662.6 | 98.64% | 8058 | 3.222%
Notes:
1. Loss data calculated using Milsoft's WindMill distribution system analysis software.
2. 'Sharyland Utilities, L.P. provided the projected 2012 system model.

## 8) distribution transf losses
Distribution Transformer Losses
Transformer Type 1 | Transformer Size | Quantity | Estimated Installed Capacity | Average No-Load Losses per Transformer | Average Full Load Losses per Transformer | Utilization Factor 4 | Total No-Load Losses | Total Load Losses 3 | Total Transformer Losses (kW)
| (kVA) |  | (kVA) | (kW) | (kW) |  | (kW) | (kW) | (kW)
1-Phase OH Type Transformer for 1-phase Service | 15 | 19098 | 286470 | 0.058 | 0.215 | 0.18649 | 1107.684 | 142.801 | 1250.485
1-Phase OH Type Transformer for 3-phase Service 2 | 25 | 42930 | 1073250 | 0.082 | 0.295 | 0.18649 | 3520.26 | 440.4412 | 3960.7012
|  | Total: | 1359720 |  |  |  | 4627.944 | 583.2422 | 5211.1862
Notes:
1. Typical distribution transformer sizes and loss values were used for this analysis. | [7 empty] | % losses through distribution transformers | 2.083%
2. Assume (3) single-phase distribution transformers for 3-Phase services
3. Peak Losses = (# of units )(Full load losses)(Utilization factor)^2
4. Utilization factor is calculated as shown below:
Utilization Factor
Total kVA Capacity | 1359720
Total kW Demand | 250126.36
Total kVar Demand | 41662.6
Total kVA Demand | 253572.4122
Utilization Factor | 18.65%
Note on C5: Matt Pamperin: Assumed Size
Note on C6: Matt Pamperin: Assume average bank size of 75kVA.
Note on F3: Matt Pamperin: Average Xfmr loss values obtained from CRN "Power Loss Management" Publication.
Note on G3: Matt Pamperin: Average Xfmr loss values obtained from CRN "Power Loss Management" Publication.

## 9) secondary losses
Service Conductor Losses
| Service Type | Average Service Length | Number of Services | Number of Customers per Service | Estimated Load per Service (1) | Load Current at 240 volts | Power Factor (1) | Cable Resistance (2) | Cable Reactance (2) | Voltage Drop Through Service Wire (3) | Line Losses per Service (4) | Total Losses in Service Wire
|  | (Ft) |  |  | (kVA) | (Amps) |  | (Ohms/1000') | (Ohms/1000') | (Volts) | (Watts) | (kW)
| 1/0AL TPX Service Drop | 100 | 28647 | 1 | 5.59 | 23.3 | 0.98641 | 0.1837 | 0.028363 | 0.86612 | 20.1807 | 578.1163
| 4/0 AL QPX Service Drop | 50 | 14310 | 1 | 5.59 | 23.3 | 0.98641 | 0.0917 | 0.026593 | 0.22094 | 5.1479 | 73.6658
[11 empty] | Total Secondary and Service Losses | 651.7821
[11 empty] | % Losses in Secondary Conductors | 0.2606%
(1) | Sharyland Utilities, L.P. System Demand |  | System Demand less distribution line losses, and distribution Transformer losses
| Total kW Demand | 250126.36 | 236857.1738
| Total kVar Demand | 41662.6
| Total kVA Demand | 253572.4122 | 240120.4131
| System Power Factor | 0.98641
| Number of Consumers |  | 42957
| Coincident Peak Load/Consumer (kVA) |  | 5.59
| Assumed Power Factor |  | 0.98641
Impedance Values of 600 volt Cable
(2) | Service Conductor Size | Conductor Diameter (in.) | Insulation Thickness (in.) | Cable Diameter (in.) | A-C Resistance (ohms/1000 ft) | Inductive Reactance (ohms/1000 ft)
| 1/0 TPX | 0.357 | 0.06 | 0.477 | 0.1837 | 0.028363
| 4/0 QPX | 0.506 | 0.06 | 0.626 | 0.0917 | 0.026593
Inductive Reactance Formula (ohms per 1,000 ft.)
Xh=(2*pi*f/1000)*{.0153+.1404*log base 10 (s/r)}
Where:
|  | Xh | Inductive reactance to neutral of one conductor in ohms per 1,000 ft.
|  | f | frequency in hertz (60 hertz)
|  | s | Spacing between the centers of the conductor in inches
|  | r | Radius of the metal portion of the conductor in inches
(3) | Secondary/Service Voltage Drop
Vdservice = (Ih)*(PF)[(Rh)*(2)*(L/1000)]+(Ih)[sin(cos-1(PF))]*{(Xh)*(2)*(L/1000)}
Where:
| Vdservice = | Voltage drop through service conductor in volts
| Ih = | Load current
| kV= | 0.240 kV
| PF= | Power factor of load current expressed as a decimal
| Rh= | Resistance of the service in ohms per 1,000 feet
| Xh= | Reactance of the service in ohms per 1,000 feet
| L= | Length of service conductor
(4) | Secondary/Service Losses
Power Losses = V*Ih
Where:
| V = | Voltage drop through service conductor in volts
| Ih = | Load current
Note on B22: Matt Pamperin: Values from ALCAN catalog data.

## Loss Analysis 2001 Mod (hidden)
HL&P Distribution Loss Analysis |  |  | 2001 Modified |  | Loss Analysis 02.xls | [6 empty] | K = | 0 | K = | 0.8 | K = | 1
|  |  | PELCAR | [7 empty] | Difference |  | Tangent ? | Difference | K Formula | Difference | K Formula | Losses Based | Difference
| Input to Sub Trfs | Sub Trf Losses | Input to Dist Sys | Pri Cond Losses | Input to Dist Trfs | Dist Trf Losses | Input to Secondary | Secondary Losses | Total Losses | Tangent ? | Losses - Tangent | Total Losses | K = 0.0 | Loss - (K=0.0) | K = 0.8 | Loss - (K=0.8) | K = 1.0 | On K = 0.8 | Loss - (K=0.8)
| (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | (%) | (%) | (%) | (%) | (MW) | (MW)
1 | 2400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2 | 2800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | 3200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
4 | 3600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 | 4000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
6 | 4400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
7 | 4800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
8 | 5200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
9 | 5600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
10 | 6000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
11 | 6400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | 6800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | 7200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
14 | 7600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | 8000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
16 | 8400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
17 | 8800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
18 | 9200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
19 | 9600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
20 | 10000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
21 | 10400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
22 | 10800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
23 | 11200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
24 | 11600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
25 | 12000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
26 | 12400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
27 | 12800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| % Losses at Peak = | #REF! |  | #REF! |  | #REF! |  | #REF!
400
| Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
| B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF!
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | 1995
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2001
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF! | 2001 Modified

## Customers Trans (hidden)
Count of Customer ID | Column Labels
Row Labels | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | Grand Total
Large Primary | 24 | 26 | 27 | 33 | 33 | 33 | 35 | 38 | 35 | 36 | 36 | 36 | 392
Large Secondary | 2372 | 2378 | 2415 | 2460 | 2480 | 2508 | 2542 | 2593 | 2629 | 2650 | 2671 | 2689 | 30387
Lights | 33 | 33 | 33 | 33 | 35 | 35 | 35 | 35 | 35 | 35 | 36 | 36 | 414
Lights_UM |  | 3695 | 3705 | 3695 | 3705 | 3704 | 3720 | 3722 | 3717 | 3740 | 3735 | 3734 | 40872
O&G Primary | 249 | 253 | 260 | 266 | 272 | 275 | 279 | 284 | 296 | 296 | 302 | 307 | 3339
O&G Secondary | 10352 | 10379 | 10521 | 10609 | 10752 | 10821 | 10906 | 10964 | 11037 | 11128 | 11184 | 11264 | 129917
Residential | 21093 | 21113 | 21232 | 21298 | 21390 | 21488 | 21596 | 21637 | 21660 | 21777 | 21795 | 21888 | 257967
Small Primary |  | 3 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 32
Small Secondary | 6637 | 6658 | 6728 | 6705 | 6703 | 6738 | 6763 | 6788 | 6810 | 6840 | 6833 | 6869 | 81072
Grand Total | 40760 | 44538 | 44923 | 45102 | 45373 | 45605 | 45879 | 46064 | 46222 | 46505 | 46595 | 46826 | 544392
[8 empty] | 42307 |  |  |  | 43056
| Total | 42307
| Residential | 21637 | 51.14% |  |  |  | Sigma Data
| Other | 20670 | 48.86%
[8 empty] | Revenue Class | Service Type | Quantity |  |  | # Cust. | % | cust/xfmr | # Xfmrs
|  | Single Phase | Three Phase |  |  |  |  | 100 | residential | 26876 | single | Single | 28647 | 66.69% | 1.5 | 19098
Large Primary | 38 |  | 38 |  |  |  |  | 400 | irrigation | 2378 | three | Three | 14310 | 33.31% | 1 | 42930
Large Secondary | 2593 |  | 2593 |  |  |  |  | 550 | Small Commercial | 1771 | single |  | 42957 |  |  | 62028
O&G Primary | 284 |  | 284 |  |  |  |  | 552 | Small Commercial | 0
O&G Secondary | 10964 | 4385.6 | 6578.4 |  | 0.86522 |  |  | 559 | Small Commercial | 11369 | three
Residential | 21637 | 21637 | [5 empty] | 661 | Large Commercial | 124 | three
Small Primary | 3 | 3 | [5 empty] | 669 | Large Commercial | 431 | three
Small Secondary | 6788 | 4751.6 | 2036.4 |  |  |  |  | 660 | Primary Metered | 45
Grand Total | 42307 | 30777.2 | 11207.8 |  |  |  |  | 668 | Primary Metered | 319
[8 empty] | 671 | Cotton Gins | 6 | three
|  | 2.0 cust per Trans | 1 cust per 3 Trans |  |  |  |  | 672 | Cotton Gins | 2 | three
43321
| Transformers | 20518.1333 | 33623.4 | [6 empty] | 364 | Exclude primary metered services
42957
From meter data provided by Sigma. Assumed to be values as of March 2013
Note on R23: Matt Pamperin: Estimate 3 Xfmrs per 3phase service

## Windmil Data (hidden)
Distribution System Line Losses
Region | 2012 CWP Model Loading | Aug 2012 SCADA Loads | % reduction | Model Load Reduced by % | Modeled kW Loads | Modeled kVAR Loads | System KVA Loading | System Load Losses | % Reduced kVAR Losses | PF
| (kW) | (kW) |  |  | (kW) | (kVAR) | (kVA) | (kW)
Celeste | 44648 | 21601.15 | 51.62% | 18% | 21664.72 | 1113.64 | 21722.31 | 403 | 827 | 99.73%
Brady | 43391 | 21844 | 49.66% | 30% | 21922.87 | 1039.4 | 22564.28 | 661 | 1191 | 97.16%
Stanton | 236029 | 206327.88 | 12.58% | 4% | 206538.77 | 39509.56 | 214272.08 | 6994 | 12498 | 96.39%
Total | 324068 | 249773.03 | 22.93% |  | 250126.36 | 41662.6 | 258558.67 | 8058 | 14516 | 96.74%
Notes:
1. Loss data calculated using Milsoft's WindMill distribution system analysis software.
2. Sharyland Utilities provided the projected 2012 system model.