## Slide 1
Jones Creek
Regional Planning Group Project
Jeff Billo
Manager, Transmission Planning
TAC
ERCOT Public
November 20, 2014

## Slide 2: Project Background
Freeport LNG
Announced natural gas liquefaction and export project on Quintana Island
  690 MW total load (no self-serve generation)
  Additional 146 MW load with 82 MW self-serve generation at pretreatment plant (not on Quintana Island)
  Load will come on between 2017 Q3 and 2018 Q3
  Freeport LNG has not yet provided commitment to CenterPoint Energy for project
Project Submission
CenterPoint Energy submitted project for RPG review and comment in July 2014
Project proposal includes new Jones Creek 345/138 kV station and multiple 138 kV system upgrades in the Freeport area

## Slide 3: ERCOT Independent Review
Study Results
Study identified thermal overload and voltage collapse conditions under contingency
ERCOT evaluated two options
Economic analysis did not show additional congestion in the area with proposed project and load addition

## Slide 4: ERCOT Recommendation
Recommendation
ERCOT will request Board of Directors endorsement of the following project (Option B):
  Construct a new 345/138 kV “Jones Creek” Substation
  Install two new 800 MVA normal rating / 1000 MVA emergency rating (800/1000 MVA) 345/138 kV autotransformers at the Jones Creek Substation
  Loop the 345 kV Dow - STP circuit 18 into the Jones Creek Substation
  Loop the 138 kV Freeport - Velasco circuit 59 into the Jones Creek Substation
  Upgrade the Velasco 138 kV Substation to a fault duty rating of 63 kA
  Split and reconfigure circuits in the Freeport area creating: 138 kV Velasco - Surfside - Freeport - Jones Creek circuit 59, 138 kV Velasco - Quintana - Jones Creek circuit 48, and 138 kV Velasco - Jones Creek circuit 59
  Reconfigure 138 kV Velasco - Franklins Camp circuit 02 to create 138 kV Jones Creek - Franklins Camp circuit 02
  Upgrade the 138 kV Jones Creek - Quintana circuit 48 and 138 kV Quintana - Velasco circuit 48 with 838 MVA normal rating / 894 MVA emergency rating (838/894 MVA)
The cost estimate is $77.8 million