## TitlePage
Report on the Capacity, Demand, and Reserves in the ERCOT Region, 2015-2024 December 1, 2014

## Contents
Table of Contents
Tab | Notes
Disclaimer | Please read.
Definitions | List of definitions
Changes from previous CDR | List of changes relative to the last CDR, published May 2014
Executive Summary | Synopsis of considerations for this report
SummerSummary | Shows load forecast, resource capacity and reserve margin for Summer 2015 through Summer 2024
SummerCapacities | List of registered resources and capabilities used in determining the capacity contribution for Summer Peak Season
SummerFuelTypes | Lists generation fuel types by MW and by percentage for Summer 2015 through Summer 2024
WinterSummary | Shows load forecast, resource capacity and reserve margin for Winter 2015/2016 through Winter 2024/2025
WinterCapacities | List of registered resources and capabilities used in determining the capacity contribution for Winter Peak Season
WinterFuelTypes | Lists generation fuel types by MW and by percentage for Winter 2015/2016 through Winter 2024/2025

## Disclaimer
Disclaimer
CDR WORKING PAPER
FOR PLANNING PURPOSES ONLY
This ERCOT Working Paper has been prepared for specific ERCOT and market participant purposes and has been developed from data provided by ERCOT market participants. The data may contain errors or become obsolete and thereby affect the conclusions and opinions of the Working Paper. ERCOT MAKES NO WARRANTY, EXPRESS OR IMPLIED, INCLUDING ANY WARRANTY OF MERCHANTABILITY OR FITNESS FOR ANY PARTICULAR PURPOSE, AND DISCLAIMS ANY AND ALL LIABILITY WITH RESPECT TO THE ACCURACY OF SAME OR THE FITNESS OR APPROPRIATENESS OF SAME FOR ANY PARTICULAR USE. THIS ERCOT WORKING PAPER IS SUPPLIED WITH ALL FAULTS. The specific suitability for any use of the Working Paper and its accuracy should be confirmed by each ERCOT market participant that contributed data for this Working Paper.

## Definitions
Definitions
Mothballed Unit
A generation resource for which a generation entity has submitted a Notification of Suspension of Operations, for which ERCOT has declined to execute an RMR agreement, and for which the generation entity has not announced retirement of the generation resource. A seasonal mothballed unit is one in which the generation entity requests a seasonal operation period that must include the summer Peak Load Season, June 1 through September 30.
Mothballed Capacity
Capacity that is designated as mothballed by a generating unit's owner as described above, and which is not available for operations during the summer Peak Load Season (June, July, August and September) or winter Peak Load Season (December, January and February).
Available Mothballed Capacity based on Owner's Return Probability
Mothballed capacity with a return-to-service probability of 50% or greater for a given season of the year, as provided by its owner, constitutes available mothballed generation. Return probabilities for individual units are considered protected information under the ERCOT Protocols and therefore are not included in this report.
Forecast Zone
Forecast Zones have the same boundaries as the 2003 Congestion Management Zones with an added Panhandle Zone for resources in the Texas Panhandle counties and outside the 2003 Congestion Management Zones.
LRs (Load Resources)
Load capable of reducing or increasing the need for electrical energy or providing Ancillary Services to the ERCOT System, as described in the ERCOT Protocols, Section 6, Ancillary Services. These Resources may provide the following Ancillary Services: Responsive Reserve Service, Non-Spinning Reserve Service, Replacement Reserve Service, and Regulation Service. The Resources must be registered and qualified by ERCOT and will be scheduled by a Qualified Scheduling Entity (QSE).
Non-Synchronous Tie
Any non-synchronous transmission interconnection between ERCOT and non-ERCOT electric power systems.
Private Use Networks
An electric network connected to the ERCOT transmission grid that contains load that is not directly metered by ERCOT (i.e., load that is typically netted with internal generation).
Reliability Must-Run (RMR) Unit
A generation resource unit operated under the terms of an agreement with ERCOT that would not otherwise be operated except that they are necessary to provide voltage support, stability or management of localized transmission constraints under first contingency criteria.
Signed IA (Standard Generation Interconnection Agreement)
An agreement that sets forth requirements for physical connection between an eligible transmission service customer and a transmission or distribution service provider.
Switchable Unit
A generation resource that can be connected to either the ERCOT transmission grid or a grid outside the ERCOT Region.
Wind Seasonal Peak Average Capacity Percentage
The average wind capacity available for the summer and winter Peak Load Seasons for a region (coastal / non-coastal) divided by the installed capacity for the region, expressed as a percentage. Details for the derivation of the percentages are outlined in ERCOT Protocol Section 3.2.6.2.2 (see http://www.ercot.com/content/mktrules/nprotocols/current/03-110114_Nodal.doc).
Wind Peak Average Capacity Contribution
The nameplate capacity of wind resources multiplied by the Seasonal Peak Average Capacity Percentage for coastal and non-coastal regions.

## Changes
Notes on Changes Relative to the Last CDR, Published May 2014
1 | Peak Demand based on the February 2014 load forecast (remains unchanged).
2 | Wind Capacity Contribution changed to historical average of "Top 20" peak load hours over 6 summer seasons (2009-2014) for Summer Period and 5 winter seasons (2009-2013) for Winter Period per the new methodology approved by the ERCOT Board of Directors in October 2014.
3 | Emergency Response Service (ERS) increases due to increased procurement for 2014.
4 | Frontera Generation (FRONTERA_FRONTEG1, FRONTERA_FRONTEG3, FRONTERA_FRONTEG3) has been moved to Switchable Resource status. Switchable Resources Unavailable to ERCOT has been increased by 524 MW for the Summer Peak Period for years 2016-2024.
5 | The following Planned Resources have been moved to Operational Status since the release of the May 2014 CDR report.
| Project Name | GINR | Unit_Code | County | Fuel | ZONE | Capacity MW
| DEER PARK ENERGY CENTER CTG 6 | 14INR0015 | DDPEC_GT6 | HARRIS | GAS | HOUSTON | 165
| PANDA SHERMAN CTG1 | 10INR0021 | PANDA_S_SHER1CT1 | GRAYSON | GAS | NORTH | 196
| PANDA SHERMAN CTG2 | 10INR0021 | PANDA_S_SHER1CT2 | GRAYSON | GAS | NORTH | 195
| PANDA SHERMAN STG | 10INR0021 | PANDA_S_SHER1ST1 | GRAYSON | GAS | NORTH | 326
| PANDA TEMPLE CTG1 | 10INR0020a | PANDA_T1_TMPL1CT1 | BELL | GAS | NORTH | 191.2
| PANDA TEMPLE CTG2 | 10INR0020a | PANDA_T1_TMPL1CT2 | BELL | GAS | NORTH | 191.2
| PANDA TEMPLE STG | 10INR0020a | PANDA_T1_TMPL1ST1 | BELL | GAS | NORTH | 334.7
| FERGUSON REPLACEMENT CTG1 | 13INR0021 | FERGCC_FERGGT1 | LLANO | GAS | SOUTH | 161.9
| FERGUSON REPLACEMENT CTG2 | 13INR0021 | FERGCC_FERGGT2 | LLANO | GAS | SOUTH | 161.9
| FERGUSON REPLACEMENT STG | 13INR0021 | FERGCC_FERGST1 | LLANO | GAS | SOUTH | 186
| BRACKETVILLE SOLAR - OCI ALAMO 4 | 14INR0024 | ECLIPSE_UNIT1 | KINNEY | SOLAR | SOUTH | 37.6
| GOLDTHWAITE WIND | 11INR0013 | GWEC_GWEC_G1 | MILLS | WIND | SOUTH | 149
| PANHANDLE WIND | 14INR0030a_2 | PH1_UNIT1-2 | CARSON | WIND | PANHANDLE | 218
| PANHANDLE WIND 2 | 14INR0030b | PH2_UNIT1-2 | CARSON | WIND | PANHANDLE | 181.7
| SPINNING SPUR WIND TWO | 13INR0048 | SSPURTWO_WIND_1 | OLDHAM | WIND | PANHANDLE | 161
6 | The following Planned Resources have finalized the necessary agreements and permits to be added to the CDR report:
| Project Name | GINR | Unit_Code | County | Fuel | In-Service Yr | Capacity MW
| ANTELOPE STATION | 13INR0028 |  | HALE | GAS | 2016 | 0/359*
| GOLDSMITH PEAKERS | 14INR0039 |  | ECTOR | GAS | 2015 | 380
| LA PALOMA ENERGY CENTER | 16INR0004 |  | CAMERON | GAS | 2016 | 730
| PHR PEAKERS | 14INR0038 |  | GALVESTON | GAS | 2015 | 388
| SKY GLOBAL POWER ONE | 16INR0057 |  | COLORADO | GAS | 2016 | 51
| OCI ALAMO 5 | 15INR0036 |  | UVALDE | SOLAR | 2015 | 105
| CAPROCK WIND | 10INR0009 |  | CASTRO | WIND | 2015 | 300
| JAVELINA WIND ENERGY | 13INR0055 |  | ZAPATA | WIND | 2015 | 250
| LOS VIENTOS IV | 15INR0037 |  | STARR | WIND | 2016 | 200
| LOS VIENTOS V | 15INR0021 |  | STARR | WIND | 2016 | 200
| PALO DURO WIND | 15INR0050 |  | ANDERSON | WIND | 2016 | 203
| PANHANDLE WIND 3 | 14INR0030c |  | CARSON | WIND | 2016 | 248.4
| PULLMAN ROAD | 15INR0079 |  | RANDALL | WIND | 2015 | 300
| SALT FORK WIND | 14INR0062 |  | GRAY | WIND | 2015 | 200
| SCANDIA WIND d | 13INR0010d |  | PARMER | WIND | 2015 | 200
| SCANDIA WIND e | 13INR0010e |  | PARMER | WIND | 2015 | 200
| SCANDIA WIND f | 13INR0010f |  | PARMER | WIND | 2016 | 200
* Summer and winter capacities. Antelope Station will be a Switchable Resource counted during the Winter Peak Season only.
7 | PUN Capacity Contribution changed to historical average of "Top 20" peak load hours (summer and winter) over 3 calendar years (2011-2013).
8 | VH Braunig U2 (BRAUNIG_VHB2, 230 MW, Gas, Bexar County) was moved from Operational Status to Mothball status starting 1/1/2015.
9 | Applied Energy (APD_APD_G1, 138 MW, Coal, Harris County) was moved from Mothball status to Retired status effective 7/2014.
10 | BTU Atkins (ATKINS_ATKINSG3-G6, 109 MW, Gas, Brazos County) was moved from Mothball status to Retired Status effective 5/2014.
11 | Existing Wind Resources, KUNITZ_WIND_NWP and KUNITZ_WIND_LGE (68 MW, Wind, Culberson County), moved to Retired status effective 8/2014.
12 | Planned Wind Resource, Moore Wind (11INR0050, 149MW, Wind, Crosby County), was cancelled by the project sponsor effective 6/2014.
13 | Planned Solar Resource, Mustang Solar Project (13INR0031, 30MW, Solar, Travis County), was cancelled effective 9/2014.

## Executive_Summary
CDR Report - Executive Summary
The methodology for developing this report is defined in Section 3.2.6 of the ERCOT Protocols (see: http://www.ercot.com/content/mktrules/nprotocols/current/03-110114_Nodal.doc). ERCOT has developed this report using data provided by resource owners and by transmission service providers. Although ERCOT works to ensure that the data provided are as accurate and current as possible, ERCOT cannot independently verify all of the information provided. Information available to ERCOT as of November 25, 2014, is included in this report. Planning reserve margins have increased since the release of the May CDR report. New capacity that entered commercial operations since the release of the May 2014 CDR report includes 2,109 MW fueled by natural gas, 710 nameplate MW of wind, and 38 MW of solar. Planned Resources that have finalized the necessary agreements and permits to be added to the CDR report include 1,549 MW of gas, 2,501 nameplate MW of wind, and 105 MW of solar. All of this new CDR-eligible capacity is estimated to enter commercial operations by the summer of 2017. Significant capacity decreases since the May 2014 CDR include the 524 MW Frontera gas-fired plant and a 230 MW unit of the V.H. Braunig gas-fired plant. Information on the Frontera plant, which is scheduled to begin exporting capacity to Mexico in 2015, is available on ERCOT's website (See: http://www.ercot.com/content/news/presentations/2014/FronteraFactSheet_FINAL.pdf). The V.H. Braunig unit will be mothballed effective January 2015. The summer peak capacity percentages for wind resources are 12 percent for non-Coastal resources and 56 percent for Coastal resources, based on a new methodology approved by the ERCOT Board of Directors on October 14, 2014. The new methodology also includes the calculation of winter season peak capacity percentages, which are 19 percent for non-Coastal and 36 percent for Coastal regions. The new summer percentages increase the summer capacity contribution by 1,319 MW, compared to the wind capacity anticipated under the previous approach, which applied a value of 8.7 percent to all resources. ERCOT did not factor into the CDR potential resource capacity impacts of several U.S. Environmental Protection Agency (EPA) regulations that are being implemented or have been proposed. ERCOT continues to analyze the anticipated impacts of these regulations and others on resource adequacy. As ERCOT receives additional information about operational changes and unit retirements, it will incorporate this information in future CDR reports.

## SummerSummary
Report on the Capacity, Demand, and Reserves in the ERCOT Region, 2015-2024
Summer Summary
Load Forecast, MW: |  | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024
| Total Summer Peak Demand (based on normal weather) | 69057 | 70014 | 70871 | 71806 | 72859 | 73784 | 74710 | 75631 | 76550 | 77471
| less: LRs Serving as Responsive Reserve | -1250.928 | -1250.928 | -1250.928 | -1250.928 | -1250.928 | -1250.928 | -1250.928 | -1250.928 | -1250.928 | -1250.928
| less: LRs Serving as Non-Spinning Reserve | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| less: Emergency Response Service (10- and 30-min ramp products) | -826.6 | -1070.8 | -1070.8 | -1070.8 | -1070.8 | -1070.8 | -1070.8 | -1070.8 | -1070.8 | -1070.8
| less: TDSP Standard Offer Load Management Programs | -265.457 | -265.457 | -265.457 | -265.457 | -265.457 | -265.457 | -265.457 | -265.457 | -265.457 | -265.457
| Firm Peak Load, MW | 66714.015 | 67426.815 | 68283.815 | 69218.815 | 70271.815 | 71196.815 | 72122.815 | 73043.815 | 73962.815 | 74883.815
Resources, MW: |  | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024
| Installed Capacity, Thermal/Hydro | 64411.5 | 64411.5 | 64411.5 | 64411.5 | 63571.5 | 63571.5 | 63571.5 | 63571.5 | 63571.5 | 63571.5
| Capacity from Private Use Networks | 4344 | 4344 | 4344 | 4344 | 4344 | 4344 | 4344 | 4344 | 4344 | 4344
| Non-Coastal Wind, Peak Average Capacity Contribution (12%) | 1202.76 | 1202.76 | 1202.76 | 1202.76 | 1202.76 | 1202.76 | 1202.76 | 1202.76 | 1202.76 | 1202.76
| Coastal Wind, Peak Average Capacity Contribution (56%) | 941.024 | 941.024 | 941.024 | 941.024 | 941.024 | 941.024 | 941.024 | 941.024 | 941.024 | 941.024
| RMR Capacity to be under Contract | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operational Generation Capacity, MW | 70899.284 | 70899.284 | 70899.284 | 70899.284 | 70059.284 | 70059.284 | 70059.284 | 70059.284 | 70059.284 | 70059.284
| Capacity Contribution - Non-Synchronous Ties, MW | 516.7 | 516.7 | 516.7 | 516.7 | 516.7 | 516.7 | 516.7 | 516.7 | 516.7 | 516.7
| Switchable Capacity, MW | 3496 | 3496 | 3496 | 3496 | 3496 | 3496 | 3496 | 3496 | 3496 | 3496
| less: Switchable Capacity Unavailable to ERCOT, MW | -470 | -824 | -824 | -824 | -824 | -824 | -524 | -524 | -524 | -524
| Available Mothballed Capacity, MW | 1933 | 1933 | 1933 | 1933 | 1933 | 1933 | 1933 | 1933 | 1933 | 1933
| Planned Resources (not wind) with Signed IA, Air Permits and Water Rights, MW | 324 | 1685.1 | 3118.1 | 3118.1 | 3118.1 | 3358.1 | 3358.1 | 3358.1 | 3358.1 | 3358.1
| Planned Non-Coastal Wind with Signed IA, Peak Average Capacity Contribution (12%) | 353.76 | 936.048 | 1119.168 | 1119.168 | 1119.168 | 1119.168 | 1119.168 | 1119.168 | 1119.168 | 1119.168
| Planned Coastal Wind with Signed IA, Peak Average Capacity Contribution (56%) | 113.12 | 305.2 | 395.36 | 395.36 | 395.36 | 395.36 | 395.36 | 395.36 | 395.36 | 395.36
| less: Retiring Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Capacity, MW | 77165.864 | 78947.332 | 80653.612 | 80653.612 | 79813.612 | 80053.612 | 80353.612 | 80353.612 | 80353.612 | 80353.612
| Reserve Margin | 15.67% | 17.09% | 18.12% | 16.52% | 13.58% | 12.44% | 11.41% | 10.01% | 8.641% | 7.304%
(Total Resources - Firm Load Forecast) / Firm Load Forecast
Report on the Capacity, Demand, and Reserves in the ERCOT Region, 2015-2024
Summer Summary

## SummerCapacities
Unit Capacities - Summer
UNIT NAME | INR | UNIT CODE | COUNTY | FUEL | ZONE | IN SERVICE YR | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024
Operational Resources
COMANCHE PEAK U1 |  | CPSES_UNIT1 | SOMERVELL | NUCLEAR | NORTH | 1990 | 1205 | 1205 | 1205 | 1205 | 1205 | 1205 | 1205 | 1205 | 1205 | 1205
COMANCHE PEAK U2 |  | CPSES_UNIT2 | SOMERVELL | NUCLEAR | NORTH | 1993 | 1195 | 1195 | 1195 | 1195 | 1195 | 1195 | 1195 | 1195 | 1195 | 1195
SOUTH TEXAS U1 |  | STP_STP_G1 | MATAGORDA | NUCLEAR | SOUTH | 1988 | 1286 | 1286 | 1286 | 1286 | 1286 | 1286 | 1286 | 1286 | 1286 | 1286
SOUTH TEXAS U2 |  | STP_STP_G2 | MATAGORDA | NUCLEAR | SOUTH | 1989 | 1295 | 1295 | 1295 | 1295 | 1295 | 1295 | 1295 | 1295 | 1295 | 1295
BIG BROWN U1 |  | BBSES_UNIT1 | FREESTONE | COAL | NORTH | 1971 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
BIG BROWN U2 |  | BBSES_UNIT2 | FREESTONE | COAL | NORTH | 1972 | 595 | 595 | 595 | 595 | 595 | 595 | 595 | 595 | 595 | 595
COLETO CREEK |  | COLETO_COLETOG1 | GOLIAD | COAL | SOUTH | 1980 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660
FAYETTE POWER PROJECT U1 |  | FPPYD1_FPP_G1 | FAYETTE | COAL | SOUTH | 1979 | 604 | 604 | 604 | 604 | 604 | 604 | 604 | 604 | 604 | 604
FAYETTE POWER PROJECT U2 |  | FPPYD1_FPP_G2 | FAYETTE | COAL | SOUTH | 1980 | 599 | 599 | 599 | 599 | 599 | 599 | 599 | 599 | 599 | 599
FAYETTE POWER PROJECT U3 |  | FPPYD2_FPP_G3 | FAYETTE | COAL | SOUTH | 1988 | 437 | 437 | 437 | 437 | 437 | 437 | 437 | 437 | 437 | 437
GIBBONS CREEK U1 |  | GIBCRK_GIB_CRG1 | GRIMES | COAL | NORTH | 1983 | 470 | 470 | 470 | 470 | 470 | 470 | 470 | 470 | 470 | 470
J K SPRUCE U1 |  | CALAVERS_JKS1 | BEXAR | COAL | SOUTH | 1992 | 555 | 555 | 555 | 555 | 555 | 555 | 555 | 555 | 555 | 555
J K SPRUCE U2 | 09INR0002 | CALAVERS_JKS2 | BEXAR | COAL | SOUTH | 2010 | 775 | 775 | 775 | 775 | 775 | 775 | 775 | 775 | 775 | 775
J T DEELY U1 |  | CALAVERS_JTD1 | BEXAR | COAL | SOUTH | 1977 | 420 | 420 | 420 | 420 | 0 | 0 | 0 | 0 | 0 | 0
J T DEELY U2 |  | CALAVERS_JTD2 | BEXAR | COAL | SOUTH | 1978 | 420 | 420 | 420 | 420 | 0 | 0 | 0 | 0 | 0 | 0
LIMESTONE U1 |  | LEG_LEG_G1 | LIMESTONE | COAL | NORTH | 1985 | 831 | 831 | 831 | 831 | 831 | 831 | 831 | 831 | 831 | 831
LIMESTONE U2 |  | LEG_LEG_G2 | LIMESTONE | COAL | NORTH | 1986 | 858 | 858 | 858 | 858 | 858 | 858 | 858 | 858 | 858 | 858
MARTIN LAKE U1 |  | MLSES_UNIT1 | RUSK | COAL | NORTH | 1977 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800
MARTIN LAKE U2 |  | MLSES_UNIT2 | RUSK | COAL | NORTH | 1978 | 805 | 805 | 805 | 805 | 805 | 805 | 805 | 805 | 805 | 805
MONTICELLO U3 |  | MNSES_UNIT3 | TITUS | COAL | NORTH | 1978 | 795 | 795 | 795 | 795 | 795 | 795 | 795 | 795 | 795 | 795
OAK GROVE SES U1 | 09INR0006a | OGSES_UNIT1A | ROBERTSON | COAL | NORTH | 2010 | 840 | 840 | 840 | 840 | 840 | 840 | 840 | 840 | 840 | 840
OAK GROVE SES U2 | 09INR0006b | OGSES_UNIT2 | ROBERTSON | COAL | NORTH | 2011 | 825 | 825 | 825 | 825 | 825 | 825 | 825 | 825 | 825 | 825
OKLAUNION U1 |  | OKLA_OKLA_G1 | WILBARGER | COAL | WEST | 1986 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650
SAN MIGUEL U1 |  | SANMIGL_SANMIGG1 | ATASCOSA | COAL | SOUTH | 1982 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391
SANDOW U5 | 08INR0003 | SD5SES_UNIT5 | MILAM | COAL | SOUTH | 2010 | 570 | 570 | 570 | 570 | 570 | 570 | 570 | 570 | 570 | 570
SANDY CREEK U1 |  | SCES_UNIT1 | MCLENNAN | COAL | NORTH | 2013 | 970 | 970 | 970 | 970 | 970 | 970 | 970 | 970 | 970 | 970
TWIN OAKS U1 |  | TNP_ONE_TNP_O_1 | ROBERTSON | COAL | NORTH | 1990 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156
TWIN OAKS U2 |  | TNP_ONE_TNP_O_2 | ROBERTSON | COAL | NORTH | 1991 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156
W A PARISH U5 |  | WAP_WAP_G5 | FT. BEND | COAL | HOUSTON | 1977 | 659 | 659 | 659 | 659 | 659 | 659 | 659 | 659 | 659 | 659
W A PARISH U6 |  | WAP_WAP_G6 | FT. BEND | COAL | HOUSTON | 1978 | 658 | 658 | 658 | 658 | 658 | 658 | 658 | 658 | 658 | 658
W A PARISH U7 |  | WAP_WAP_G7 | FT. BEND | COAL | HOUSTON | 1980 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577
W A PARISH U8 |  | WAP_WAP_G8 | FT. BEND | COAL | HOUSTON | 1982 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610
A VON ROSENBERG 1 CTG 1 | 00INR0017 | BRAUNIG_AVR1_CT1 | BEXAR | GAS | SOUTH | 2000 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
A VON ROSENBERG 1 CTG 2 | 00INR0017 | BRAUNIG_AVR1_CT2 | BEXAR | GAS | SOUTH | 2000 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
A VON ROSENBERG 1 STG | 00INR0017 | BRAUNIG_AVR1_ST | BEXAR | GAS | SOUTH | 2000 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170
B M DAVIS CTG 3 | 09INR0038 | B_DAVIS_B_DAVIG3 | NUECES | GAS | SOUTH | 2010 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157
B M DAVIS CTG 4 | 09INR0038 | B_DAVIS_B_DAVIG4 | NUECES | GAS | SOUTH | 2010 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157
B M DAVIS STG 2 |  | B_DAVIS_B_DAVIG2 | NUECES | GAS | SOUTH | 1976 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319
BASTROP ENERGY CENTER CTG 1 | 01INR0021 | BASTEN_GTG1100 | BASTROP | GAS | SOUTH | 2002 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
BASTROP ENERGY CENTER CTG 2 | 01INR0021 | BASTEN_GTG2100 | BASTROP | GAS | SOUTH | 2002 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
BASTROP ENERGY CENTER STG | 01INR0021 | BASTEN_ST0100 | BASTROP | GAS | SOUTH | 2002 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233
BOSQUE COUNTY PEAKING CTG 1 | 00INR0018 | BOSQUESW_BSQSU_1 | BOSQUE | GAS | NORTH | 2000 | 143.2 | 143.2 | 143.2 | 143.2 | 143.2 | 143.2 | 143.2 | 143.2 | 143.2 | 143.2
BOSQUE COUNTY PEAKING CTG 2 | 00INR0018 | BOSQUESW_BSQSU_2 | BOSQUE | GAS | NORTH | 2000 | 143.2 | 143.2 | 143.2 | 143.2 | 143.2 | 143.2 | 143.2 | 143.2 | 143.2 | 143.2
BOSQUE COUNTY PEAKING CTG 3 | 00INR0018 | BOSQUESW_BSQSU_3 | BOSQUE | GAS | NORTH | 2001 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2
BOSQUE COUNTY PEAKING STG 4 | 00INR0028 | BOSQUESW_BSQSU_4 | BOSQUE | GAS | NORTH | 2001 | 81.4 | 81.4 | 81.4 | 81.4 | 81.4 | 81.4 | 81.4 | 81.4 | 81.4 | 81.4
BOSQUE COUNTY PEAKING STG 5 | 08INR0046 | BOSQUESW_BSQSU_5 | BOSQUE | GAS | NORTH | 2009 | 190.5 | 190.5 | 190.5 | 190.5 | 190.5 | 190.5 | 190.5 | 190.5 | 190.5 | 190.5
BRAZOS VALLEY CTG 1 | 01INR0031 | BVE_UNIT1 | FORT BEND | GAS | HOUSTON | 2003 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166
BRAZOS VALLEY CTG 2 | 01INR0031 | BVE_UNIT2 | FORT BEND | GAS | HOUSTON | 2003 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166
BRAZOS VALLEY STG 3 | 01INR0031 | BVE_UNIT3 | FORT BEND | GAS | HOUSTON | 2003 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270
CALENERGY (FALCON SEABOARD) CTG 1 |  | FLCNS_UNIT1 | HOWARD | GAS | WEST | 1987 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
CALENERGY (FALCON SEABOARD) CTG 2 |  | FLCNS_UNIT2 | HOWARD | GAS | WEST | 1987 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
CALENERGY (FALCON SEABOARD) STG 3 |  | FLCNS_UNIT3 | HOWARD | GAS | WEST | 1988 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
CEDAR BAYOU CTG 4 | 08INR0035 | CBY4_CT41 | CHAMBERS | GAS | HOUSTON | 2009 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163
CEDAR BAYOU CTG 5 | 08INR0035 | CBY4_CT42 | CHAMBERS | GAS | HOUSTON | 2009 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163
CEDAR BAYOU STG 6 | 08INR0035 | CBY4_ST04 | CHAMBERS | GAS | HOUSTON | 2009 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
COLORADO BEND ENERGY CENTER CTG 1 | 06INR0035 | CBEC_GT1 | WHARTON | GAS | HOUSTON | 2007 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76
COLORADO BEND ENERGY CENTER CTG 2 | 06INR0035 | CBEC_GT2 | WHARTON | GAS | HOUSTON | 2007 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
COLORADO BEND ENERGY CENTER CTG 3 | 06INR0035 | CBEC_GT3 | WHARTON | GAS | HOUSTON | 2008 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
COLORADO BEND ENERGY CENTER CTG 4 | 06INR0035 | CBEC_GT4 | WHARTON | GAS | HOUSTON | 2008 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
COLORADO BEND ENERGY CENTER STG 1 | 06INR0035 | CBEC_STG1 | WHARTON | GAS | HOUSTON | 2007 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103
COLORADO BEND ENERGY CENTER STG 2 | 06INR0035 | CBEC_STG2 | WHARTON | GAS | HOUSTON | 2008 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106
CVC CHANNELVIEW CTG 1 | 02INR0004 | CVC_CVC_G1 | HARRIS | GAS | HOUSTON | 2008 | 155.4 | 155.4 | 155.4 | 155.4 | 155.4 | 155.4 | 155.4 | 155.4 | 155.4 | 155.4
CVC CHANNELVIEW CTG 2 | 02INR0004 | CVC_CVC_G2 | HARRIS | GAS | HOUSTON | 2008 | 165.1 | 165.1 | 165.1 | 165.1 | 165.1 | 165.1 | 165.1 | 165.1 | 165.1 | 165.1
CVC CHANNELVIEW CTG 3 | 02INR0004 | CVC_CVC_G3 | HARRIS | GAS | HOUSTON | 2008 | 163.9 | 163.9 | 163.9 | 163.9 | 163.9 | 163.9 | 163.9 | 163.9 | 163.9 | 163.9
CVC CHANNELVIEW STG 5 | 02INR0004 | CVC_CVC_G5 | HARRIS | GAS | HOUSTON | 2008 | 134.2 | 134.2 | 134.2 | 134.2 | 134.2 | 134.2 | 134.2 | 134.2 | 134.2 | 134.2
DEER PARK ENERGY CENTER CTG 1 | 02INR0020 | DDPEC_GT1 | HARRIS | GAS | HOUSTON | 2002 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181
DEER PARK ENERGY CENTER CTG 2 | 02INR0020 | DDPEC_GT2 | HARRIS | GAS | HOUSTON | 2002 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193
DEER PARK ENERGY CENTER CTG 3 | 02INR0020 | DDPEC_GT3 | HARRIS | GAS | HOUSTON | 2002 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181
DEER PARK ENERGY CENTER CTG 4 | 02INR0020 | DDPEC_GT4 | HARRIS | GAS | HOUSTON | 2002 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193
DEER PARK ENERGY CENTER STG | 02INR0020 | DDPEC_ST1 | HARRIS | GAS | HOUSTON | 2002 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290
DEER PARK ENERGY CENTER CTG 6 | 14INR0015 | DDPEC_GT6 | HARRIS | GAS | HOUSTON | 2014 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
ENNIS POWER STATION CTG 2 | 01INR0008 | ETCCS_CT1 | ELLIS | GAS | NORTH | 2002 | 196 | 196 | 196 | 196 | 196 | 196 | 196 | 196 | 196 | 196
ENNIS POWER STATION STG 1 | 01INR0008 | ETCCS_UNIT1 | ELLIS | GAS | NORTH | 2002 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116
FERGUSON REPLACEMENT CTG1 | 13INR0021 | FERGCC_FERGGT1 | LLANO | GAS | SOUTH | 2014 | 161.9 | 161.9 | 161.9 | 161.9 | 161.9 | 161.9 | 161.9 | 161.9 | 161.9 | 161.9
FERGUSON REPLACEMENT CTG2 | 13INR0021 | FERGCC_FERGGT2 | LLANO | GAS | SOUTH | 2014 | 161.9 | 161.9 | 161.9 | 161.9 | 161.9 | 161.9 | 161.9 | 161.9 | 161.9 | 161.9
FERGUSON REPLACEMENT STG | 13INR0021 | FERGCC_FERGST1 | LLANO | GAS | SOUTH | 2014 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186
FORNEY ENERGY CENTER CTG 11 | 01INR0007 | FRNYPP_GT11 | KAUFMAN | GAS | NORTH | 2003 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168
FORNEY ENERGY CENTER CTG 12 | 01INR0007 | FRNYPP_GT12 | KAUFMAN | GAS | NORTH | 2003 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
FORNEY ENERGY CENTER CTG 13 | 01INR0007 | FRNYPP_GT13 | KAUFMAN | GAS | NORTH | 2003 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
FORNEY ENERGY CENTER CTG 21 | 01INR0007 | FRNYPP_GT21 | KAUFMAN | GAS | NORTH | 2003 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168
FORNEY ENERGY CENTER CTG 22 | 01INR0007 | FRNYPP_GT22 | KAUFMAN | GAS | NORTH | 2003 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
FORNEY ENERGY CENTER CTG 23 | 01INR0007 | FRNYPP_GT23 | KAUFMAN | GAS | NORTH | 2003 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
FORNEY ENERGY CENTER STG 10 | 01INR0007 | FRNYPP_ST10 | KAUFMAN | GAS | NORTH | 2003 | 417 | 417 | 417 | 417 | 417 | 417 | 417 | 417 | 417 | 417
FORNEY ENERGY CENTER STG 20 | 01INR0007 | FRNYPP_ST20 | KAUFMAN | GAS | NORTH | 2003 | 417 | 417 | 417 | 417 | 417 | 417 | 417 | 417 | 417 | 417
FREESTONE ENERGY CENTER CTG 1 | 01INR0009 | FREC_GT1 | FREESTONE | GAS | NORTH | 2002 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6
FREESTONE ENERGY CENTER CTG 2 | 01INR0009 | FREC_GT2 | FREESTONE | GAS | NORTH | 2002 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6
FREESTONE ENERGY CENTER STG 3 | 01INR0009 | FREC_ST3 | FREESTONE | GAS | NORTH | 2002 | 176.2 | 176.2 | 176.2 | 176.2 | 176.2 | 176.2 | 176.2 | 176.2 | 176.2 | 176.2
FREESTONE ENERGY CENTER CTG 4 | 01INR0009 | FREC_GT4 | FREESTONE | GAS | NORTH | 2002 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7
FREESTONE ENERGY CENTER CTG 5 | 01INR0009 | FREC_GT5 | FREESTONE | GAS | NORTH | 2002 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7
FREESTONE ENERGY CENTER STG 6 | 01INR0009 | FREC_ST6 | FREESTONE | GAS | NORTH | 2002 | 174.5 | 174.5 | 174.5 | 174.5 | 174.5 | 174.5 | 174.5 | 174.5 | 174.5 | 174.5
GUADALUPE GEN STN CTG 1 | 01INR0004 | GUADG_GAS1 | GUADALUPE | GAS | SOUTH | 2000 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148
GUADALUPE GEN STN CTG 2 | 01INR0004 | GUADG_GAS2 | GUADALUPE | GAS | SOUTH | 2000 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148
GUADALUPE GEN STN CTG 3 | 01INR0004 | GUADG_GAS3 | GUADALUPE | GAS | SOUTH | 2000 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148
GUADALUPE GEN STN CTG 4 | 01INR0004 | GUADG_GAS4 | GUADALUPE | GAS | SOUTH | 2000 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148
GUADALUPE GEN STN STG 5 | 01INR0004 | GUADG_STM5 | GUADALUPE | GAS | SOUTH | 2000 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197
GUADALUPE GEN STN STG 6 | 01INR0004 | GUADG_STM6 | GUADALUPE | GAS | SOUTH | 2000 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197
HAYS ENERGY FACILITY CSG 1 | 01INR0003 | HAYSEN_HAYSENG1 | HAYS | GAS | SOUTH | 2002 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216
HAYS ENERGY FACILITY CSG 2 | 01INR0003 | HAYSEN_HAYSENG2 | HAYS | GAS | SOUTH | 2002 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216
HAYS ENERGY FACILITY CSG 3 | 01INR0003 | HAYSEN_HAYSENG3 | HAYS | GAS | SOUTH | 2002 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225
HAYS ENERGY FACILITY CSG 4 | 01INR0003 | HAYSEN_HAYSENG4 | HAYS | GAS | SOUTH | 2002 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225
HIDALGO CTG 1 | 00INR0006 | DUKE_DUKE_GT1 | HIDALGO | GAS | SOUTH | 2000 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143
HIDALGO CTG 2 | 00INR0006 | DUKE_DUKE_GT2 | HIDALGO | GAS | SOUTH | 2000 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143
HIDALGO STG | 00INR0006 | DUKE_DUKE_ST1 | HIDALGO | GAS | SOUTH | 2000 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172
JACK COUNTY GEN FACILITY CTG 1 | 05INR0010 | JACKCNTY_CT1 | JACK | GAS | NORTH | 2005 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166
JACK COUNTY GEN FACILITY CTG 2 | 05INR0010 | JACKCNTY_CT2 | JACK | GAS | NORTH | 2005 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
JACK COUNTY GEN FACILITY STG 1 | 05INR0010 | JACKCNTY_STG | JACK | GAS | NORTH | 2005 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295
JACK COUNTY GEN FACILITY CTG 3 | 10INR0010 | JCKCNTY2_CT3 | JACK | GAS | NORTH | 2011 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166
JACK COUNTY GEN FACILITY CTG 4 | 10INR0010 | JCKCNTY2_CT4 | JACK | GAS | NORTH | 2011 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
JACK COUNTY GEN FACILITY STG 2 | 10INR0010 | JCKCNTY2_ST2 | JACK | GAS | NORTH | 2011 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295
JOHNSON COUNTY GEN FACILITY CTG |  | TEN_CT1 | JOHNSON | GAS | NORTH | 1997 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163
JOHNSON COUNTY GEN FACILITY STG |  | TEN_STG | JOHNSON | GAS | NORTH | 1997 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106
LAMAR POWER PROJECT CTG 11 | 00INR0008 | LPCCS_CT11 | LAMAR | GAS | NORTH | 2000 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163
LAMAR POWER PROJECT CTG 12 | 00INR0008 | LPCCS_CT12 | LAMAR | GAS | NORTH | 2000 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153
LAMAR POWER PROJECT CTG 21 | 00INR0008 | LPCCS_CT21 | LAMAR | GAS | NORTH | 2000 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153
LAMAR POWER PROJECT CTG 22 | 00INR0008 | LPCCS_CT22 | LAMAR | GAS | NORTH | 2000 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163
LAMAR POWER PROJECT STG 1 | 00INR0008 | LPCCS_UNIT1 | LAMAR | GAS | NORTH | 2000 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204
LAMAR POWER PROJECT STG 2 | 00INR0008 | LPCCS_UNIT2 | LAMAR | GAS | NORTH | 2000 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204
LOST PINES CTG 1 | 02INR0005 | LOSTPI_LOSTPGT1 | BASTROP | GAS | SOUTH | 2001 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170
LOST PINES CTG 2 | 02INR0005 | LOSTPI_LOSTPGT2 | BASTROP | GAS | SOUTH | 2001 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170
LOST PINES STG | 02INR0005 | LOSTPI_LOSTPST1 | BASTROP | GAS | SOUTH | 2001 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188
MAGIC VALLEY CTG 1 | 00INR0009 | NEDIN_NEDIN_G1 | HIDALGO | GAS | SOUTH | 2001 | 208.6 | 208.6 | 208.6 | 208.6 | 208.6 | 208.6 | 208.6 | 208.6 | 208.6 | 208.6
MAGIC VALLEY CTG 2 | 00INR0009 | NEDIN_NEDIN_G2 | HIDALGO | GAS | SOUTH | 2001 | 208.6 | 208.6 | 208.6 | 208.6 | 208.6 | 208.6 | 208.6 | 208.6 | 208.6 | 208.6
MAGIC VALLEY STG | 00INR0009 | NEDIN_NEDIN_G3 | HIDALGO | GAS | SOUTH | 2001 | 253 | 253 | 253 | 253 | 253 | 253 | 253 | 253 | 253 | 253
MIDLOTHIAN CS 1 | 00INR0012 | MDANP_CT1 | ELLIS | GAS | NORTH | 2001 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235
MIDLOTHIAN CS 2 | 00INR0012 | MDANP_CT2 | ELLIS | GAS | NORTH | 2001 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235
MIDLOTHIAN CS 3 | 00INR0012 | MDANP_CT3 | ELLIS | GAS | NORTH | 2001 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235
MIDLOTHIAN CS 4 | 00INR0012 | MDANP_CT4 | ELLIS | GAS | NORTH | 2001 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235
MIDLOTHIAN CS 5 | 02INR0008 | MDANP_CT5 | ELLIS | GAS | NORTH | 2002 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252
MIDLOTHIAN CS 6 | 02INR0008 | MDANP_CT6 | ELLIS | GAS | NORTH | 2002 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252
NUECES BAY CTG 8 | 09INR0039 | NUECES_B_NUECESG8 | NUECES | GAS | SOUTH | 2010 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157
NUECES BAY CTG 9 | 09INR0039 | NUECES_B_NUECESG9 | NUECES | GAS | SOUTH | 2010 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157
NUECES BAY STG 7 |  | NUECES_B_NUECESG7 | NUECES | GAS | SOUTH | 1972 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319
ODESSA-ECTOR GEN STN CTG 11 | 01INR0026 | OECCS_CT11 | ECTOR | GAS | WEST | 2001 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151
ODESSA-ECTOR GEN STN CTG 12 | 01INR0026 | OECCS_CT12 | ECTOR | GAS | WEST | 2001 | 140.4 | 140.4 | 140.4 | 140.4 | 140.4 | 140.4 | 140.4 | 140.4 | 140.4 | 140.4
ODESSA-ECTOR GEN STN CTG 21 | 01INR0026 | OECCS_CT21 | ECTOR | GAS | WEST | 2001 | 144.7 | 144.7 | 144.7 | 144.7 | 144.7 | 144.7 | 144.7 | 144.7 | 144.7 | 144.7
ODESSA-ECTOR GEN STN CTG 22 | 01INR0026 | OECCS_CT22 | ECTOR | GAS | WEST | 2001 | 142.4 | 142.4 | 142.4 | 142.4 | 142.4 | 142.4 | 142.4 | 142.4 | 142.4 | 142.4
ODESSA-ECTOR GEN STN STG 1 | 01INR0026 | OECCS_UNIT1 | ECTOR | GAS | WEST | 2001 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210
ODESSA-ECTOR GEN STN STG 2 | 01INR0026 | OECCS_UNIT2 | ECTOR | GAS | WEST | 2001 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210
PANDA SHERMAN CTG1 | 10INR0021 | PANDA_S_SHER1CT1 | GRAYSON | GAS | NORTH | 2014 | 196 | 196 | 196 | 196 | 196 | 196 | 196 | 196 | 196 | 196
PANDA SHERMAN CTG2 | 10INR0021 | PANDA_S_SHER1CT2 | GRAYSON | GAS | NORTH | 2014 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195
PANDA SHERMAN STG | 10INR0021 | PANDA_S_SHER1ST1 | GRAYSON | GAS | NORTH | 2014 | 326 | 326 | 326 | 326 | 326 | 326 | 326 | 326 | 326 | 326
PANDA TEMPLE CTG1 | 10INR0020a | PANDA_T1_TMPL1CT1 | BELL | GAS | NORTH | 2014 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195
PANDA TEMPLE CTG2 | 10INR0020a | PANDA_T1_TMPL1CT2 | BELL | GAS | NORTH | 2014 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195
PANDA TEMPLE STG | 10INR0020a | PANDA_T1_TMPL1ST1 | BELL | GAS | NORTH | 2014 | 312 | 312 | 312 | 312 | 312 | 312 | 312 | 312 | 312 | 312
PARIS ENERGY CENTER CTG 1 |  | TNSKA_GT1 | LAMAR | GAS | NORTH | 1989 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76
PARIS ENERGY CENTER CTG 2 |  | TNSKA_GT2 | LAMAR | GAS | NORTH | 1989 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76
PARIS ENERGY CENTER STG |  | TNSKA_STG | LAMAR | GAS | NORTH | 1990 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87
PASGEN CTG 2 |  | PSG_PSG_GT2 | HARRIS | GAS | HOUSTON | 2000 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164
PASGEN CTG 3 |  | PSG_PSG_GT3 | HARRIS | GAS | HOUSTON | 2000 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164
PASGEN STG 2 |  | PSG_PSG_ST2 | HARRIS | GAS | HOUSTON | 2000 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
QUAIL RUN ENERGY CTG 1 | 06INR0036 | QALSW_GT2 | ECTOR | GAS | WEST | 2007 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
QUAIL RUN ENERGY CTG 2 | 06INR0036 | QALSW_GT3 | ECTOR | GAS | WEST | 2008 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
QUAIL RUN ENERGY CTG 3 | 06INR0036 | QALSW_STG1 | ECTOR | GAS | WEST | 2007 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
QUAIL RUN ENERGY CTG 4 | 06INR0036 | QALSW_STG2 | ECTOR | GAS | WEST | 2008 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
QUAIL RUN ENERGY STG 1 | 06INR0036 | QALSW_GT1 | ECTOR | GAS | WEST | 2007 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
QUAIL RUN ENERGY STG 2 | 06INR0036 | QALSW_GT4 | ECTOR | GAS | WEST | 2008 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
SAM RAYBURN CTG 7 | 03INR0014 | RAYBURN_RAYBURG7 | VICTORIA | GAS | SOUTH | 2003 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
RIO NOGALES CTG 1 | 02INR0001 | RIONOG_CT1 | GUADALUPE | GAS | SOUTH | 2002 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154
RIO NOGALES CTG 2 | 02INR0001 | RIONOG_CT2 | GUADALUPE | GAS | SOUTH | 2002 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154
RIO NOGALES CTG 3 | 02INR0001 | RIONOG_CT3 | GUADALUPE | GAS | SOUTH | 2002 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154
RIO NOGALES STG 4 | 02INR0001 | RIONOG_ST1 | GUADALUPE | GAS | SOUTH | 2002 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323
SAM RAYBURN CTG 8 | 03INR0014 | RAYBURN_RAYBURG8 | VICTORIA | GAS | SOUTH | 2003 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
SAM RAYBURN CTG 9 | 03INR0014 | RAYBURN_RAYBURG9 | VICTORIA | GAS | SOUTH | 2003 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
SAM RAYBURN STG 10 | 03INR0014 | RAYBURN_RAYBURG10 | VICTORIA | GAS | SOUTH | 2003 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
SANDHILL ENERGY CENTER CTG 5A | 03INR0033 | SANDHSYD_SH_5A | TRAVIS | GAS | SOUTH | 2004 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
SANDHILL ENERGY CENTER STG 5C | 03INR0033 | SANDHSYD_SH_5C | TRAVIS | GAS | SOUTH | 2004 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145
SILAS RAY STG 6 |  | SILASRAY_SILAS_6 | CAMERON | GAS | SOUTH | 1962 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
SILAS RAY CTG 9 |  | SILASRAY_SILAS_9 | CAMERON | GAS | SOUTH | 1996 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
T H WHARTON CTG 31 |  | THW_THWGT31 | HARRIS | GAS | HOUSTON | 1972 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON CTG 32 |  | THW_THWGT32 | HARRIS | GAS | HOUSTON | 1972 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON CTG 33 |  | THW_THWGT33 | HARRIS | GAS | HOUSTON | 1972 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON CTG 34 |  | THW_THWGT34 | HARRIS | GAS | HOUSTON | 1972 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON STG 3 |  | THW_THWST_3 | HARRIS | GAS | HOUSTON | 1974 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104
T H WHARTON CTG 41 |  | THW_THWGT41 | HARRIS | GAS | HOUSTON | 1972 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON CTG 42 |  | THW_THWGT42 | HARRIS | GAS | HOUSTON | 1972 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON CTG 43 |  | THW_THWGT43 | HARRIS | GAS | HOUSTON | 1974 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON CTG 44 |  | THW_THWGT44 | HARRIS | GAS | HOUSTON | 1974 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON STG 4 |  | THW_THWST_4 | HARRIS | GAS | HOUSTON | 1974 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104
TEXAS CITY CTG A |  | TXCTY_CTA | GALVESTON | GAS | HOUSTON | 2000 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6
TEXAS CITY CTG B |  | TXCTY_CTB | GALVESTON | GAS | HOUSTON | 2000 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6
TEXAS CITY CTG C |  | TXCTY_CTC | GALVESTON | GAS | HOUSTON | 2000 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6
TEXAS CITY STG |  | TXCTY_ST | GALVESTON | GAS | HOUSTON | 2000 | 131.6 | 131.6 | 131.6 | 131.6 | 131.6 | 131.6 | 131.6 | 131.6 | 131.6 | 131.6
VICTORIA POWER STATION CTG 6 | 08INR0050 | VICTORIA_VICTORG6 | VICTORIA | GAS | SOUTH | 2009 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
VICTORIA POWER STATION STG 5 | 08INR0050 | VICTORIA_VICTORG5 | VICTORIA | GAS | SOUTH | 1963 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
WICHITA FALLS CTG 1 |  | WFCOGEN_UNIT1 | WICHITA | GAS | WEST | 1987 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
WICHITA FALLS CTG 2 |  | WFCOGEN_UNIT2 | WICHITA | GAS | WEST | 1987 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
WICHITA FALLS CTG 3 |  | WFCOGEN_UNIT3 | WICHITA | GAS | WEST | 1987 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
WICHITA FALLS STG 4 |  | WFCOGEN_UNIT4 | WICHITA | GAS | WEST | 1987 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
WISE-TRACTEBEL POWER CTG 1 | 02INR0009 | WCPP_CT1 | WISE | GAS | NORTH | 2004 | 212 | 212 | 212 | 212 | 212 | 212 | 212 | 212 | 212 | 212
WISE-TRACTEBEL POWER CTG 2 | 02INR0009 | WCPP_CT2 | WISE | GAS | NORTH | 2004 | 212 | 212 | 212 | 212 | 212 | 212 | 212 | 212 | 212 | 212
WISE-TRACTEBEL POWER STG 1 | 02INR0009 | WCPP_ST1 | WISE | GAS | NORTH | 2004 | 241 | 241 | 241 | 241 | 241 | 241 | 241 | 241 | 241 | 241
WOLF HOLLOW POWER CTG 1 | 01INR0015 | WHCCS_CT1 | HOOD | GAS | NORTH | 2002 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5
WOLF HOLLOW POWER CTG 2 | 01INR0015 | WHCCS_CT2 | HOOD | GAS | NORTH | 2002 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5
WOLF HOLLOW POWER STG | 01INR0015 | WHCCS_STG | HOOD | GAS | NORTH | 2002 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280
ATKINS 7 |  | ATKINS_ATKINSG7 | BRAZOS | GAS | NORTH | 1973 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
DANSBY CTG 2 |  | DANSBY_DANSBYG2 | BRAZOS | GAS | NORTH | 2004 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
DANSBY CTG 3 | 09INR0072 | DANSBY_DANSBYG3 | BRAZOS | GAS | NORTH | 2010 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
DECKER CREEK CTG 1 |  | DECKER_DPGT_1 | TRAVIS | GAS | SOUTH | 1989 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
DECKER CREEK CTG 2 |  | DECKER_DPGT_2 | TRAVIS | GAS | SOUTH | 1989 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
DECKER CREEK CTG 3 |  | DECKER_DPGT_3 | TRAVIS | GAS | SOUTH | 1989 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
DECKER CREEK CTG 4 |  | DECKER_DPGT_4 | TRAVIS | GAS | SOUTH | 1989 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
DECORDOVA CTG 1 |  | DCSES_CT10 | HOOD | GAS | NORTH | 1990 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71
DECORDOVA CTG 2 |  | DCSES_CT20 | HOOD | GAS | NORTH | 1990 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
DECORDOVA CTG 3 |  | DCSES_CT30 | HOOD | GAS | NORTH | 1990 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
DECORDOVA CTG 4 |  | DCSES_CT40 | HOOD | GAS | NORTH | 1990 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68
EXTEX LAPORTE GEN STN CTG 1 | 01INR0044 | AZ_AZ_G1 | HARRIS | GAS | HOUSTON | 2009 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
EXTEX LAPORTE GEN STN CTG 2 | 01INR0044 | AZ_AZ_G2 | HARRIS | GAS | HOUSTON | 2009 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
EXTEX LAPORTE GEN STN CTG 3 | 01INR0044 | AZ_AZ_G3 | HARRIS | GAS | HOUSTON | 2009 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
EXTEX LAPORTE GEN STN CTG 4 | 01INR0044 | AZ_AZ_G4 | HARRIS | GAS | HOUSTON | 2009 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
GREENS BAYOU CTG 73 |  | GBY_GBYGT73 | HARRIS | GAS | HOUSTON | 1976 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
GREENS BAYOU CTG 74 |  | GBY_GBYGT74 | HARRIS | GAS | HOUSTON | 1976 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
GREENS BAYOU CTG 81 |  | GBY_GBYGT81 | HARRIS | GAS | HOUSTON | 1976 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
GREENS BAYOU CTG 83 |  | GBY_GBYGT83 | HARRIS | GAS | HOUSTON | 1976 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
GREENS BAYOU CTG 84 |  | GBY_GBYGT84 | HARRIS | GAS | HOUSTON | 1976 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
GREENVILLE ENGINE PLANT | 10INR0070 | STEAM_ENGINE_1 | HUNT | GAS | NORTH | 2010 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4
GREENVILLE ENGINE PLANT | 10INR0070 | STEAM_ENGINE_2 | HUNT | GAS | NORTH | 2010 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4
GREENVILLE ENGINE PLANT | 10INR0070 | STEAM_ENGINE_3 | HUNT | GAS | NORTH | 2010 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4
LAREDO CTG 4 | 08INR0064 | LARDVFTN_G4 | WEBB | GAS | SOUTH | 2008 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2
LAREDO CTG 5 | 08INR0064 | LARDVFTN_G5 | WEBB | GAS | SOUTH | 2008 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2
LEON CREEK PEAKER CTG 1 | 04INR0009 | LEON_CRK_LCPCT1 | BEXAR | GAS | SOUTH | 2004 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
LEON CREEK PEAKER CTG 2 | 04INR0009 | LEON_CRK_LCPCT2 | BEXAR | GAS | SOUTH | 2004 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
LEON CREEK PEAKER CTG 3 | 04INR0009 | LEON_CRK_LCPCT3 | BEXAR | GAS | SOUTH | 2004 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
LEON CREEK PEAKER CTG 4 | 04INR0009 | LEON_CRK_LCPCT4 | BEXAR | GAS | SOUTH | 2004 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
MORGAN CREEK CTG 1 |  | MGSES_CT1 | MITCHELL | GAS | WEST | 1988 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68
MORGAN CREEK CTG 2 |  | MGSES_CT2 | MITCHELL | GAS | WEST | 1988 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68
MORGAN CREEK CTG 3 |  | MGSES_CT3 | MITCHELL | GAS | WEST | 1988 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68
MORGAN CREEK CTG 4 |  | MGSES_CT4 | MITCHELL | GAS | WEST | 1988 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68
MORGAN CREEK CTG 5 |  | MGSES_CT5 | MITCHELL | GAS | WEST | 1988 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68
MORGAN CREEK CTG 6 |  | MGSES_CT6 | MITCHELL | GAS | WEST | 1988 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67
PEARSALL IC ENGINE PLANT A | 09INR0079a | PEARSAL2_AGR_A | FRIO | GAS | SOUTH | 2012 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
PEARSALL IC ENGINE PLANT B | 09INR0079a | PEARSAL2_AGR_B | FRIO | GAS | SOUTH | 2012 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
PEARSALL IC ENGINE PLANT C | 09INR0079b | PEARSAL2_AGR_C | FRIO | GAS | SOUTH | 2012 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
PEARSALL IC ENGINE PLANT D | 09INR0079b | PEARSAL2_AGR_D | FRIO | GAS | SOUTH | 2012 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
PERMIAN BASIN CTG 1 |  | PB2SES_CT1 | WARD | GAS | WEST | 1988 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68
PERMIAN BASIN CTG 2 |  | PB2SES_CT2 | WARD | GAS | WEST | 1988 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
PERMIAN BASIN CTG 3 |  | PB2SES_CT3 | WARD | GAS | WEST | 1988 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68
PERMIAN BASIN CTG 4 |  | PB2SES_CT4 | WARD | GAS | WEST | 1990 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
PERMIAN BASIN CTG 5 |  | PB2SES_CT5 | WARD | GAS | WEST | 1990 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
R W MILLER CTG 4 |  | MIL_MILLERG4 | PALO PINTO | GAS | NORTH | 2000 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104
R W MILLER CTG 5 |  | MIL_MILLERG5 | PALO PINTO | GAS | NORTH | 2000 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104
RAY OLINGER CTG 4 | 00INR0024 | OLINGR_OLING_4 | COLLIN | GAS | NORTH | 2001 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
SAM RAYBURN CTG 1 |  | RAYBURN_RAYBURG1 | VICTORIA | GAS | SOUTH | 1963 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
SAM RAYBURN CTG 2 |  | RAYBURN_RAYBURG2 | VICTORIA | GAS | SOUTH | 1963 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
SAN JACINTO SES CTG 1 |  | SJS_SJS_G1 | HARRIS | GAS | HOUSTON | 1995 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
SAN JACINTO SES CTG 2 |  | SJS_SJS_G2 | HARRIS | GAS | HOUSTON | 1995 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
SANDHILL ENERGY CENTER CTG 1 | 01INR0041 | SANDHSYD_SH1 | TRAVIS | GAS | SOUTH | 2001 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
SANDHILL ENERGY CENTER CTG 2 | 01INR0041 | SANDHSYD_SH2 | TRAVIS | GAS | SOUTH | 2001 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
SANDHILL ENERGY CENTER CTG 3 | 01INR0041 | SANDHSYD_SH3 | TRAVIS | GAS | SOUTH | 2001 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
SANDHILL ENERGY CENTER CTG 4 | 01INR0041 | SANDHSYD_SH4 | TRAVIS | GAS | SOUTH | 2001 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
SANDHILL ENERGY CENTER CTG 6 | 09INR0045 | SANDHSYD_SH6 | TRAVIS | GAS | SOUTH | 2010 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
SANDHILL ENERGY CENTER CTG 7 | 09INR0045 | SANDHSYD_SH7 | TRAVIS | GAS | SOUTH | 2010 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
SILAS RAY CTG 10 | 04INR0014 | SILASRAY_SILAS_10 | CAMERON | GAS | SOUTH | 2004 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
T H WHARTON CTG 51 |  | THW_THWGT51 | HARRIS | GAS | HOUSTON | 1975 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON CTG 52 |  | THW_THWGT52 | HARRIS | GAS | HOUSTON | 1975 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON CTG 53 |  | THW_THWGT53 | HARRIS | GAS | HOUSTON | 1975 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON CTG 54 |  | THW_THWGT54 | HARRIS | GAS | HOUSTON | 1975 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON CTG 55 |  | THW_THWGT55 | HARRIS | GAS | HOUSTON | 1975 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON CTG 56 |  | THW_THWGT56 | HARRIS | GAS | HOUSTON | 1975 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON CTG G1 |  | THW_THWGT_1 | HARRIS | GAS | HOUSTON | 1967 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
TEXAS GULF SULPHUR |  | TGF_TGFGT_1 | WHARTON | GAS | HOUSTON | 1985 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
V H BRAUNIG CTG 5 | 09INR0028 | BRAUNIG_VHB6CT5 | BEXAR | GAS | SOUTH | 2009 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
V H BRAUNIG CTG 6 | 09INR0028 | BRAUNIG_VHB6CT6 | BEXAR | GAS | SOUTH | 2009 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
V H BRAUNIG CTG 7 | 09INR0028 | BRAUNIG_VHB6CT7 | BEXAR | GAS | SOUTH | 2009 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
V H BRAUNIG CTG 8 | 09INR0028 | BRAUNIG_VHB6CT8 | BEXAR | GAS | SOUTH | 2009 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
W A PARISH CTG 1 |  | WAP_WAPGT_1 | FT. BEND | GAS | HOUSTON | 1967 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
W A PARISH - PETRA NOVA CTG | 12INR0086 | PNPI_GT2 | FORT BEND | GAS | HOUSTON | 2013 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
WINCHESTER POWER PARK CTG 1 | 09INR0027 | WIPOPA_WPP_G1 | FAYETTE | GAS | SOUTH | 2009 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
WINCHESTER POWER PARK CTG 2 | 09INR0027 | WIPOPA_WPP_G2 | FAYETTE | GAS | SOUTH | 2009 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
WINCHESTER POWER PARK CTG 3 | 09INR0027 | WIPOPA_WPP_G3 | FAYETTE | GAS | SOUTH | 2009 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
WINCHESTER POWER PARK CTG 4 | 09INR0027 | WIPOPA_WPP_G4 | FAYETTE | GAS | SOUTH | 2009 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
B M DAVIS STG U1 |  | B_DAVIS_B_DAVIG1 | NUECES | GAS | SOUTH | 1974 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335
CEDAR BAYOU STG U1 |  | CBY_CBY_G1 | CHAMBERS | GAS | HOUSTON | 1970 | 745 | 745 | 745 | 745 | 745 | 745 | 745 | 745 | 745 | 745
CEDAR BAYOU STG U2 |  | CBY_CBY_G2 | CHAMBERS | GAS | HOUSTON | 1972 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749
DANSBY STG U1 |  | DANSBY_DANSBYG1 | BRAZOS | GAS | NORTH | 1978 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
DECKER CREEK STG U1 |  | DECKER_DPG1 | TRAVIS | GAS | SOUTH | 1971 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315
DECKER CREEK STG U2 |  | DECKER_DPG2 | TRAVIS | GAS | SOUTH | 1978 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
GRAHAM STG U1 |  | GRSES_UNIT1 | YOUNG | GAS | WEST | 1960 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225
GRAHAM STG U2 |  | GRSES_UNIT2 | YOUNG | GAS | WEST | 1969 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390
GREENS BAYOU STG U5 |  | GBY_GBY_5 | HARRIS | GAS | HOUSTON | 1973 | 371 | 371 | 371 | 371 | 371 | 371 | 371 | 371 | 371 | 371
HANDLEY STG U3 |  | HLSES_UNIT3 | TARRANT | GAS | NORTH | 1963 | 395 | 395 | 395 | 395 | 395 | 395 | 395 | 395 | 395 | 395
HANDLEY STG U4 |  | HLSES_UNIT4 | TARRANT | GAS | NORTH | 1976 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435
HANDLEY STG U5 |  | HLSES_UNIT5 | TARRANT | GAS | NORTH | 1977 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435
LAKE HUBBARD STG U1 |  | LHSES_UNIT1 | DALLAS | GAS | NORTH | 1970 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392
LAKE HUBBARD STG U2 |  | LHSES_UNIT2A | DALLAS | GAS | NORTH | 1973 | 515 | 515 | 515 | 515 | 515 | 515 | 515 | 515 | 515 | 515
MOUNTAIN CREEK STG U6 |  | MCSES_UNIT6 | DALLAS | GAS | NORTH | 1956 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
MOUNTAIN CREEK STG U7 |  | MCSES_UNIT7 | DALLAS | GAS | NORTH | 1958 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115
MOUNTAIN CREEK STG U8 |  | MCSES_UNIT8 | DALLAS | GAS | NORTH | 1967 | 565 | 565 | 565 | 565 | 565 | 565 | 565 | 565 | 565 | 565
O W SOMMERS STG U1 |  | CALAVERS_OWS1 | BEXAR | GAS | SOUTH | 1972 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
O W SOMMERS STG U2 |  | CALAVERS_OWS2 | BEXAR | GAS | SOUTH | 1974 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
PEARSALL STG U1 |  | PEARSALL_PEARS_1 | FRIO | GAS | SOUTH | 1961 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
PEARSALL STG U2 |  | PEARSALL_PEARS_2 | FRIO | GAS | SOUTH | 1961 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
PEARSALL STG U3 |  | PEARSALL_PEARS_3 | FRIO | GAS | SOUTH | 1961 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
POWERLANE PLANT STG U1 |  | STEAM1A_STEAM_1 | HUNT | GAS | NORTH | 1966 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
POWERLANE PLANT STG U2 |  | STEAM_STEAM_2 | HUNT | GAS | NORTH | 1967 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
POWERLANE PLANT STG U3 |  | STEAM_STEAM_3 | HUNT | GAS | NORTH | 1978 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41
R W MILLER STG U1 |  | MIL_MILLERG1 | PALO PINTO | GAS | NORTH | 2000 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
R W MILLER STG U2 |  | MIL_MILLERG2 | PALO PINTO | GAS | NORTH | 2000 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
R W MILLER STG U3 |  | MIL_MILLERG3 | PALO PINTO | GAS | NORTH | 2000 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208
RAY OLINGER STG U1 |  | OLINGR_OLING_1 | COLLIN | GAS | NORTH | 1967 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
RAY OLINGER STG U2 |  | OLINGR_OLING_2 | COLLIN | GAS | NORTH | 1971 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107
RAY OLINGER STG U3 |  | OLINGR_OLING_3 | COLLIN | GAS | NORTH | 1975 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146
SIM GIDEON STG U1 |  | GIDEON_GIDEONG1 | BASTROP | GAS | SOUTH | 1965 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130
SIM GIDEON STG U2 |  | GIDEON_GIDEONG2 | BASTROP | GAS | SOUTH | 1968 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135
SIM GIDEON STG U3 |  | GIDEON_GIDEONG3 | BASTROP | GAS | SOUTH | 1972 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336
SPENCER STG U4 |  | SPNCER_SPNCE_4 | DENTON | GAS | NORTH | 1966 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
SPENCER STG U5 |  | SPNCER_SPNCE_5 | DENTON | GAS | NORTH | 1973 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
STRYKER CREEK STG U1 |  | SCSES_UNIT1A | CHEROKEE | GAS | NORTH | 1958 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
STRYKER CREEK STG U2 |  | SCSES_UNIT2 | CHEROKEE | GAS | NORTH | 1965 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502
TRINIDAD STG U6 |  | TRSES_UNIT6 | HENDERSON | GAS | NORTH | 1965 | 226 | 226 | 226 | 226 | 226 | 226 | 226 | 226 | 226 | 226
V H BRAUNIG STG U1 |  | BRAUNIG_VHB1 | BEXAR | GAS | SOUTH | 1966 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
V H BRAUNIG STG U3 |  | BRAUNIG_VHB3 | BEXAR | GAS | SOUTH | 1970 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412
W A PARISH STG U1 |  | WAP_WAP_G1 | FT. BEND | GAS | HOUSTON | 1958 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
W A PARISH STG U2 |  | WAP_WAP_G2 | FT. BEND | GAS | HOUSTON | 1958 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
W A PARISH STG U3 |  | WAP_WAP_G3 | FT. BEND | GAS | HOUSTON | 1961 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 246
W A PARISH STG U4 |  | WAP_WAP_G4 | FT. BEND | GAS | HOUSTON | 1968 | 536 | 536 | 536 | 536 | 536 | 536 | 536 | 536 | 536 | 536
NOTREES BATTERY | 12INR0076 | NWF_NBS | WINKLER/ECTOR | STORAGE | WEST | 2012 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7
ACACIA SOLAR |  | ACACIA_UNIT_1 | PRESIDIO | SOLAR | WEST | 2012 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
BRACKETVILLE SOLAR - OCI ALAMO 4 | 14INR0024 | ECLIPSE_UNIT1 | KINNEY | SOLAR | SOUTH | 2014 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6
OCI ALAMO 1 SOLAR | 13INR0058 | OCI_ALM1_UNIT1 | BEXAR | SOLAR | SOUTH | 2013 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2
WEBBERVILLE SOLAR | 10INR0082 | WEBBER_S_WSP1 | TRAVIS | SOLAR | SOUTH | 2011 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
BLUE WING 1 |  | DG_BROOK_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6
BLUE WING 2 |  | DG_ELMEN_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3
SOMERSET 1 |  | DG_SOME1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6
SOMERSET 2 |  | DG_SOME2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
SUNEDISON RABEL ROAD |  | DG_VALL1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SUNEDISON VALLEY ROAD |  | DG_VALL2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
NACOGDOCHES POWER | 09INR0007 | NACPW_UNIT1 | NACOGDOCHES | BIOMASS | NORTH | 2012 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105
LUFKIN BIOMASS | 08INR0033 | LFBIO_UNIT1 | ANGELINA | BIOMASS | NORTH | 2012 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
ALVIN |  | AV_DG1 | GALVESTON | BIOMASS | HOUSTON | 2002 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7
AUSTIN LANDFILL GAS |  | DG_SPRIN_4UNITS | TRAVIS | BIOMASS | SOUTH | 2007 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4
COVEL GARDENS POWER STATION |  | DG_MEDIN_1UNIT | BEXAR | BIOMASS | SOUTH | 2005 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
DFW GAS RECOVERY |  | DG_BIO2_4UNITS | DENTON | BIOMASS | NORTH | 2009 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4
DG_BIOENERGY PARTNERS |  | DG_BIOE_2UNITS | DENTON | BIOMASS | NORTH | 1988 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2
FW REGION GEN FACILITY |  | DG_RDLML_1UNIT | TARRANT | BIOMASS | NORTH | 2011 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
HUMBLE |  | HB_DG1 | HARRIS | BIOMASS | HOUSTON | 2002 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
LIBERTY |  | LB_DG1 | HARRIS | BIOMASS | HOUSTON | 2002 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9
MCKINNEY LANDFILL |  | DG_MKNSW_2UNITS | COLLIN | BIOMASS | NORTH | 2011 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
MESQUITE CREEK ENERGY |  | DG_FREIH_2UNITS | COMAL | BIOMASS | SOUTH | 2011 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
SKYLINE LANDFILL GAS |  | DG_FERIS_4_UNITS | DALLAS | BIOMASS | NORTH | 2007 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4
TRINITY BAY |  | TRN_DG1 | CHAMBERS | BIOMASS | HOUSTON | 2002 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9
TRINITY OAKS LFG |  | DG_KLBRG_1UNIT | DALLAS | BIOMASS | NORTH | 2011 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
WALZEM ROAD |  | DG_WALZE_4UNITS | BEXAR | BIOMASS | SOUTH | 2002 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8
WESTSIDE |  | DG_WSTHL_3UNITS | PARKER | BIOMASS | NORTH | 2010 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8
Operational Capacity Total (Coal, Gas, Nuclear, Biomass, Solar) | [6 empty] | 63978.1 | 63978.1 | 63978.1 | 63978.1 | 63138.1 | 63138.1 | 63138.1 | 63138.1 | 63138.1 | 63138.1
Operational Resources (Hydro)
AMISTAD HYDRO 1 |  | AMISTAD_AMISTAG1 | VAL VERDE | HYDRO | SOUTH | 1983 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9
AMISTAD HYDRO 2 |  | AMISTAD_AMISTAG2 | VAL VERDE | HYDRO | SOUTH | 1983 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9
AUSTIN HYDRO 1 |  | AUSTPL_AUSTING1 | TRAVIS | HYDRO | SOUTH | 1940 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
AUSTIN HYDRO 2 |  | AUSTPL_AUSTING2 | TRAVIS | HYDRO | SOUTH | 1940 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
BUCHANAN HYDRO 1 |  | BUCHAN_BUCHANG1 | LLANO | HYDRO | SOUTH | 1938 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
BUCHANAN HYDRO 2 |  | BUCHAN_BUCHANG2 | LLANO | HYDRO | SOUTH | 1938 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
BUCHANAN HYDRO 3 |  | BUCHAN_BUCHANG3 | LLANO | HYDRO | SOUTH | 1950 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
DENISON DAM 1 |  | DNDAM_DENISOG1 | GRAYSON | HYDRO | NORTH | 1944 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
DENISON DAM 2 |  | DNDAM_DENISOG2 | GRAYSON | HYDRO | NORTH | 1948 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
FALCON HYDRO 1 |  | FALCON_FALCONG1 | STARR | HYDRO | SOUTH | 1954 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
FALCON HYDRO 2 |  | FALCON_FALCONG2 | STARR | HYDRO | SOUTH | 1954 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
FALCON HYDRO 3 |  | FALCON_FALCONG3 | STARR | HYDRO | SOUTH | 1954 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
GRANITE SHOALS HYDRO 1 |  | WIRTZ_WIRTZ_G1 | BURNET | HYDRO | SOUTH | 1951 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
GRANITE SHOALS HYDRO 2 |  | WIRTZ_WIRTZ_G2 | BURNET | HYDRO | SOUTH | 1951 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
INKS HYDRO 1 |  | INKSDA_INKS_G1 | LLANO | HYDRO | SOUTH | 1938 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
MARBLE FALLS HYDRO 1 |  | MARBFA_MARBFAG1 | BURNET | HYDRO | SOUTH | 1951 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
MARBLE FALLS HYDRO 2 |  | MARBFA_MARBFAG2 | BURNET | HYDRO | SOUTH | 1951 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
MARSHALL FORD HYDRO 1 |  | MARSFO_MARSFOG1 | TRAVIS | HYDRO | SOUTH | 1941 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
MARSHALL FORD HYDRO 2 |  | MARSFO_MARSFOG2 | TRAVIS | HYDRO | SOUTH | 1941 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
MARSHALL FORD HYDRO 3 |  | MARSFO_MARSFOG3 | TRAVIS | HYDRO | SOUTH | 1941 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
WHITNEY DAM HYDRO |  | WND_WHITNEY1 | BOSQUE | HYDRO | NORTH | 1953 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
WHITNEY DAM HYDRO 2 |  | WND_WHITNEY2 | BOSQUE | HYDRO | NORTH | 1953 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
CANYON |  | CANYHY_CANYHYG1 | COMAL | HYDRO | SOUTH | 1989 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
EAGLE PASS HYDRO |  | EAGLE_HY_EAGLE_HY1 | MAVERICK | HYDRO | SOUTH | 2005 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
LAKEWOOD TAP |  | DG_LKWDT_2UNITS | GONZALES | HYDRO | SOUTH | 1931 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8
LEWISVILLE |  | DG_LWSVL_1UNIT | DENTON | HYDRO | NORTH | 1991 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2
MCQUEENEY |  | DG_MCQUE_5UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7
SCHUMANSVILLE |  | DG_SCHUM_2UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6
Operational Capacity Total (Hydro) | [6 empty] | 540.7 | 540.7 | 540.7 | 540.7 | 540.7 | 540.7 | 540.7 | 540.7 | 540.7 | 540.7
Hydro Capacity Contribution (Top 20 Hours) |  | HYDRO_CAP_CONT |  |  |  |  | 433.4 | 433.4 | 433.4 | 433.4 | 433.4 | 433.4 | 433.4 | 433.4 | 433.4 | 433.4
Operational Capacity Total (Including Hydro) | [6 empty] | 64411.5 | 64411.5 | 64411.5 | 64411.5 | 63571.5 | 63571.5 | 63571.5 | 63571.5 | 63571.5 | 63571.5
Private-Use Network Capacity Contribution (Top 20 Hours) |  | PUN_CAP_CONT |  | GAS |  |  | 4344 | 4344 | 4344 | 4344 | 4344 | 4344 | 4344 | 4344 | 4344 | 4344
Wind Resources
ANACACHO WIND | 12INR0072 | ANACACHO_ANA | KINNEY | WIND | SOUTH | 2012 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8
BARTON CHAPEL WIND | 06INR0021 | BRTSW_BCW1 | JACK | WIND | WEST | 2007 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
BLUE SUMMIT WIND 5 | 12INR0075 | BLSUMMIT_BLSMT1_5 | WILBARGER | WIND | WEST | 2013 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
BLUE SUMMIT WIND 6 | 12INR0075 | BLSUMMIT_BLSMT1_6 | WILBARGER | WIND | WEST | 2013 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4
BOBCAT BLUFF WIND | 08INR0049 | BCATWIND_WIND_1 | ARCHER | WIND | NORTH | 2012 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
BUFFALO GAP WIND FARM 1 | 04INR0015 | BUFF_GAP_UNIT1 | TAYLOR | WIND | WEST | 2006 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6
BUFFALO GAP WIND FARM 2_1 | 06INR0037 | BUFF_GAP_UNIT2_1 | TAYLOR | WIND | WEST | 2007 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5
BUFFALO GAP WIND FARM 2_2 | 06INR0037 | BUFF_GAP_UNIT2_2 | TAYLOR | WIND | WEST | 2007 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117
BUFFALO GAP WIND FARM 3 | 07INR0030 | BUFF_GAP_UNIT3 | TAYLOR | WIND | WEST | 2008 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2
BULL CREEK WIND PLANT U1 | 07INR0037 | BULLCRK_WND1 | BORDEN | WIND | WEST | 2009 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88
BULL CREEK WIND PLANT U2 | 07INR0037 | BULLCRK_WND2 | BORDEN | WIND | WEST | 2009 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
CALLAHAN WIND | 04INR0013 | CALLAHAN_WND1 | CALLAHAN | WIND | WEST | 2004 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114
CAMP SPRINGS WIND 1 | 06INR0038 | CSEC_CSECG1 | SCURRY | WIND | WEST | 2007 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5
CAMP SPRINGS WIND 2 | 07INR0040 | CSEC_CSECG2 | SCURRY | WIND | WEST | 2007 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
CAPRICORN RIDGE WIND 1 | 07INR0018 | CAPRIDGE_CR1 | STERLING | WIND | WEST | 2007 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5
CAPRICORN RIDGE WIND 2 | 07INR0041 | CAPRIDGE_CR3 | STERLING | WIND | WEST | 2008 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186
CAPRICORN RIDGE WIND 3 | 07INR0041 | CAPRIDGE_CR2 | STERLING | WIND | WEST | 2007 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5
CAPRICORN RIDGE WIND 4 | 08INR0063 | CAPRIDG4_CR4 | COKE/STERLING | WIND | WEST | 2008 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5
CEDRO HILL WIND 1 | 09INR0082 | CEDROHIL_CHW1 | WEBB | WIND | SOUTH | 2010 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
CEDRO HILL WIND 2 | 09INR0083 | CEDROHIL_CHW2 | WEBB | WIND | SOUTH | 2010 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
CHAMPION WIND FARM | 07INR0045d | CHAMPION_UNIT1 | NOLAN AND MITCHELL | WIND | WEST | 2008 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5
DESERT SKY WIND FARM 1 |  | INDNENR_INDNENR | PECOS | WIND | WEST | 2002 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84
DESERT SKY WIND FARM 2 |  | INDNENR_INDNENR_2 | PECOS | WIND | WEST | 2002 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5
ELBOW CREEK WIND PROJECT | 08INR0053 | ELB_ELBCREEK | HOWARD | WIND | WEST | 2008 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7
FOREST CREEK WIND FARM | 05INR0019 | MCDLD_FCW1 | GLASSCOCK | WIND | WEST | 2007 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2
GOAT WIND | 07INR0028 | GOAT_GOATWIND | STERLING | WIND | WEST | 2008 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
GOAT WIND 2 | 07INR0028b | GOAT_GOATWIN2 | STERLING | WIND | WEST | 2010 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6
GOLDTHWAITE WIND 1 | 11INR0013 | GWEC_GWEC_G1 | MILLS | WIND | NORTH | 2014 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6
GREEN MOUNTAIN WIND (BRAZOS) U1 | 03INR0020 | BRAZ_WND_WND1 | SCURRY/BORDEN | WIND | WEST | 2003 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99
GREEN MOUNTAIN WIND (BRAZOS) U2 | 03INR0020 | BRAZ_WND_WND2 | SCURRY/BORDEN | WIND | WEST | 2003 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
HACKBERRY WIND FARM | 04INR0011e | HWF_HWFG1 | SHACKELFORD | WIND | WEST | 2008 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5
HORSE HOLLOW WIND 1 | 05INR0015 | H_HOLLOW_WND1 | TAYLOR | WIND | WEST | 2005 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 213
HORSE HOLLOW WIND 2 | 05INR0018 | HHOLLOW2_WIND1 | TAYLOR | WIND | WEST | 2006 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184
HORSE HOLLOW WIND 3 | 06INR0040 | HHOLLOW3_WND_1 | TAYLOR | WIND | WEST | 2006 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5
HORSE HOLLOW WIND 4 | 06INR0040 | HHOLLOW4_WND1 | TAYLOR | WIND | WEST | 2006 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115
INADALE WIND | 07INR0045b | INDL_INADALE1 | NOLAN | WIND | WEST | 2008 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6
INDIAN MESA WIND FARM | 00INR0022 | INDNNWP_INDNNWP | PECOS COUNTY | WIND | WEST | 2001 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5
KING MOUNTAIN NE | 00INR0025 | KING_NE_KINGNE | UPTON | WIND | WEST | 2001 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3
KING MOUNTAIN NW | 00INR0025 | KING_NW_KINGNW | UPTON | WIND | WEST | 2001 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3
KING MOUNTAIN SE | 00INR0025 | KING_SE_KINGSE | UPTON | WIND | WEST | 2001 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3
KING MOUNTAIN SW | 00INR0025 | KING_SW_KINGSW | UPTON | WIND | WEST | 2001 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3
LANGFORD WIND POWER | 10INR0026 | LGD_LANGFORD | TOM GREEN | WIND | WEST | 2009 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
LONE STAR WIND 1 (MESQUITE) | 04INR0011 | LNCRK_G83 | SHACKELFORD | WIND | WEST | 2006 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
LONE STAR WIND 2 (POST OAK) U1 | 04INR0011a | LNCRK2_G871 | SHACKELFORD | WIND | WEST | 2007 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
LONE STAR WIND 2 (POST OAK) U2 | 04INR0011a | LNCRK2_G872 | SHACKELFORD | WIND | WEST | 2007 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
LORAINE WINDPARK I | 09INR0047 | LONEWOLF_G1 | MITCHELL | WIND | WEST | 2009 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5
LORAINE WINDPARK II | 09INR0047 | LONEWOLF_G2 | MITCHELL | WIND | WEST | 2009 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51
LORAINE WINDPARK III | 09INR0047 | LONEWOLF_G3 | MITCHELL | WIND | WEST | 2011 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5
LORAINE WINDPARK IV | 09INR0047 | LONEWOLF_G4 | MITCHELL | WIND | WEST | 2011 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
MCADOO WIND FARM | 08INR0028 | MWEC_G1 | DICKENS | WIND | WEST | 2008 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
NOTREES WIND FARM 1 | 07INR0005 | NWF_NWF1 | WINKLER/ECTOR | WIND | WEST | 2009 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6
NOTREES WIND FARM 2 | 07INR0005 | NWF_NWF2 | WINKLER/ECTOR | WIND | WEST | 2009 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OCOTILLO WIND FARM | 04INR0017 | OWF_OWF | HOWARD | WIND | WEST | 2008 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8
PANHANDLE WIND 1 U1 | 14INR0030a_2 | PH1_UNIT1 | CARSON | WIND | PANHANDLE | 2014 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2
PANHANDLE WIND 1 U2 | 14INR0030a_2 | PH1_UNIT2 | CARSON | WIND | PANHANDLE | 2014 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2
PANHANDLE WIND 2 U1 | 14INR0030b | PH2_UNIT1 | CARSON | WIND | PANHANDLE | 2014 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7
PANHANDLE WIND 2 U2 | 14INR0030b | PH2_UNIT2 | CARSON | WIND | PANHANDLE | 2014 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92
PANTHER CREEK 1 | 07INR0022 | PC_NORTH_PANTHER1 | HOWARD | WIND | WEST | 2008 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5
PANTHER CREEK 2 | 08INR0037 | PC_SOUTH_PANTHER2 | HOWARD | WIND | WEST | 2008 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5
PANTHER CREEK 3 | 11INR0015 | PC_SOUTH_PANTHER3 | HOWARD | WIND | WEST | 2009 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5
PECOS WIND (WOODWARD 1) | 01INR0035 | WOODWRD1_WOODWRD1 | PECOS | WIND | WEST | 2001 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5
PECOS WIND (WOODWARD 2) | 01INR0035 | WOODWRD2_WOODWRD2 | PECOS | WIND | WEST | 2001 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2
PYRON WIND FARM | 07INR0045a | PYR_PYRON1 | SCURRY AND FISHER | WIND | WEST | 2008 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249
RED CANYON WIND | 05INR0017 | RDCANYON_RDCNY1 | BORDEN | WIND | WEST | 2006 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84
ROSCOE WIND FARM | 07INR0045e | TKWSW1_ROSCOE | NOLAN | WIND | WEST | 2008 | 209 | 209 | 209 | 209 | 209 | 209 | 209 | 209 | 209 | 209
SAND BLUFF WIND FARM | 05INR0019 | MCDLD_SBW1 | GLASSCOCK | WIND | WEST | 2008 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
SENATE WIND PROJECT | 08INR0011 | SENATEWD_UNIT1 | JACK | WIND | WEST | 2012 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
SHERBINO I WIND | 06INR0012a | KEO_KEO_SM1 | PECOS | WIND | WEST | 2008 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
SHERBINO 2 WIND | 06INR0012b | KEO_SHRBINO2 | PECOS | WIND | WEST | 2011 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
SILVER STAR WIND | 03INR0034 | FLTCK_SSI | EASTLAND | WIND | NORTH | 2008 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SNYDER WIND FARM | 04INR0020 | ENAS_ENA1 | SCURRY | WIND | WEST | 2007 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63
SOUTH TRENT WIND FARM | 07INR0029 | STWF_T1 | NOLAN & TAYLOR | WIND | WEST | 2008 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2
SPINNING SPUR WIND TWO | 13INR0048 | SSPURTWO_WIND_1 | OLDHAM | WIND | PANHANDLE | 2014 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161
STANTON WIND ENERGY | 07INR0010 | SWEC_G1 | MARTIN | WIND | WEST | 2008 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
SWEETWATER WIND 1 | 01INR0036 | SWEETWND_WND1 | NOLAN | WIND | WEST | 2003 | 36.6 | 36.6 | 36.6 | 36.6 | 36.6 | 36.6 | 36.6 | 36.6 | 36.6 | 36.6
SWEETWATER WIND 2A | 01INR0036 | SWEETWN2_WND24 | NOLAN | WIND | WEST | 2006 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9
SWEETWATER WIND 2B | 01INR0036 | SWEETWN2_WND2 | NOLAN | WIND | WEST | 2004 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5
SWEETWATER WIND 3A | 01INR0036 | SWEETWN3_WND3A | NOLAN | WIND | WEST | 2011 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5
SWEETWATER WIND 3B | 01INR0036 | SWEETWN3_WND3B | NOLAN | WIND | WEST | 2011 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5
SWEETWATER WIND 4-5 | 07INR0023 | SWEETWN4_WND5 | NOLAN | WIND | WEST | 2007 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2
SWEETWATER WIND 4-4B | 07INR0023 | SWEETWN4_WND4B | NOLAN | WIND | WEST | 2007 | 103.7 | 103.7 | 103.7 | 103.7 | 103.7 | 103.7 | 103.7 | 103.7 | 103.7 | 103.7
SWEETWATER WIND 4-4A | 07INR0023 | SWEETWN4_WND4A | NOLAN | WIND | WEST | 2007 | 117.8 | 117.8 | 117.8 | 117.8 | 117.8 | 117.8 | 117.8 | 117.8 | 117.8 | 117.8
TEXAS BIG SPRING WIND a |  | SGMTN_SIGNALMT | HOWARD | WIND | WEST | 1999 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7
TEXAS BIG SPRING WIND b |  | SGMTN_SIGNALM2 | HOWARD | WIND | WEST | 1999 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
TRENT WIND FARM | 01INR0038 | TRENT_TRENT | NOLAN | WIND | WEST | 2001 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
TRINITY HILLS WIND 1 | 08INR0062 | TRINITY_TH1_BUS1 | YOUNG | WIND | NORTH | 2012 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5
TRINITY HILLS WIND 2 | 08INR0062 | TRINITY_TH1_BUS2 | YOUNG | WIND | NORTH | 2012 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5
TURKEY TRACK WIND ENERGY CENTER | 07INR0011 | TTWEC_G1 | NOLAN | WIND | WEST | 2008 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5
WEST TEXAS WIND ENERGY |  | SW_MESA_SW_MESA | UPTON/CROCKETT COUNTIES | WIND | WEST | 1999 | 74.2 | 74.2 | 74.2 | 74.2 | 74.2 | 74.2 | 74.2 | 74.2 | 74.2 | 74.2
WHIRLWIND ENERGY | 07INR0003 | WEC_WECG1 | FLOYD | WIND | NORTH | 2007 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
WHITETAIL WIND ENERGY PROJECT | 11INR0091 | EXGNWTL_WIND_1 | WEBB AND DUVAL | WIND | SOUTH | 2012 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
WKN MOZART WIND | 09INR0061 | MOZART_WIND_1 | KENT & STONEWALL COUNTY | WIND | WEST | 2012 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
WOLF RIDGE WIND | 07INR0034 | WHTTAIL_WR1 | COOKE | WIND | NORTH | 2008 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5
TSTC WEST TEXAS WIND |  | DG_ROSC2_1UNIT | NOLAN | WIND | WEST | 2008 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Wind Capacity Total (Non-Coastal Counties) | [6 empty] | 10023 | 10023 | 10023 | 10023 | 10023 | 10023 | 10023 | 10023 | 10023 | 10023
GULF WIND I | 05INR0015a | TGW_T1 | KENEDY | WIND-C | SOUTH | 2010 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6
GULF WIND II | 05INR0015a | TGW_T2 | KENEDY | WIND-C | SOUTH | 2010 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6
LOS VIENTOS WIND I | 11INR0033 | LV1_LV1A | WILLACY/CAMERON | WIND-C | SOUTH | 2013 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1
LOS VIENTOS WIND II | 11INR0033 | LV1_LV1B | WILLACY/CAMERON | WIND-C | SOUTH | 2013 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6
MAGIC VALLEY WIND (REDFISH) 1A | 10INR0060 | REDFISH_MV1A | WILLACY | WIND-C | SOUTH | 2012 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8
MAGIC VALLEY WIND (REDFISH) 1B | 10INR0060 | REDFISH_MV1B | WILLACY | WIND-C | SOUTH | 2012 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5
PAPALOTE CREEK WIND FARM | 08INR0012a | PAP1_PAP1 | SAN PATRICIO | WIND-C | SOUTH | 2009 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9
PAPALOTE CREEK WIND FARM II | 08INR0012b | COTTON_PAP2 | SAN PATRICIO | WIND-C | SOUTH | 2010 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1
PENASCAL WIND 1 | 06INR0022a | PENA_UNIT1 | KENEDY | WIND-C | SOUTH | 2009 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8
PENASCAL WIND 2 | 06INR0022b | PENA_UNIT2 | KENEDY | WIND-C | SOUTH | 2009 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6
PENASCAL WIND 3 | 06INR0022b | PENA3_UNIT3 | KENEDY | WIND-C | SOUTH | 2011 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8
HARBOR WIND |  | DG_NUECE_6UNITS | NUECES | WIND-C | SOUTH | 2012 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
Wind Capacity Total (Coastal Counties) | [6 empty] | 1680.4 | 1680.4 | 1680.4 | 1680.4 | 1680.4 | 1680.4 | 1680.4 | 1680.4 | 1680.4 | 1680.4
Wind Capacity Total Total | [6 empty] | 11703.4 | 11703.4 | 11703.4 | 11703.4 | 11703.4 | 11703.4 | 11703.4 | 11703.4 | 11703.4 | 11703.4
Reliability Must-Run (RMR) Capacity |  | RMR_CAP_CONT |  | GAS |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DC-Tie Resources
EAGLE PASS TIE |  | DC_S | MAVERICK |  | SOUTH |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
EAST TIE |  | DC_E | FANNIN |  | NORTH |  | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
LAREDO VFT TIE |  | DC_L | WEBB |  | SOUTH |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
NORTH TIE |  | DC_N | WILBARGER |  | WEST |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
SHARYLAND RAILROAD TIE |  | DC_R | HIDALGO |  | SOUTH |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
SHARYLAND RAILROAD TIE (FUTURE) |  | DC_R2 | HIDALGO |  | SOUTH |  | 20 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
DC-Ties Total | [6 empty] | 1120 | 1250 | 1250 | 1250 | 1250 | 1250 | 1250 | 1250 | 1250 | 1250
DC-Ties Capacity Contribution (Top 20 Hours) |  | DCTIE_CAP_CONT |  | OTHER |  |  | 516.7 | 516.7 | 516.7 | 516.7 | 516.7 | 516.7 | 516.7 | 516.7 | 516.7 | 516.7
Switchable Resources
KIAMICHI ENERGY FACILITY 1CT101 | 03INR0012 | KMCHI_1CT101 | PITTSBURG | GAS | NORTH | 2003 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153
KIAMICHI ENERGY FACILITY 1CT201 | 03INR0012 | KMCHI_1CT201 | PITTSBURG | GAS | NORTH | 2003 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
KIAMICHI ENERGY FACILITY 1ST | 03INR0012 | KMCHI_1ST | PITTSBURG | GAS | NORTH | 2003 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315
KIAMICHI ENERGY FACILITY 2CT101 | 03INR0012 | KMCHI_2CT101 | PITTSBURG | GAS | NORTH | 2003 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153
KIAMICHI ENERGY FACILITY 2CT201 | 03INR0012 | KMCHI_2CT201 | PITTSBURG | GAS | NORTH | 2003 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
KIAMICHI ENERGY FACILITY 2ST | 03INR0012 | KMCHI_2ST | PITTSBURG | GAS | NORTH | 2003 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315
TENASKA-FRONTIER CTG 1 | 00PSR4 | FTR_FTR_G1 | GRIMES | GAS | HOUSTON | 2000 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
TENASKA-FRONTIER CTG 2 | 00PSR4 | FTR_FTR_G2 | GRIMES | GAS | HOUSTON | 2000 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
TENASKA-FRONTIER CTG 3 | 00PSR4 | FTR_FTR_G3 | GRIMES | GAS | HOUSTON | 2000 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
TENASKA-FRONTIER STG 4 | 00PSR4 | FTR_FTR_G4 | GRIMES | GAS | HOUSTON | 2000 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400
TENASKA-GATEWAY CTG 1 | 01INR0019 | TGCCS_CT1 | RUSK | GAS | NORTH | 2001 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156
TENASKA-GATEWAY CTG 2 | 01INR0019 | TGCCS_CT2 | RUSK | GAS | NORTH | 2001 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135
TENASKA-GATEWAY CTG 3 | 01INR0019 | TGCCS_CT3 | RUSK | GAS | NORTH | 2001 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153
TENASKA-GATEWAY STG 4 | 01INR0019 | TGCCS_UNIT4 | RUSK | GAS | NORTH | 2001 | 402 | 402 | 402 | 402 | 402 | 402 | 402 | 402 | 402 | 402
FRONTERA GENERATION CTG 1 |  | FRONTERA_FRONTEG1 | HIDALGO | GAS | SOUTH | 1999 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170
FRONTERA GENERATION CTG 2 |  | FRONTERA_FRONTEG2 | HIDALGO | GAS | SOUTH | 1999 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170
FRONTERA GENERATION STG |  | FRONTERA_FRONTEG3 | HIDALGO | GAS | SOUTH | 2000 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184
Switchable Capacity Total | [6 empty] | 3496 | 3496 | 3496 | 3496 | 3496 | 3496 | 3496 | 3496 | 3496 | 3496
Switchable Capacity Unavailable to ERCOT |  | SWITCH_UNAVAIL |  | GAS |  |  | -470 | -824 | -824 | -824 | -824 | -824 | -524 | -524 | -524 | -524
Available Mothball Capacity based on Owner's Return Probability |  | MOTH_AVAIL |  | COAL |  |  | 1933 | 1933 | 1933 | 1933 | 1933 | 1933 | 1933 | 1933 | 1933 | 1933
Planned Resources with Executed SGIA, Air Permit, GHG Permit and Water Rights
TEXAS CLEAN ENERGY PROJECT | 13INR0023 |  | ECTOR | COAL | WEST | 2019 | 0 | 0 | 0 | 0 | 0 | 240 | 240 | 240 | 240 | 240
PANDA TEMPLE II CTG1 | 10INR0020b | PANDA_T2_TMPL2CT1 | BELL | GAS | NORTH | 2015 | 0 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2
PANDA TEMPLE II CTG2 | 10INR0020b | PANDA_T2_TMPL2CT2 | BELL | GAS | NORTH | 2015 | 0 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2
PANDA TEMPLE II STG | 10INR0020b | PANDA_T2_TMPL2ST1 | BELL | GAS | NORTH | 2015 | 0 | 334.7 | 334.7 | 334.7 | 334.7 | 334.7 | 334.7 | 334.7 | 334.7 | 334.7
FGE TEXAS I | 16INR0010 |  | MITCHELL | GAS | WEST | 2017 | 0 | 0 | 703 | 703 | 703 | 703 | 703 | 703 | 703 | 703
ANTELOPE STATION IC & CTG | 13INR0028 |  | HALE | GAS | PANHANDLE | 2016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GOLDSMITH PEAKERS | 14INR0039 |  | ECTOR | GAS | WEST | 2015 | 294 | 294 | 294 | 294 | 294 | 294 | 294 | 294 | 294 | 294
LA PALOMA ENERGY CENTER | 16INR0004 |  | CAMERON | GAS | SOUTH | 2016 | 0 | 0 | 730 | 730 | 730 | 730 | 730 | 730 | 730 | 730
PHR PEAKERS | 14INR0038 |  | GALVESTON | GAS | HOUSTON | 2015 | 0 | 388 | 388 | 388 | 388 | 388 | 388 | 388 | 388 | 388
SKY GLOBAL POWER ONE | 16INR0057 |  | COLORADO | GAS | SOUTH | 2016 | 0 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51
WHITE CAMP SOLAR (WCSOLAR1_100PV) | 11INR0094 |  | KENT | SOLAR | WEST | 2015 | 0 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
PECOS BARILLA SOLAR (HOVEY_UNIT1) | 12INR0059 |  | PECOS | SOLAR | WEST | 2014 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
OCI ALAMO 5 | 15INR0036 |  | UVALDE | SOLAR | SOUTH | 2015 | 0 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105
Planned Capacity Total (Not Wind) | [6 empty] | 324 | 1685.1 | 3118.1 | 3118.1 | 3118.1 | 3358.1 | 3358.1 | 3358.1 | 3358.1 | 3358.1
Planned Wind Resources with Executed SGIA
STEPHENS RANCH WIND 1 (SRWE1_UNIT1) | 12INR0034a |  | BORDEN | WIND | WEST | 2014 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211
STEPHENS RANCH WIND 2 | 12INR0034b |  | BORDEN | WIND | WEST | 2015 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
MARIAH WIND a | 13INR0010a |  | PARMER | WIND | PANHANDLE | 2015 | 0 | 232 | 232 | 232 | 232 | 232 | 232 | 232 | 232 | 232
MIAMI WIND 1 (MIAM1_G1-2) | 14INR0012a |  | GRAY | WIND | PANHANDLE | 2014 | 289 | 289 | 289 | 289 | 289 | 289 | 289 | 289 | 289 | 289
MARIAH WIND b | 13INR0010b |  | PARMER | WIND | PANHANDLE | 2015 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
MIDWAY FARMS WIND | 11INR0054 |  | SAN PATRICIO | WIND-C | SOUTH | 2016 | 0 | 0 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161
LONGHORN ENERGY CENTER (LHORN_N_UNIT1-2) | 14INR0023 |  | BRISCOE | WIND | WEST | 2015 | 0 | 361 | 361 | 361 | 361 | 361 | 361 | 361 | 361 | 361
GRANDVIEW (CONWAY) 1 (GRANDVW1_GV1A-B) | 13INR0005a |  | CARSON | WIND | PANHANDLE | 2014 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211
GRANDVIEW (CONWAY) 2 | 13INR0005b |  | CARSON | WIND | PANHANDLE | 2015 | 0 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389
SOUTH CLAY WINDFARM | 11INR0079a |  | CLAY | WIND | WEST | 2015 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
BAFFIN (PENASCAL WIND FARM 3) (BAFFIN_UNIT1-2) | 06INR0022c |  | KENEDY | WIND-C | SOUTH | 2014 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202
MARIAH WIND c | 13INR0010c |  | PARMER | WIND | PANHANDLE | 2016 | 0 | 0 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168
MESQUITE CREEK WIND (MESQCRK_WND1-2) | 09INR0051 |  | BORDEN | WIND | WEST | 2015 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211
GUNSIGHT MOUNTAIN | 08INR0018 |  | HOWARD | WIND | WEST | 2015 | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
BRISCOE WIND FARM | 14INR0072 |  | BRISCOE | WIND | WEST | 2015 | 0 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
CAMERON COUNTY WIND | 11INR0057 |  | CAMERON | WIND-C | SOUTH | 2015 | 0 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
COMANCHE RUN WIND | 12INR0029 |  | SWISHER | WIND | PANHANDLE | 2016 | 0 | 0 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
CPV RATTLESNAKE DEN PH 1 | 13INR0020a |  | GLASSCOCK | WIND | WEST | 2015 | 0 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211
CPV RATTLESNAKE DEN PH 2 | 13INR0020b |  | GLASSCOCK | WIND | WEST | 2016 | 0 | 0 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158
GREEN PASTURES WIND (GPASTURE_WIND_I & II) | 12INR0070 |  | KNOX | WIND | WEST | 2015 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
HEREFORD WIND (HRFDWIND_WIND_G & V) | 13INR0059a |  | CASTRO | WIND | PANHANDLE | 2014 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
JUMBO ROAD WIND (HRFDWIND_JRDWIND1-2) | 13INR0059b |  | CASTRO | WIND | PANHANDLE | 2015 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
KEECHI WIND 138 KV JOPLIN (KEECHI_U1) | 14INR0049_2 |  | JACK | WIND | NORTH | 2014 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102
LOGANS GAP WIND I | 13INR0050 |  | COMANCHE | WIND | NORTH | 2015 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
LOS VIENTOS III (LV3_UNIT_1) | 13INR0052 |  | STARR | WIND | SOUTH | 2015 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
MIAMI WIND 1b | 14INR0012b |  | GRAY | WIND | PANHANDLE | 2015 | 0 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111
PAMPA WIND PROJECT | 12INR0018 |  | GRAY | WIND | PANHANDLE | 2017 | 0 | 0 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
PATRIOT (PETRONILLA) WIND | 11INR0062 |  | NUECES | WIND-C | SOUTH | 2015 | 0 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
ROUTE66 WIND | 14INR0032a |  | RANDALL | WIND | PANHANDLE | 2015 | 0 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
SENDERO WIND ENERGY PROJECT | 12INR0068 |  | JIM HOGG | WIND | SOUTH | 2015 | 0 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
SOUTH PLAINS WIND I | 14INR0025a |  | FLOYD | WIND | WEST | 2015 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
SOUTH PLAINS WIND II | 14INR0025b |  | FLOYD | WIND | WEST | 2015 | 0 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
SPINNING SPUR WIND THREE | 14INR0053 |  | OLDHAM | WIND | PANHANDLE | 2015 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194
WINDTHORST 2 (WNDTHST2_UNIT1) | 13INR0057 |  | ARCHER | WIND | WEST | 2014 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
WAKE WIND ENERGY | 14INR0047 |  | DICKENS | WIND | WEST | 2015 | 0 | 299 | 299 | 299 | 299 | 299 | 299 | 299 | 299 | 299
CAPROCK WIND | 10INR0009 |  | CASTRO | WIND | PANHANDLE | 2015 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
JAVELINA WIND ENERGY | 13INR0055 |  | ZAPATA | WIND | SOUTH | 2015 | 0 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250
LOS VIENTOS IV | 15INR0037 |  | STARR | WIND | SOUTH | 2015 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
LOS VIENTOS V | 15INR0021 |  | STARR | WIND | SOUTH | 2015 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
PALO DURO WIND | 15INR0050 |  | DEAF SMITH | WIND | PANHANDLE | 2015 | 0 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203
PANHANDLE WIND 3 | 14INR0030c |  | CARSON | WIND | PANHANDLE | 2015 | 0 | 248.4 | 248.4 | 248.4 | 248.4 | 248.4 | 248.4 | 248.4 | 248.4 | 248.4
PULLMAN ROAD WIND | 15INR0079 |  | RANDALL | WIND | PANHANDLE | 2015 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
SALT FORK WIND | 14INR0062 |  | GRAY | WIND | PANHANDLE | 2015 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
SCANDIA WIND d | 13INR0010d |  | PARMER | WIND | PANHANDLE | 2015 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
SCANDIA WIND e | 13INR0010e |  | PARMER | WIND | PANHANDLE | 2015 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
SCANDIA WIND f | 13INR0010f |  | PARMER | WIND | PANHANDLE | 2016 | 0 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
Planned Wind Capacity Total | [6 empty] | 3150 | 8345.4 | 10032.4 | 10032.4 | 10032.4 | 10032.4 | 10032.4 | 10032.4 | 10032.4 | 10032.4
Planned Wind Capacity Sub-total (Non-Coastal Counties) | [6 empty] | 2948 | 7800.4 | 9326.4 | 9326.4 | 9326.4 | 9326.4 | 9326.4 | 9326.4 | 9326.4 | 9326.4
Planned Wind Capacity Sub-total (by Coastal County)
|  | CAMERON_NEW_WIND | CAMERON | WIND | SOUTH |  | 0 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
|  | WILLACY_NEW_WIND | WILLACY | WIND | SOUTH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | KENEDY_NEW_WIND | KENEDY | WIND | SOUTH |  | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202
|  | KLEBERG_NEW_WIND | KLEBERG | WIND | SOUTH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | NUECES_NEW_WIND | NUECES | WIND | SOUTH |  | 0 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
|  | SAN_PATRICIO_NEW_WIND | SAN PATRICIO | WIND | SOUTH |  | 0 | 0 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161
|  | REFUGIO_NEW_WIND | REFUGIO | WIND | SOUTH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | ARANSAS_NEW_WIND | ARANSAS | WIND | SOUTH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | CALHOUN_NEW_WIND | CALHOUN | WIND | SOUTH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | MATAGORDA_NEW_WIND | MATAGORDA | WIND | SOUTH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | BRAZORIA_NEW_WIND | BRAZORIA | WIND | HOUSTON |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Planned Wind Capacity Sub-total (All Coastal Counties) | [6 empty] | 202 | 545 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706
Mothballed Capacity
GREENS BAYOU CTG 82 |  | GBY_GBYGT82 | HARRIS | GAS | HOUSTON | 1976 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58
NORTH TEXAS CTG 1 |  | NTX_NTX_1 | PARKER | GAS | NORTH | 1958 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
NORTH TEXAS CTG 2 |  | NTX_NTX_2 | PARKER | GAS | NORTH | 1958 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
NORTH TEXAS CTG 3 |  | NTX_NTX_3 | PARKER | GAS | NORTH | 1963 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
PERMIAN BASIN SES U6 |  | PBSES_UNIT6 | WARD | GAS | WEST | 1973 | 515 | 515 | 515 | 515 | 515 | 515 | 515 | 515 | 515 | 515
SILAS RAY CTG 5 |  | SILASRAY_SILAS_5 | CAMERON | GAS | SOUTH | 1953 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
VALLEY SES U1 |  | VLSES_UNIT1 | FANNIN | GAS | NORTH | 1962 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174
VALLEY SES U2 |  | VLSES_UNIT2 | FANNIN | GAS | NORTH | 1967 | 520 | 520 | 520 | 520 | 520 | 520 | 520 | 520 | 520 | 520
VALLEY SES U3 |  | VLSES_UNIT3 | FANNIN | GAS | NORTH | 1971 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375
J T DEELY U1 (MOTHBALLED) |  | CALAVERS_JTD1_M | BEXAR | COAL | SOUTH | 2018 | 0 | 0 | 0 | 0 | 420 | 420 | 420 | 420 | 420 | 420
J T DEELY U2 (MOTHBALLED) |  | CALAVERS_JTD2_M | BEXAR | COAL | SOUTH | 2018 | 0 | 0 | 0 | 0 | 420 | 420 | 420 | 420 | 420 | 420
S R BERTRON CTG 2 |  | SRB_SRBGT_2 | HARRIS | GAS | HOUSTON | 1967 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
S R BERTRON U1 |  | SRB_SRB_G1 | HARRIS | GAS | HOUSTON | 1958 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118
S R BERTRON U2 |  | SRB_SRB_G2 | HARRIS | GAS | HOUSTON | 1956 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174
S R BERTRON U3 |  | SRB_SRB_G3 | HARRIS | GAS | HOUSTON | 1959 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211
S R BERTRON U4 |  | SRB_SRB_G4 | HARRIS | GAS | HOUSTON | 1960 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211
V H BRAUNIG STG U2 |  | BRAUNIG_VHB2 | BEXAR | GAS | SOUTH | 1968 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230
Total Mothballed Capacity | [6 empty] | 2684 | 2684 | 2684 | 2684 | 3524 | 3524 | 3524 | 3524 | 3524 | 3524
Seasonal Mothballed Capacity
MARTIN LAKE U3 |  | MLSES_UNIT3 | RUSK | COAL | NORTH | 1979 | 805 | 805 | 805 | 805 | 805 | 805 | 805 | 805 | 805 | 805
MONTICELLO U1 |  | MNSES_UNIT1 | TITUS | COAL | NORTH | 1974 | 535 | 535 | 535 | 535 | 535 | 535 | 535 | 535 | 535 | 535
MONTICELLO U2 |  | MNSES_UNIT2 | TITUS | COAL | NORTH | 1975 | 535 | 535 | 535 | 535 | 535 | 535 | 535 | 535 | 535 | 535
Total Seasonal Mothballed Capacity | [6 empty] | 1875 | 1875 | 1875 | 1875 | 1875 | 1875 | 1875 | 1875 | 1875 | 1875
Retiring Capacity Unavailable to ERCOT (since May 2014)
APPLIED ENERGY |  | APD_APD_G1 | HARRIS | COAL | HOUSTON | 1986 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138
ATKINS CTG 3 |  | ATKINS_ATKINSG3 | BRAZOS | GAS | NORTH | 1954 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
ATKINS CTG 4 |  | ATKINS_ATKINSG4 | BRAZOS | GAS | NORTH | 1958 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
ATKINS CTG 5 |  | ATKINS_ATKINSG5 | BRAZOS | GAS | NORTH | 1965 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
ATKINS CTG 6 |  | ATKINS_ATKINSG6 | BRAZOS | GAS | NORTH | 1969 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
DELAWARE MOUNTAIN WIND FARM | 99INR0004 | KUNITZ_WIND_NWP | CULBERSON COUNTY | WIND | WEST | 1999 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5
KUNITZ WIND - WINDPOWER PARTNERS 1994 |  | KUNITZ_WIND_LGE | CULBERSON COUNTY | WIND | WEST | 1995 | 39.8 | 39.8 | 39.8 | 39.8 | 39.8 | 39.8 | 39.8 | 39.8 | 39.8 | 39.8
Total Retiring Capacity Unavailable to ERCOT | [6 empty] | 315.3 | 315.3 | 315.3 | 315.3 | 315.3 | 315.3 | 315.3 | 315.3 | 315.3 | 315.3
Excluded Resources, per notification from developer
COBISA-GREENVILLE | 06INR0006 |  | HUNT | GAS | NORTH | 2017 | 0 | 0 | 0 | 1820 | 1820 | 1820 | 1820 | 1820 | 1820 | 1820
Excluded Resources, pending water supply contract
PONDERA KING POWER PROJECT | 10INR0022 |  | HARRIS | GAS | HOUSTON | 2017 | 0 | 0 | 0 | 881.7 | 881.7 | 881.7 | 881.7 | 881.7 | 881.7 | 881.7

## SummerFuelTypes
Summer Fuel Types - ERCOT
Fuel type is based on the primary fuel. Capacity contribution of the wind resources is included at 12% for Non-Coastal and 56% for Coastal counties. Private Use Network, Hydro and Non-Synchronous Tie resources are included based on the three-year average historical capability for each Summer Season 20 peak load hours. Non-Synchronous Tie resources are categorized as Other. Mothballed resource capacity is excluded except for Available Mothball Capacity based on Owner's Return Probability.
In MW
Fuel_Type | Capacity_Pct | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024
Biomass | 100% | 235.3 | 235.3 | 235.3 | 235.3 | 235.3 | 235.3 | 235.3 | 235.3 | 235.3 | 235.3
Coal | 100% | 19219 | 19219 | 19219 | 19219 | 18379 | 18619 | 18619 | 18619 | 18619 | 18619
Gas | 100% | 48947.3 | 49749.4 | 51182.4 | 51182.4 | 51182.4 | 51182.4 | 51482.4 | 51482.4 | 51482.4 | 51482.4
Nuclear | 100% | 4981 | 4981 | 4981 | 4981 | 4981 | 4981 | 4981 | 4981 | 4981 | 4981
Other | 100% | 516.7 | 516.7 | 516.7 | 516.7 | 516.7 | 516.7 | 516.7 | 516.7 | 516.7 | 516.7
Hydro | 80% | 432.56 | 432.56 | 432.56 | 432.56 | 432.56 | 432.56 | 432.56 | 432.56 | 432.56 | 432.56
Wind | 12% | 1556.52 | 2138.808 | 2321.928 | 2321.928 | 2321.928 | 2321.928 | 2321.928 | 2321.928 | 2321.928 | 2321.928
Wind-C | 56% | 1054.144 | 1246.224 | 1336.384 | 1336.384 | 1336.384 | 1336.384 | 1336.384 | 1336.384 | 1336.384 | 1336.384
Solar | 100% | 188.8 | 393.8 | 393.8 | 393.8 | 393.8 | 393.8 | 393.8 | 393.8 | 393.8 | 393.8
Storage | 100% | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7
Total |  | 77165.024 | 78946.492 | 80652.772 | 80652.772 | 79812.772 | 80052.772 | 80352.772 | 80352.772 | 80352.772 | 80352.772
In Percentages
Fuel_Type |  | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024
Biomass |  | 0.3049% | 0.298% | 0.2917% | 0.2917% | 0.2948% | 0.2939% | 0.2928% | 0.2928% | 0.2928% | 0.2928%
Coal |  | 24.91% | 24.34% | 23.83% | 23.83% | 23.03% | 23.26% | 23.17% | 23.17% | 23.17% | 23.17%
Natural Gas |  | 63.43% | 63.02% | 63.46% | 63.46% | 64.13% | 63.94% | 64.07% | 64.07% | 64.07% | 64.07%
Nuclear |  | 6.455% | 6.309% | 6.176% | 6.176% | 6.241% | 6.222% | 6.199% | 6.199% | 6.199% | 6.199%
Other |  | 0.6696% | 0.6545% | 0.6406% | 0.6406% | 0.6474% | 0.6454% | 0.643% | 0.643% | 0.643% | 0.643%
Hydro |  | 0.5606% | 0.5479% | 0.5363% | 0.5363% | 0.542% | 0.5403% | 0.5383% | 0.5383% | 0.5383% | 0.5383%
Wind |  | 2.017% | 2.709% | 2.879% | 2.879% | 2.909% | 2.9% | 2.89% | 2.89% | 2.89% | 2.89%
Wind-C |  | 1.366% | 1.579% | 1.657% | 1.657% | 1.674% | 1.669% | 1.663% | 1.663% | 1.663% | 1.663%
Solar |  | 0.2447% | 0.4988% | 0.4883% | 0.4883% | 0.4934% | 0.4919% | 0.4901% | 0.4901% | 0.4901% | 0.4901%
Storage |  | 0.04367% | 0.04269% | 0.04178% | 0.04178% | 0.04222% | 0.0421% | 0.04194% | 0.04194% | 0.04194% | 0.04194%
Total |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%

## WinterSummary
Report on the Capacity, Demand, and Reserves in the ERCOT Region, 2015-2024
Winter Summary
Load Forecast, MW: |  | 2015/2016 | 2016/2017 | 2017/2018 | 2018/2019 | 2019/2020 | 2020/2021 | 2021/2022 | 2022/2023 | 2023/2024 | 2024/2025
| Total Winter Peak Demand (based on normal weather) | 52837.006 | 53719.121 | 54579.312 | 55440.7278 | 56280.6432 | 57115.7777 | 57962.0193 | 58804.466 | 59642.616 | 60479.6487
| less: LRS Serving as Responsive Reserve | -1145.052 | -1145.052 | -1145.052 | -1145.052 | -1145.052 | -1145.052 | -1145.052 | -1145.052 | -1145.052 | -1145.052
| less: LRS Serving as Non-Spinning Reserve | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| less: Emergency Response Service (10- and 30-min ramp products) | -1043.6 | -1329.5 | -1329.5 | -1329.5 | -1329.5 | -1329.5 | -1329.5 | -1329.5 | -1329.5 | -1329.5
| less: TDSP Standard Offer Load Management Programs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Firm Peak Load, MW | 50648.354 | 51244.569 | 52104.76 | 52966.1758 | 53806.0912 | 54641.2257 | 55487.4673 | 56329.914 | 57168.064 | 58005.0967
Resources, MW: |  | 2015/2016 | 2016/2017 | 2017/2018 | 2018/2019 | 2019/2020 | 2020/2021 | 2021/2022 | 2022/2023 | 2023/2024 | 2024/2025
| Installed Capacity, Thermal/Hydro | 66421.6 | 66421.6 | 66421.6 | 66421.6 | 65571.6 | 65571.6 | 65571.6 | 65571.6 | 65571.6 | 65571.6
| Capacity from Private Use Networks | 4318 | 4318 | 4318 | 4318 | 4318 | 4318 | 4318 | 4318 | 4318 | 4318
| Non-Coastal Wind, Peak Average Capacity Contribution (19%) | 1904.37 | 1904.37 | 1904.37 | 1904.37 | 1904.37 | 1904.37 | 1904.37 | 1904.37 | 1904.37 | 1904.37
| Coastal Wind, Peak Average Capacity Contribution (36%) | 604.944 | 604.944 | 604.944 | 604.944 | 604.944 | 604.944 | 604.944 | 604.944 | 604.944 | 604.944
| RMR Capacity to be under Contract | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operational Generation Capacity, MW | 73248.914 | 73248.914 | 73248.914 | 73248.914 | 72398.914 | 72398.914 | 72398.914 | 72398.914 | 72398.914 | 72398.914
| Capacity Contribution - Non-Synchronous Ties | 494.8 | 494.8 | 494.8 | 494.8 | 494.8 | 494.8 | 494.8 | 494.8 | 494.8 | 494.8
| Switchable Capacity | 3702 | 3702 | 3702 | 3702 | 3702 | 3702 | 3702 | 3702 | 3702 | 3702
| less: Switchable Capacity Unavailable to ERCOT | -470 | -824 | -824 | -824 | -824 | -524 | -524 | -524 | -524 | -524
| Available Mothballed Capacity | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58
| Planned Resources (not wind) with Signed IA, Air Permits and Water Rights | 1736.4 | 2146.4 | 3675.4 | 3675.4 | 3915.4 | 3915.4 | 3915.4 | 3915.4 | 3915.4 | 3915.4
| Planned Non-Coastal Wind with Signed IA, Peak Average Capacity Contribution (19%) | 1141.71 | 1512.02 | 1771.94 | 1771.94 | 1771.94 | 1771.94 | 1771.94 | 1771.94 | 1771.94 | 1771.94
| Planned Coastal Wind with Signed IA, Peak Average Capacity Contribution (36%) | 196.2 | 196.2 | 254.16 | 254.16 | 254.16 | 254.16 | 254.16 | 254.16 | 254.16 | 254.16
| less: Retiring Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Capacity, MW | 80108.024 | 80534.334 | 82381.214 | 82381.214 | 81771.214 | 82071.214 | 82071.214 | 82071.214 | 82071.214 | 82071.214
| Reserve Margin | 58.17% | 57.16% | 58.11% | 55.54% | 51.97% | 50.2% | 47.91% | 45.7% | 43.56% | 41.49%
(Total Resources - Firm Load Forecast) / Firm Load Forecast
Report on the Capacity, Demand, and Reserves in the ERCOT Region, 2015-2024
Winter Summary

## WinterCapacities
Unit Capacities - Winter
UNIT NAME | INR | UNIT CODE | COUNTY | FUEL | ZONE | IN SERVICE YR | 2015/2016 | 2016/2017 | 2017/2018 | 2018/2019 | 2019/2020 | 2020/2021 | 2021/2022 | 2022/2023 | 2023/2024 | 2024/2025
Operational Resources
COMANCHE PEAK U1 |  | CPSES_UNIT1 | SOMERVELL | NUCLEAR | NORTH | 1990 | 1235 | 1235 | 1235 | 1235 | 1235 | 1235 | 1235 | 1235 | 1235 | 1235
COMANCHE PEAK U2 |  | CPSES_UNIT2 | SOMERVELL | NUCLEAR | NORTH | 1993 | 1225 | 1225 | 1225 | 1225 | 1225 | 1225 | 1225 | 1225 | 1225 | 1225
SOUTH TEXAS U1 |  | STP_STP_G1 | MATAGORDA | NUCLEAR | SOUTH | 1988 | 1350 | 1350 | 1350 | 1350 | 1350 | 1350 | 1350 | 1350 | 1350 | 1350
SOUTH TEXAS U2 |  | STP_STP_G2 | MATAGORDA | NUCLEAR | SOUTH | 1989 | 1354 | 1354 | 1354 | 1354 | 1354 | 1354 | 1354 | 1354 | 1354 | 1354
BIG BROWN U1 |  | BBSES_UNIT1 | FREESTONE | COAL | NORTH | 1971 | 606 | 606 | 606 | 606 | 606 | 606 | 606 | 606 | 606 | 606
BIG BROWN U2 |  | BBSES_UNIT2 | FREESTONE | COAL | NORTH | 1972 | 602 | 602 | 602 | 602 | 602 | 602 | 602 | 602 | 602 | 602
COLETO CREEK |  | COLETO_COLETOG1 | GOLIAD | COAL | SOUTH | 1980 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660
FAYETTE POWER PROJECT U1 |  | FPPYD1_FPP_G1 | FAYETTE | COAL | SOUTH | 1979 | 603 | 603 | 603 | 603 | 603 | 603 | 603 | 603 | 603 | 603
FAYETTE POWER PROJECT U2 |  | FPPYD1_FPP_G2 | FAYETTE | COAL | SOUTH | 1980 | 605 | 605 | 605 | 605 | 605 | 605 | 605 | 605 | 605 | 605
FAYETTE POWER PROJECT U3 |  | FPPYD2_FPP_G3 | FAYETTE | COAL | SOUTH | 1988 | 449 | 449 | 449 | 449 | 449 | 449 | 449 | 449 | 449 | 449
GIBBONS CREEK U1 |  | GIBCRK_GIB_CRG1 | GRIMES | COAL | NORTH | 1983 | 470 | 470 | 470 | 470 | 470 | 470 | 470 | 470 | 470 | 470
J K SPRUCE U1 |  | CALAVERS_JKS1 | BEXAR | COAL | SOUTH | 1992 | 562 | 562 | 562 | 562 | 562 | 562 | 562 | 562 | 562 | 562
J K SPRUCE U2 | 09INR0002 | CALAVERS_JKS2 | BEXAR | COAL | SOUTH | 2010 | 775 | 775 | 775 | 775 | 775 | 775 | 775 | 775 | 775 | 775
J T DEELY U1 |  | CALAVERS_JTD1 | BEXAR | COAL | SOUTH | 1977 | 430 | 430 | 430 | 430 | 0 | 0 | 0 | 0 | 0 | 0
J T DEELY U2 |  | CALAVERS_JTD2 | BEXAR | COAL | SOUTH | 1978 | 420 | 420 | 420 | 420 | 0 | 0 | 0 | 0 | 0 | 0
LIMESTONE U1 |  | LEG_LEG_G1 | LIMESTONE | COAL | NORTH | 1985 | 831 | 831 | 831 | 831 | 831 | 831 | 831 | 831 | 831 | 831
LIMESTONE U2 |  | LEG_LEG_G2 | LIMESTONE | COAL | NORTH | 1986 | 858 | 858 | 858 | 858 | 858 | 858 | 858 | 858 | 858 | 858
MARTIN LAKE U1 |  | MLSES_UNIT1 | RUSK | COAL | NORTH | 1977 | 815 | 815 | 815 | 815 | 815 | 815 | 815 | 815 | 815 | 815
MARTIN LAKE U2 |  | MLSES_UNIT2 | RUSK | COAL | NORTH | 1978 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820
MONTICELLO U3 |  | MNSES_UNIT3 | TITUS | COAL | NORTH | 1978 | 795 | 795 | 795 | 795 | 795 | 795 | 795 | 795 | 795 | 795
OAK GROVE SES U1 | 09INR0006a | OGSES_UNIT1A | ROBERTSON | COAL | NORTH | 2010 | 840 | 840 | 840 | 840 | 840 | 840 | 840 | 840 | 840 | 840
OAK GROVE SES U2 | 09INR0006b | OGSES_UNIT2 | ROBERTSON | COAL | NORTH | 2011 | 825 | 825 | 825 | 825 | 825 | 825 | 825 | 825 | 825 | 825
OKLAUNION U1 |  | OKLA_OKLA_G1 | WILBARGER | COAL | WEST | 1986 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650
SAN MIGUEL U1 |  | SANMIGL_SANMIGG1 | ATASCOSA | COAL | SOUTH | 1982 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391
SANDOW U5 | 08INR0003 | SD5SES_UNIT5 | MILAM | COAL | SOUTH | 2010 | 570 | 570 | 570 | 570 | 570 | 570 | 570 | 570 | 570 | 570
SANDY CREEK U1 |  | SCES_UNIT1 | MCLENNAN | COAL | NORTH | 2013 | 970 | 970 | 970 | 970 | 970 | 970 | 970 | 970 | 970 | 970
TWIN OAKS U1 |  | TNP_ONE_TNP_O_1 | ROBERTSON | COAL | NORTH | 1990 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158
TWIN OAKS U2 |  | TNP_ONE_TNP_O_2 | ROBERTSON | COAL | NORTH | 1991 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158
W A PARISH U5 |  | WAP_WAP_G5 | FT. BEND | COAL | HOUSTON | 1977 | 659 | 659 | 659 | 659 | 659 | 659 | 659 | 659 | 659 | 659
W A PARISH U6 |  | WAP_WAP_G6 | FT. BEND | COAL | HOUSTON | 1978 | 658 | 658 | 658 | 658 | 658 | 658 | 658 | 658 | 658 | 658
W A PARISH U7 |  | WAP_WAP_G7 | FT. BEND | COAL | HOUSTON | 1980 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577
W A PARISH U8 |  | WAP_WAP_G8 | FT. BEND | COAL | HOUSTON | 1982 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610
A VON ROSENBERG 1 CTG 1 | 00INR0017 | BRAUNIG_AVR1_CT1 | BEXAR | GAS | SOUTH | 2000 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
A VON ROSENBERG 1 CTG 2 | 00INR0017 | BRAUNIG_AVR1_CT2 | BEXAR | GAS | SOUTH | 2000 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
A VON ROSENBERG 1 STG | 00INR0017 | BRAUNIG_AVR1_ST | BEXAR | GAS | SOUTH | 2000 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170
B M DAVIS CTG 3 | 09INR0038 | B_DAVIS_B_DAVIG3 | NUECES | GAS | SOUTH | 2010 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
B M DAVIS CTG 4 | 09INR0038 | B_DAVIS_B_DAVIG4 | NUECES | GAS | SOUTH | 2010 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
B M DAVIS STG 2 |  | B_DAVIS_B_DAVIG2 | NUECES | GAS | SOUTH | 1976 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320
BASTROP ENERGY CENTER CTG 1 | 01INR0021 | BASTEN_GTG1100 | BASTROP | GAS | SOUTH | 2002 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
BASTROP ENERGY CENTER CTG 2 | 01INR0021 | BASTEN_GTG2100 | BASTROP | GAS | SOUTH | 2002 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
BASTROP ENERGY CENTER STG | 01INR0021 | BASTEN_ST0100 | BASTROP | GAS | SOUTH | 2002 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234
BOSQUE COUNTY PEAKING CTG 1 | 00INR0018 | BOSQUESW_BSQSU_1 | BOSQUE | GAS | NORTH | 2000 | 166.6 | 166.6 | 166.6 | 166.6 | 166.6 | 166.6 | 166.6 | 166.6 | 166.6 | 166.6
BOSQUE COUNTY PEAKING CTG 2 | 00INR0018 | BOSQUESW_BSQSU_2 | BOSQUE | GAS | NORTH | 2000 | 166.6 | 166.6 | 166.6 | 166.6 | 166.6 | 166.6 | 166.6 | 166.6 | 166.6 | 166.6
BOSQUE COUNTY PEAKING CTG 3 | 00INR0018 | BOSQUESW_BSQSU_3 | BOSQUE | GAS | NORTH | 2001 | 168.5 | 168.5 | 168.5 | 168.5 | 168.5 | 168.5 | 168.5 | 168.5 | 168.5 | 168.5
BOSQUE COUNTY PEAKING STG 4 | 00INR0028 | BOSQUESW_BSQSU_4 | BOSQUE | GAS | NORTH | 2001 | 85.2 | 85.2 | 85.2 | 85.2 | 85.2 | 85.2 | 85.2 | 85.2 | 85.2 | 85.2
BOSQUE COUNTY PEAKING STG 5 | 08INR0046 | BOSQUESW_BSQSU_5 | BOSQUE | GAS | NORTH | 2009 | 200.7 | 200.7 | 200.7 | 200.7 | 200.7 | 200.7 | 200.7 | 200.7 | 200.7 | 200.7
BRAZOS VALLEY CTG 1 | 01INR0031 | BVE_UNIT1 | FORT BEND | GAS | HOUSTON | 2003 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168
BRAZOS VALLEY CTG 2 | 01INR0031 | BVE_UNIT2 | FORT BEND | GAS | HOUSTON | 2003 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168
BRAZOS VALLEY STG 3 | 01INR0031 | BVE_UNIT3 | FORT BEND | GAS | HOUSTON | 2003 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270
CALENERGY (FALCON SEABOARD) CTG 1 |  | FLCNS_UNIT1 | HOWARD | GAS | WEST | 1987 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5
CALENERGY (FALCON SEABOARD) CTG 2 |  | FLCNS_UNIT2 | HOWARD | GAS | WEST | 1987 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5
CALENERGY (FALCON SEABOARD) STG 3 |  | FLCNS_UNIT3 | HOWARD | GAS | WEST | 1988 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
CEDAR BAYOU CTG 4 | 08INR0035 | CBY4_CT41 | CHAMBERS | GAS | HOUSTON | 2009 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173
CEDAR BAYOU CTG 5 | 08INR0035 | CBY4_CT42 | CHAMBERS | GAS | HOUSTON | 2009 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173
CEDAR BAYOU STG 6 | 08INR0035 | CBY4_ST04 | CHAMBERS | GAS | HOUSTON | 2009 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186
COLORADO BEND ENERGY CENTER CTG 1 | 06INR0035 | CBEC_GT1 | WHARTON | GAS | HOUSTON | 2007 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88
COLORADO BEND ENERGY CENTER CTG 2 | 06INR0035 | CBEC_GT2 | WHARTON | GAS | HOUSTON | 2007 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84
COLORADO BEND ENERGY CENTER CTG 3 | 06INR0035 | CBEC_GT3 | WHARTON | GAS | HOUSTON | 2008 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88
COLORADO BEND ENERGY CENTER CTG 4 | 06INR0035 | CBEC_GT4 | WHARTON | GAS | HOUSTON | 2008 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83
COLORADO BEND ENERGY CENTER STG 1 | 06INR0035 | CBEC_STG1 | WHARTON | GAS | HOUSTON | 2007 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105
COLORADO BEND ENERGY CENTER STG 2 | 06INR0035 | CBEC_STG2 | WHARTON | GAS | HOUSTON | 2008 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108
CVC CHANNELVIEW CTG 1 | 02INR0004 | CVC_CVC_G1 | HARRIS | GAS | HOUSTON | 2008 | 157.8 | 157.8 | 157.8 | 157.8 | 157.8 | 157.8 | 157.8 | 157.8 | 157.8 | 157.8
CVC CHANNELVIEW CTG 2 | 02INR0004 | CVC_CVC_G2 | HARRIS | GAS | HOUSTON | 2008 | 166.5 | 166.5 | 166.5 | 166.5 | 166.5 | 166.5 | 166.5 | 166.5 | 166.5 | 166.5
CVC CHANNELVIEW CTG 3 | 02INR0004 | CVC_CVC_G3 | HARRIS | GAS | HOUSTON | 2008 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8
CVC CHANNELVIEW STG 5 | 02INR0004 | CVC_CVC_G5 | HARRIS | GAS | HOUSTON | 2008 | 132.9 | 132.9 | 132.9 | 132.9 | 132.9 | 132.9 | 132.9 | 132.9 | 132.9 | 132.9
DEER PARK ENERGY CENTER CTG 1 | 02INR0020 | DDPEC_GT1 | HARRIS | GAS | HOUSTON | 2002 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203
DEER PARK ENERGY CENTER CTG 2 | 02INR0020 | DDPEC_GT2 | HARRIS | GAS | HOUSTON | 2002 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215
DEER PARK ENERGY CENTER CTG 3 | 02INR0020 | DDPEC_GT3 | HARRIS | GAS | HOUSTON | 2002 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203
DEER PARK ENERGY CENTER CTG 4 | 02INR0020 | DDPEC_GT4 | HARRIS | GAS | HOUSTON | 2002 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215
DEER PARK ENERGY CENTER STG | 02INR0020 | DDPEC_ST1 | HARRIS | GAS | HOUSTON | 2002 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290
DEER PARK ENERGY CENTER CTG 6 | 14INR0015 | DDPEC_GT6 | HARRIS | GAS | HOUSTON | 2014 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190
ENNIS POWER STATION CTG 2 | 01INR0008 | ETCCS_CT1 | ELLIS | GAS | NORTH | 2002 | 231 | 231 | 231 | 231 | 231 | 231 | 231 | 231 | 231 | 231
ENNIS POWER STATION STG 1 | 01INR0008 | ETCCS_UNIT1 | ELLIS | GAS | NORTH | 2002 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127
FERGUSON REPLACEMENT CTG1 | 13INR0021 | FERGCC_FERGGT1 | LLANO | GAS | SOUTH | 2014 | 186.1 | 186.1 | 186.1 | 186.1 | 186.1 | 186.1 | 186.1 | 186.1 | 186.1 | 186.1
FERGUSON REPLACEMENT CTG2 | 13INR0021 | FERGCC_FERGGT2 | LLANO | GAS | SOUTH | 2014 | 186.1 | 186.1 | 186.1 | 186.1 | 186.1 | 186.1 | 186.1 | 186.1 | 186.1 | 186.1
FERGUSON REPLACEMENT STG | 13INR0021 | FERGCC_FERGST1 | LLANO | GAS | SOUTH | 2014 | 194.9 | 194.9 | 194.9 | 194.9 | 194.9 | 194.9 | 194.9 | 194.9 | 194.9 | 194.9
FORNEY ENERGY CENTER CTG 11 | 01INR0007 | FRNYPP_GT11 | KAUFMAN | GAS | NORTH | 2003 | 191 | 191 | 191 | 191 | 191 | 191 | 191 | 191 | 191 | 191
FORNEY ENERGY CENTER CTG 12 | 01INR0007 | FRNYPP_GT12 | KAUFMAN | GAS | NORTH | 2003 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183
FORNEY ENERGY CENTER CTG 13 | 01INR0007 | FRNYPP_GT13 | KAUFMAN | GAS | NORTH | 2003 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183
FORNEY ENERGY CENTER CTG 21 | 01INR0007 | FRNYPP_GT21 | KAUFMAN | GAS | NORTH | 2003 | 191 | 191 | 191 | 191 | 191 | 191 | 191 | 191 | 191 | 191
FORNEY ENERGY CENTER CTG 22 | 01INR0007 | FRNYPP_GT22 | KAUFMAN | GAS | NORTH | 2003 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183
FORNEY ENERGY CENTER CTG 23 | 01INR0007 | FRNYPP_GT23 | KAUFMAN | GAS | NORTH | 2003 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183
FORNEY ENERGY CENTER STG 10 | 01INR0007 | FRNYPP_ST10 | KAUFMAN | GAS | NORTH | 2003 | 417 | 417 | 417 | 417 | 417 | 417 | 417 | 417 | 417 | 417
FORNEY ENERGY CENTER STG 20 | 01INR0007 | FRNYPP_ST20 | KAUFMAN | GAS | NORTH | 2003 | 417 | 417 | 417 | 417 | 417 | 417 | 417 | 417 | 417 | 417
FREESTONE ENERGY CENTER CTG 1 | 01INR0009 | FREC_GT1 | FREESTONE | GAS | NORTH | 2002 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7
FREESTONE ENERGY CENTER CTG 2 | 01INR0009 | FREC_GT2 | FREESTONE | GAS | NORTH | 2002 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7
FREESTONE ENERGY CENTER STG 3 | 01INR0009 | FREC_ST3 | FREESTONE | GAS | NORTH | 2002 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8
FREESTONE ENERGY CENTER CTG 4 | 01INR0009 | FREC_GT4 | FREESTONE | GAS | NORTH | 2002 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1
FREESTONE ENERGY CENTER CTG 5 | 01INR0009 | FREC_GT5 | FREESTONE | GAS | NORTH | 2002 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1
FREESTONE ENERGY CENTER STG 6 | 01INR0009 | FREC_ST6 | FREESTONE | GAS | NORTH | 2002 | 179.7 | 179.7 | 179.7 | 179.7 | 179.7 | 179.7 | 179.7 | 179.7 | 179.7 | 179.7
GUADALUPE GEN STN CTG 1 | 01INR0004 | GUADG_GAS1 | GUADALUPE | GAS | SOUTH | 2000 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
GUADALUPE GEN STN CTG 2 | 01INR0004 | GUADG_GAS2 | GUADALUPE | GAS | SOUTH | 2000 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
GUADALUPE GEN STN CTG 3 | 01INR0004 | GUADG_GAS3 | GUADALUPE | GAS | SOUTH | 2000 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
GUADALUPE GEN STN CTG 4 | 01INR0004 | GUADG_GAS4 | GUADALUPE | GAS | SOUTH | 2000 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
GUADALUPE GEN STN STG 5 | 01INR0004 | GUADG_STM5 | GUADALUPE | GAS | SOUTH | 2000 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203
GUADALUPE GEN STN STG 6 | 01INR0004 | GUADG_STM6 | GUADALUPE | GAS | SOUTH | 2000 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203
HAYS ENERGY FACILITY CSG 1 | 01INR0003 | HAYSEN_HAYSENG1 | HAYS | GAS | SOUTH | 2002 | 237 | 237 | 237 | 237 | 237 | 237 | 237 | 237 | 237 | 237
HAYS ENERGY FACILITY CSG 2 | 01INR0003 | HAYSEN_HAYSENG2 | HAYS | GAS | SOUTH | 2002 | 237 | 237 | 237 | 237 | 237 | 237 | 237 | 237 | 237 | 237
HAYS ENERGY FACILITY CSG 3 | 01INR0003 | HAYSEN_HAYSENG3 | HAYS | GAS | SOUTH | 2002 | 247 | 247 | 247 | 247 | 247 | 247 | 247 | 247 | 247 | 247
HAYS ENERGY FACILITY CSG 4 | 01INR0003 | HAYSEN_HAYSENG4 | HAYS | GAS | SOUTH | 2002 | 247 | 247 | 247 | 247 | 247 | 247 | 247 | 247 | 247 | 247
HIDALGO CTG 1 | 00INR0006 | DUKE_DUKE_GT1 | HIDALGO | GAS | SOUTH | 2000 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
HIDALGO CTG 2 | 00INR0006 | DUKE_DUKE_GT2 | HIDALGO | GAS | SOUTH | 2000 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
HIDALGO STG | 00INR0006 | DUKE_DUKE_ST1 | HIDALGO | GAS | SOUTH | 2000 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176
JACK COUNTY GEN FACILITY CTG 1 | 05INR0010 | JACKCNTY_CT1 | JACK | GAS | NORTH | 2005 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
JACK COUNTY GEN FACILITY CTG 2 | 05INR0010 | JACKCNTY_CT2 | JACK | GAS | NORTH | 2005 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
JACK COUNTY GEN FACILITY STG 1 | 05INR0010 | JACKCNTY_STG | JACK | GAS | NORTH | 2005 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310
JACK COUNTY GEN FACILITY CTG 3 | 10INR0010 | JCKCNTY2_CT3 | JACK | GAS | NORTH | 2011 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
JACK COUNTY GEN FACILITY CTG 4 | 10INR0010 | JCKCNTY2_CT4 | JACK | GAS | NORTH | 2011 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
JACK COUNTY GEN FACILITY STG 2 | 10INR0010 | JCKCNTY2_ST2 | JACK | GAS | NORTH | 2011 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310
JOHNSON COUNTY GEN FACILITY CTG |  | TEN_CT1 | JOHNSON | GAS | NORTH | 1997 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177
JOHNSON COUNTY GEN FACILITY STG |  | TEN_STG | JOHNSON | GAS | NORTH | 1997 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106
LAMAR POWER PROJECT CTG 11 | 00INR0008 | LPCCS_CT11 | LAMAR | GAS | NORTH | 2000 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186
LAMAR POWER PROJECT CTG 12 | 00INR0008 | LPCCS_CT12 | LAMAR | GAS | NORTH | 2000 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176
LAMAR POWER PROJECT CTG 21 | 00INR0008 | LPCCS_CT21 | LAMAR | GAS | NORTH | 2000 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176
LAMAR POWER PROJECT CTG 22 | 00INR0008 | LPCCS_CT22 | LAMAR | GAS | NORTH | 2000 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186
LAMAR POWER PROJECT STG 1 | 00INR0008 | LPCCS_UNIT1 | LAMAR | GAS | NORTH | 2000 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204
LAMAR POWER PROJECT STG 2 | 00INR0008 | LPCCS_UNIT2 | LAMAR | GAS | NORTH | 2000 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204
LOST PINES CTG 1 | 02INR0005 | LOSTPI_LOSTPGT1 | BASTROP | GAS | SOUTH | 2001 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183
LOST PINES CTG 2 | 02INR0005 | LOSTPI_LOSTPGT2 | BASTROP | GAS | SOUTH | 2001 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183
LOST PINES STG | 02INR0005 | LOSTPI_LOSTPST1 | BASTROP | GAS | SOUTH | 2001 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192
MAGIC VALLEY CTG 1 | 00INR0009 | NEDIN_NEDIN_G1 | HIDALGO | GAS | SOUTH | 2001 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6
MAGIC VALLEY CTG 2 | 00INR0009 | NEDIN_NEDIN_G2 | HIDALGO | GAS | SOUTH | 2001 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6
MAGIC VALLEY STG | 00INR0009 | NEDIN_NEDIN_G3 | HIDALGO | GAS | SOUTH | 2001 | 257.9 | 257.9 | 257.9 | 257.9 | 257.9 | 257.9 | 257.9 | 257.9 | 257.9 | 257.9
MIDLOTHIAN CS 1 | 00INR0012 | MDANP_CT1 | ELLIS | GAS | NORTH | 2001 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240
MIDLOTHIAN CS 2 | 00INR0012 | MDANP_CT2 | ELLIS | GAS | NORTH | 2001 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240
MIDLOTHIAN CS 3 | 00INR0012 | MDANP_CT3 | ELLIS | GAS | NORTH | 2001 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240
MIDLOTHIAN CS 4 | 00INR0012 | MDANP_CT4 | ELLIS | GAS | NORTH | 2001 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240
MIDLOTHIAN CS 5 | 02INR0008 | MDANP_CT5 | ELLIS | GAS | NORTH | 2002 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257
MIDLOTHIAN CS 6 | 02INR0008 | MDANP_CT6 | ELLIS | GAS | NORTH | 2002 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257
NUECES BAY CTG 8 | 09INR0039 | NUECES_B_NUECESG8 | NUECES | GAS | SOUTH | 2010 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
NUECES BAY CTG 9 | 09INR0039 | NUECES_B_NUECESG9 | NUECES | GAS | SOUTH | 2010 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
NUECES BAY STG 7 |  | NUECES_B_NUECESG7 | NUECES | GAS | SOUTH | 1972 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320
ODESSA-ECTOR GEN STN CTG 11 | 01INR0026 | OECCS_CT11 | ECTOR | GAS | WEST | 2001 | 162.6 | 162.6 | 162.6 | 162.6 | 162.6 | 162.6 | 162.6 | 162.6 | 162.6 | 162.6
ODESSA-ECTOR GEN STN CTG 12 | 01INR0026 | OECCS_CT12 | ECTOR | GAS | WEST | 2001 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2
ODESSA-ECTOR GEN STN CTG 21 | 01INR0026 | OECCS_CT21 | ECTOR | GAS | WEST | 2001 | 155.8 | 155.8 | 155.8 | 155.8 | 155.8 | 155.8 | 155.8 | 155.8 | 155.8 | 155.8
ODESSA-ECTOR GEN STN CTG 22 | 01INR0026 | OECCS_CT22 | ECTOR | GAS | WEST | 2001 | 153.3 | 153.3 | 153.3 | 153.3 | 153.3 | 153.3 | 153.3 | 153.3 | 153.3 | 153.3
ODESSA-ECTOR GEN STN STG 1 | 01INR0026 | OECCS_UNIT1 | ECTOR | GAS | WEST | 2001 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216
ODESSA-ECTOR GEN STN STG 2 | 01INR0026 | OECCS_UNIT2 | ECTOR | GAS | WEST | 2001 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216
PANDA SHERMAN CTG1 | 10INR0021 | PANDA_S_SHER1CT1 | GRAYSON | GAS | NORTH | 2014 | 218.45 | 218.45 | 218.45 | 218.45 | 218.45 | 218.45 | 218.45 | 218.45 | 218.45 | 218.45
PANDA SHERMAN CTG2 | 10INR0021 | PANDA_S_SHER1CT2 | GRAYSON | GAS | NORTH | 2014 | 218.45 | 218.45 | 218.45 | 218.45 | 218.45 | 218.45 | 218.45 | 218.45 | 218.45 | 218.45
PANDA SHERMAN STG | 10INR0021 | PANDA_S_SHER1ST1 | GRAYSON | GAS | NORTH | 2014 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6
PANDA TEMPLE CTG1 | 10INR0020a | PANDA_T1_TMPL1CT1 | BELL | GAS | NORTH | 2014 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5
PANDA TEMPLE CTG2 | 10INR0020a | PANDA_T1_TMPL1CT2 | BELL | GAS | NORTH | 2014 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5
PANDA TEMPLE STG | 10INR0020a | PANDA_T1_TMPL1ST1 | BELL | GAS | NORTH | 2014 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6
PARIS ENERGY CENTER CTG 1 |  | TNSKA_GT1 | LAMAR | GAS | NORTH | 1989 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87
PARIS ENERGY CENTER CTG 2 |  | TNSKA_GT2 | LAMAR | GAS | NORTH | 1989 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87
PARIS ENERGY CENTER STG |  | TNSKA_STG | LAMAR | GAS | NORTH | 1990 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89
PASGEN CTG 2 |  | PSG_PSG_GT2 | HARRIS | GAS | HOUSTON | 2000 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176
PASGEN CTG 3 |  | PSG_PSG_GT3 | HARRIS | GAS | HOUSTON | 2000 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176
PASGEN STG 2 |  | PSG_PSG_ST2 | HARRIS | GAS | HOUSTON | 2000 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
QUAIL RUN ENERGY CTG 1 | 06INR0036 | QALSW_GT2 | ECTOR | GAS | WEST | 2007 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86
QUAIL RUN ENERGY CTG 2 | 06INR0036 | QALSW_GT3 | ECTOR | GAS | WEST | 2008 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
QUAIL RUN ENERGY CTG 3 | 06INR0036 | QALSW_STG1 | ECTOR | GAS | WEST | 2007 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
QUAIL RUN ENERGY CTG 4 | 06INR0036 | QALSW_STG2 | ECTOR | GAS | WEST | 2008 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
QUAIL RUN ENERGY STG 1 | 06INR0036 | QALSW_GT1 | ECTOR | GAS | WEST | 2007 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84
QUAIL RUN ENERGY STG 2 | 06INR0036 | QALSW_GT4 | ECTOR | GAS | WEST | 2008 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
SAM RAYBURN CTG 7 | 03INR0014 | RAYBURN_RAYBURG7 | VICTORIA | GAS | SOUTH | 2003 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
RIO NOGALES CTG 1 | 02INR0001 | RIONOG_CT1 | GUADALUPE | GAS | SOUTH | 2002 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175
RIO NOGALES CTG 2 | 02INR0001 | RIONOG_CT2 | GUADALUPE | GAS | SOUTH | 2002 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175
RIO NOGALES CTG 3 | 02INR0001 | RIONOG_CT3 | GUADALUPE | GAS | SOUTH | 2002 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175
RIO NOGALES STG 4 | 02INR0001 | RIONOG_ST1 | GUADALUPE | GAS | SOUTH | 2002 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323
SAM RAYBURN CTG 8 | 03INR0014 | RAYBURN_RAYBURG8 | VICTORIA | GAS | SOUTH | 2003 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51
SAM RAYBURN CTG 9 | 03INR0014 | RAYBURN_RAYBURG9 | VICTORIA | GAS | SOUTH | 2003 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
SAM RAYBURN STG 10 | 03INR0014 | RAYBURN_RAYBURG10 | VICTORIA | GAS | SOUTH | 2003 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
SANDHILL ENERGY CENTER CTG 5A | 03INR0033 | SANDHSYD_SH_5A | TRAVIS | GAS | SOUTH | 2004 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170
SANDHILL ENERGY CENTER STG 5C | 03INR0033 | SANDHSYD_SH_5C | TRAVIS | GAS | SOUTH | 2004 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
SILAS RAY STG 6 |  | SILASRAY_SILAS_6 | CAMERON | GAS | SOUTH | 1962 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
SILAS RAY CTG 9 |  | SILASRAY_SILAS_9 | CAMERON | GAS | SOUTH | 1996 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49
T H WHARTON CTG 31 |  | THW_THWGT31 | HARRIS | GAS | HOUSTON | 1972 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON CTG 32 |  | THW_THWGT32 | HARRIS | GAS | HOUSTON | 1972 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON CTG 33 |  | THW_THWGT33 | HARRIS | GAS | HOUSTON | 1972 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON CTG 34 |  | THW_THWGT34 | HARRIS | GAS | HOUSTON | 1972 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON STG 3 |  | THW_THWST_3 | HARRIS | GAS | HOUSTON | 1974 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104
T H WHARTON CTG 41 |  | THW_THWGT41 | HARRIS | GAS | HOUSTON | 1972 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON CTG 42 |  | THW_THWGT42 | HARRIS | GAS | HOUSTON | 1972 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON CTG 43 |  | THW_THWGT43 | HARRIS | GAS | HOUSTON | 1974 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON CTG 44 |  | THW_THWGT44 | HARRIS | GAS | HOUSTON | 1974 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON STG 4 |  | THW_THWST_4 | HARRIS | GAS | HOUSTON | 1974 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104
TEXAS CITY CTG A |  | TXCTY_CTA | GALVESTON | GAS | HOUSTON | 2000 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4
TEXAS CITY CTG B |  | TXCTY_CTB | GALVESTON | GAS | HOUSTON | 2000 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4
TEXAS CITY CTG C |  | TXCTY_CTC | GALVESTON | GAS | HOUSTON | 2000 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4
TEXAS CITY STG |  | TXCTY_ST | GALVESTON | GAS | HOUSTON | 2000 | 131.5 | 131.5 | 131.5 | 131.5 | 131.5 | 131.5 | 131.5 | 131.5 | 131.5 | 131.5
VICTORIA POWER STATION CTG 6 | 08INR0050 | VICTORIA_VICTORG6 | VICTORIA | GAS | SOUTH | 2009 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168
VICTORIA POWER STATION STG 5 | 08INR0050 | VICTORIA_VICTORG5 | VICTORIA | GAS | SOUTH | 1963 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132
WICHITA FALLS CTG 1 |  | WFCOGEN_UNIT1 | WICHITA | GAS | WEST | 1987 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
WICHITA FALLS CTG 2 |  | WFCOGEN_UNIT2 | WICHITA | GAS | WEST | 1987 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
WICHITA FALLS CTG 3 |  | WFCOGEN_UNIT3 | WICHITA | GAS | WEST | 1987 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
WICHITA FALLS STG 4 |  | WFCOGEN_UNIT4 | WICHITA | GAS | WEST | 1987 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
WISE-TRACTEBEL POWER CTG 1 | 02INR0009 | WCPP_CT1 | WISE | GAS | NORTH | 2004 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275
WISE-TRACTEBEL POWER CTG 2 | 02INR0009 | WCPP_CT2 | WISE | GAS | NORTH | 2004 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275
WISE-TRACTEBEL POWER STG 1 | 02INR0009 | WCPP_ST1 | WISE | GAS | NORTH | 2004 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290
WOLF HOLLOW POWER CTG 1 | 01INR0015 | WHCCS_CT1 | HOOD | GAS | NORTH | 2002 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249
WOLF HOLLOW POWER CTG 2 | 01INR0015 | WHCCS_CT2 | HOOD | GAS | NORTH | 2002 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249
WOLF HOLLOW POWER STG | 01INR0015 | WHCCS_STG | HOOD | GAS | NORTH | 2002 | 293 | 293 | 293 | 293 | 293 | 293 | 293 | 293 | 293 | 293
ATKINS 7 |  | ATKINS_ATKINSG7 | BRAZOS | GAS | NORTH | 1973 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
DANSBY CTG 2 |  | DANSBY_DANSBYG2 | BRAZOS | GAS | NORTH | 2004 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
DANSBY CTG 3 | 09INR0072 | DANSBY_DANSBYG3 | BRAZOS | GAS | NORTH | 2010 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
DECKER CREEK CTG 1 |  | DECKER_DPGT_1 | TRAVIS | GAS | SOUTH | 1989 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
DECKER CREEK CTG 2 |  | DECKER_DPGT_2 | TRAVIS | GAS | SOUTH | 1989 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
DECKER CREEK CTG 3 |  | DECKER_DPGT_3 | TRAVIS | GAS | SOUTH | 1989 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
DECKER CREEK CTG 4 |  | DECKER_DPGT_4 | TRAVIS | GAS | SOUTH | 1989 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
DECORDOVA CTG 1 |  | DCSES_CT10 | HOOD | GAS | NORTH | 1990 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
DECORDOVA CTG 2 |  | DCSES_CT20 | HOOD | GAS | NORTH | 1990 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
DECORDOVA CTG 3 |  | DCSES_CT30 | HOOD | GAS | NORTH | 1990 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
DECORDOVA CTG 4 |  | DCSES_CT40 | HOOD | GAS | NORTH | 1990 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77
EXTEX LAPORTE GEN STN CTG 1 | 01INR0044 | AZ_AZ_G1 | HARRIS | GAS | HOUSTON | 2009 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
EXTEX LAPORTE GEN STN CTG 2 | 01INR0044 | AZ_AZ_G2 | HARRIS | GAS | HOUSTON | 2009 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
EXTEX LAPORTE GEN STN CTG 3 | 01INR0044 | AZ_AZ_G3 | HARRIS | GAS | HOUSTON | 2009 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
EXTEX LAPORTE GEN STN CTG 4 | 01INR0044 | AZ_AZ_G4 | HARRIS | GAS | HOUSTON | 2009 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
GREENS BAYOU CTG 73 |  | GBY_GBYGT73 | HARRIS | GAS | HOUSTON | 1976 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
GREENS BAYOU CTG 74 |  | GBY_GBYGT74 | HARRIS | GAS | HOUSTON | 1976 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
GREENS BAYOU CTG 81 |  | GBY_GBYGT81 | HARRIS | GAS | HOUSTON | 1976 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
GREENS BAYOU CTG 83 |  | GBY_GBYGT83 | HARRIS | GAS | HOUSTON | 1976 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64
GREENS BAYOU CTG 84 |  | GBY_GBYGT84 | HARRIS | GAS | HOUSTON | 1976 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
GREENVILLE ENGINE PLANT | 10INR0070 | STEAM_ENGINE_1 | HUNT | GAS | NORTH | 2010 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4
GREENVILLE ENGINE PLANT | 10INR0070 | STEAM_ENGINE_2 | HUNT | GAS | NORTH | 2010 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4
GREENVILLE ENGINE PLANT | 10INR0070 | STEAM_ENGINE_3 | HUNT | GAS | NORTH | 2010 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4
LAREDO CTG 4 | 08INR0064 | LARDVFTN_G4 | WEBB | GAS | SOUTH | 2008 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5
LAREDO CTG 5 | 08INR0064 | LARDVFTN_G5 | WEBB | GAS | SOUTH | 2008 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5
LEON CREEK PEAKER CTG 1 | 04INR0009 | LEON_CRK_LCPCT1 | BEXAR | GAS | SOUTH | 2004 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
LEON CREEK PEAKER CTG 2 | 04INR0009 | LEON_CRK_LCPCT2 | BEXAR | GAS | SOUTH | 2004 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
LEON CREEK PEAKER CTG 3 | 04INR0009 | LEON_CRK_LCPCT3 | BEXAR | GAS | SOUTH | 2004 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
LEON CREEK PEAKER CTG 4 | 04INR0009 | LEON_CRK_LCPCT4 | BEXAR | GAS | SOUTH | 2004 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
MORGAN CREEK CTG 1 |  | MGSES_CT1 | MITCHELL | GAS | WEST | 1988 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
MORGAN CREEK CTG 2 |  | MGSES_CT2 | MITCHELL | GAS | WEST | 1988 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
MORGAN CREEK CTG 3 |  | MGSES_CT3 | MITCHELL | GAS | WEST | 1988 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
MORGAN CREEK CTG 4 |  | MGSES_CT4 | MITCHELL | GAS | WEST | 1988 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
MORGAN CREEK CTG 5 |  | MGSES_CT5 | MITCHELL | GAS | WEST | 1988 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
MORGAN CREEK CTG 6 |  | MGSES_CT6 | MITCHELL | GAS | WEST | 1988 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
PEARSALL IC ENGINE PLANT A | 09INR0079a | PEARSAL2_AGR_A | FRIO | GAS | SOUTH | 2012 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
PEARSALL IC ENGINE PLANT B | 09INR0079a | PEARSAL2_AGR_B | FRIO | GAS | SOUTH | 2012 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
PEARSALL IC ENGINE PLANT C | 09INR0079b | PEARSAL2_AGR_C | FRIO | GAS | SOUTH | 2012 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
PEARSALL IC ENGINE PLANT D | 09INR0079b | PEARSAL2_AGR_D | FRIO | GAS | SOUTH | 2012 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
PERMIAN BASIN CTG 1 |  | PB2SES_CT1 | WARD | GAS | WEST | 1988 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71
PERMIAN BASIN CTG 2 |  | PB2SES_CT2 | WARD | GAS | WEST | 1988 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71
PERMIAN BASIN CTG 3 |  | PB2SES_CT3 | WARD | GAS | WEST | 1988 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
PERMIAN BASIN CTG 4 |  | PB2SES_CT4 | WARD | GAS | WEST | 1990 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
PERMIAN BASIN CTG 5 |  | PB2SES_CT5 | WARD | GAS | WEST | 1990 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
R W MILLER CTG 4 |  | MIL_MILLERG4 | PALO PINTO | GAS | NORTH | 2000 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115
R W MILLER CTG 5 |  | MIL_MILLERG5 | PALO PINTO | GAS | NORTH | 2000 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115
RAY OLINGER CTG 4 | 00INR0024 | OLINGR_OLING_4 | COLLIN | GAS | NORTH | 2001 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84
SAM RAYBURN CTG 1 |  | RAYBURN_RAYBURG1 | VICTORIA | GAS | SOUTH | 1963 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5
SAM RAYBURN CTG 2 |  | RAYBURN_RAYBURG2 | VICTORIA | GAS | SOUTH | 1963 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5
SAN JACINTO SES CTG 1 |  | SJS_SJS_G1 | HARRIS | GAS | HOUSTON | 1995 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
SAN JACINTO SES CTG 2 |  | SJS_SJS_G2 | HARRIS | GAS | HOUSTON | 1995 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
SANDHILL ENERGY CENTER CTG 1 | 01INR0041 | SANDHSYD_SH1 | TRAVIS | GAS | SOUTH | 2001 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SANDHILL ENERGY CENTER CTG 2 | 01INR0041 | SANDHSYD_SH2 | TRAVIS | GAS | SOUTH | 2001 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SANDHILL ENERGY CENTER CTG 3 | 01INR0041 | SANDHSYD_SH3 | TRAVIS | GAS | SOUTH | 2001 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SANDHILL ENERGY CENTER CTG 4 | 01INR0041 | SANDHSYD_SH4 | TRAVIS | GAS | SOUTH | 2001 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SANDHILL ENERGY CENTER CTG 6 | 09INR0045 | SANDHSYD_SH6 | TRAVIS | GAS | SOUTH | 2010 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SANDHILL ENERGY CENTER CTG 7 | 09INR0045 | SANDHSYD_SH7 | TRAVIS | GAS | SOUTH | 2010 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SILAS RAY CTG 10 | 04INR0014 | SILASRAY_SILAS_10 | CAMERON | GAS | SOUTH | 2004 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
T H WHARTON CTG 51 |  | THW_THWGT51 | HARRIS | GAS | HOUSTON | 1975 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON CTG 52 |  | THW_THWGT52 | HARRIS | GAS | HOUSTON | 1975 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON CTG 53 |  | THW_THWGT53 | HARRIS | GAS | HOUSTON | 1975 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON CTG 54 |  | THW_THWGT54 | HARRIS | GAS | HOUSTON | 1975 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON CTG 55 |  | THW_THWGT55 | HARRIS | GAS | HOUSTON | 1975 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON CTG 56 |  | THW_THWGT56 | HARRIS | GAS | HOUSTON | 1975 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON CTG G1 |  | THW_THWGT_1 | HARRIS | GAS | HOUSTON | 1967 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
TEXAS GULF SULPHUR |  | TGF_TGFGT_1 | WHARTON | GAS | HOUSTON | 1985 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89
V H BRAUNIG CTG 5 | 09INR0028 | BRAUNIG_VHB6CT5 | BEXAR | GAS | SOUTH | 2009 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
V H BRAUNIG CTG 6 | 09INR0028 | BRAUNIG_VHB6CT6 | BEXAR | GAS | SOUTH | 2009 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
V H BRAUNIG CTG 7 | 09INR0028 | BRAUNIG_VHB6CT7 | BEXAR | GAS | SOUTH | 2009 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
V H BRAUNIG CTG 8 | 09INR0028 | BRAUNIG_VHB6CT8 | BEXAR | GAS | SOUTH | 2009 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
W A PARISH CTG 1 |  | WAP_WAPGT_1 | FT. BEND | GAS | HOUSTON | 1967 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
W A PARISH - PETRA NOVA CTG | 12INR0086 | PNPI_GT2 | FORT BEND | GAS | HOUSTON | 2013 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88
WINCHESTER POWER PARK CTG 1 | 09INR0027 | WIPOPA_WPP_G1 | FAYETTE | GAS | SOUTH | 2009 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
WINCHESTER POWER PARK CTG 2 | 09INR0027 | WIPOPA_WPP_G2 | FAYETTE | GAS | SOUTH | 2009 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
WINCHESTER POWER PARK CTG 3 | 09INR0027 | WIPOPA_WPP_G3 | FAYETTE | GAS | SOUTH | 2009 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
WINCHESTER POWER PARK CTG 4 | 09INR0027 | WIPOPA_WPP_G4 | FAYETTE | GAS | SOUTH | 2009 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
B M DAVIS STG U1 |  | B_DAVIS_B_DAVIG1 | NUECES | GAS | SOUTH | 1974 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335
CEDAR BAYOU STG U1 |  | CBY_CBY_G1 | CHAMBERS | GAS | HOUSTON | 1970 | 745 | 745 | 745 | 745 | 745 | 745 | 745 | 745 | 745 | 745
CEDAR BAYOU STG U2 |  | CBY_CBY_G2 | CHAMBERS | GAS | HOUSTON | 1972 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749
DANSBY STG U1 |  | DANSBY_DANSBYG1 | BRAZOS | GAS | NORTH | 1978 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
DECKER CREEK STG U1 |  | DECKER_DPG1 | TRAVIS | GAS | SOUTH | 1971 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320
DECKER CREEK STG U2 |  | DECKER_DPG2 | TRAVIS | GAS | SOUTH | 1978 | 428 | 428 | 428 | 428 | 428 | 428 | 428 | 428 | 428 | 428
GRAHAM STG U1 |  | GRSES_UNIT1 | YOUNG | GAS | WEST | 1960 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225
GRAHAM STG U2 |  | GRSES_UNIT2 | YOUNG | GAS | WEST | 1969 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390
GREENS BAYOU STG U5 |  | GBY_GBY_5 | HARRIS | GAS | HOUSTON | 1973 | 371 | 371 | 371 | 371 | 371 | 371 | 371 | 371 | 371 | 371
HANDLEY STG U3 |  | HLSES_UNIT3 | TARRANT | GAS | NORTH | 1963 | 395 | 395 | 395 | 395 | 395 | 395 | 395 | 395 | 395 | 395
HANDLEY STG U4 |  | HLSES_UNIT4 | TARRANT | GAS | NORTH | 1976 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435
HANDLEY STG U5 |  | HLSES_UNIT5 | TARRANT | GAS | NORTH | 1977 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435
LAKE HUBBARD STG U1 |  | LHSES_UNIT1 | DALLAS | GAS | NORTH | 1970 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392
LAKE HUBBARD STG U2 |  | LHSES_UNIT2A | DALLAS | GAS | NORTH | 1973 | 515 | 515 | 515 | 515 | 515 | 515 | 515 | 515 | 515 | 515
MOUNTAIN CREEK STG U6 |  | MCSES_UNIT6 | DALLAS | GAS | NORTH | 1956 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122
MOUNTAIN CREEK STG U7 |  | MCSES_UNIT7 | DALLAS | GAS | NORTH | 1958 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118
MOUNTAIN CREEK STG U8 |  | MCSES_UNIT8 | DALLAS | GAS | NORTH | 1967 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568
O W SOMMERS STG U1 |  | CALAVERS_OWS1 | BEXAR | GAS | SOUTH | 1972 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
O W SOMMERS STG U2 |  | CALAVERS_OWS2 | BEXAR | GAS | SOUTH | 1974 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
PEARSALL STG U1 |  | PEARSALL_PEARS_1 | FRIO | GAS | SOUTH | 1961 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
PEARSALL STG U2 |  | PEARSALL_PEARS_2 | FRIO | GAS | SOUTH | 1961 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
PEARSALL STG U3 |  | PEARSALL_PEARS_3 | FRIO | GAS | SOUTH | 1961 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
POWERLANE PLANT STG U1 |  | STEAM1A_STEAM_1 | HUNT | GAS | NORTH | 1966 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
POWERLANE PLANT STG U2 |  | STEAM_STEAM_2 | HUNT | GAS | NORTH | 1967 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
POWERLANE PLANT STG U3 |  | STEAM_STEAM_3 | HUNT | GAS | NORTH | 1978 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41
R W MILLER STG U1 |  | MIL_MILLERG1 | PALO PINTO | GAS | NORTH | 2000 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
R W MILLER STG U2 |  | MIL_MILLERG2 | PALO PINTO | GAS | NORTH | 2000 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
R W MILLER STG U3 |  | MIL_MILLERG3 | PALO PINTO | GAS | NORTH | 2000 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208
RAY OLINGER STG U1 |  | OLINGR_OLING_1 | COLLIN | GAS | NORTH | 1967 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
RAY OLINGER STG U2 |  | OLINGR_OLING_2 | COLLIN | GAS | NORTH | 1971 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107
RAY OLINGER STG U3 |  | OLINGR_OLING_3 | COLLIN | GAS | NORTH | 1975 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146
SIM GIDEON STG U1 |  | GIDEON_GIDEONG1 | BASTROP | GAS | SOUTH | 1965 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130
SIM GIDEON STG U2 |  | GIDEON_GIDEONG2 | BASTROP | GAS | SOUTH | 1968 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135
SIM GIDEON STG U3 |  | GIDEON_GIDEONG3 | BASTROP | GAS | SOUTH | 1972 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340
SPENCER STG U4 |  | SPNCER_SPNCE_4 | DENTON | GAS | NORTH | 1966 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
SPENCER STG U5 |  | SPNCER_SPNCE_5 | DENTON | GAS | NORTH | 1973 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
STRYKER CREEK STG U1 |  | SCSES_UNIT1A | CHEROKEE | GAS | NORTH | 1958 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
STRYKER CREEK STG U2 |  | SCSES_UNIT2 | CHEROKEE | GAS | NORTH | 1965 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502
TRINIDAD STG U6 |  | TRSES_UNIT6 | HENDERSON | GAS | NORTH | 1965 | 226 | 226 | 226 | 226 | 226 | 226 | 226 | 226 | 226 | 226
V H BRAUNIG STG U1 |  | BRAUNIG_VHB1 | BEXAR | GAS | SOUTH | 1966 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
V H BRAUNIG STG U3 |  | BRAUNIG_VHB3 | BEXAR | GAS | SOUTH | 1970 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412
W A PARISH STG U1 |  | WAP_WAP_G1 | FT. BEND | GAS | HOUSTON | 1958 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
W A PARISH STG U2 |  | WAP_WAP_G2 | FT. BEND | GAS | HOUSTON | 1958 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
W A PARISH STG U3 |  | WAP_WAP_G3 | FT. BEND | GAS | HOUSTON | 1961 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258
W A PARISH STG U4 |  | WAP_WAP_G4 | FT. BEND | GAS | HOUSTON | 1968 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552
NOTREES BATTERY | 12INR0076 | NWF_NBS | WINKLER/ECTOR | STORAGE | WEST | 2012 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7
ACACIA SOLAR |  | ACACIA_UNIT_1 | PRESIDIO | SOLAR | WEST | 2012 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
BRACKETVILLE SOLAR - OCI ALAMO 4 | 14INR0024 | ECLIPSE_UNIT1 | KINNEY | SOLAR | SOUTH | 2014 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6
OCI ALAMO 1 SOLAR | 13INR0058 | OCI_ALM1_UNIT1 | BEXAR | SOLAR | SOUTH | 2013 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2
WEBBERVILLE SOLAR | 10INR0082 | WEBBER_S_WSP1 | TRAVIS | SOLAR | SOUTH | 2011 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
BLUE WING 1 |  | DG_BROOK_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6
BLUE WING 2 |  | DG_ELMEN_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3
SOMERSET 1 |  | DG_SOME1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6
SOMERSET 2 |  | DG_SOME2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
SUNEDISON RABEL ROAD |  | DG_VALL1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SUNEDISON VALLEY ROAD |  | DG_VALL2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
NACOGDOCHES POWER | 09INR0007 | NACPW_UNIT1 | NACOGDOCHES | BIOMASS | NORTH | 2012 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105
LUFKIN BIOMASS | 08INR0033 | LFBIO_UNIT1 | ANGELINA | BIOMASS | NORTH | 2012 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
ALVIN |  | AV_DG1 | GALVESTON | BIOMASS | HOUSTON | 2002 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7
AUSTIN LANDFILL GAS |  | DG_SPRIN_4UNITS | TRAVIS | BIOMASS | SOUTH | 2007 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4
COVEL GARDENS POWER STATION |  | DG_MEDIN_1UNIT | BEXAR | BIOMASS | SOUTH | 2005 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
DFW GAS RECOVERY |  | DG_BIO2_4UNITS | DENTON | BIOMASS | NORTH | 2009 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4
DG_BIOENERGY PARTNERS |  | DG_BIOE_2UNITS | DENTON | BIOMASS | NORTH | 1988 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2
FW REGION GEN FACILITY |  | DG_RDLML_1UNIT | TARRANT | BIOMASS | NORTH | 2011 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
HUMBLE |  | HB_DG1 | HARRIS | BIOMASS | HOUSTON | 2002 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
LIBERTY |  | LB_DG1 | HARRIS | BIOMASS | HOUSTON | 2002 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9
MCKINNEY LANDFILL |  | DG_MKNSW_2UNITS | COLLIN | BIOMASS | NORTH | 2011 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
MESQUITE CREEK ENERGY |  | DG_FREIH_2UNITS | COMAL | BIOMASS | SOUTH | 2011 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
SKYLINE LANDFILL GAS |  | DG_FERIS_4_UNITS | DALLAS | BIOMASS | NORTH | 2007 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4
TRINITY BAY |  | TRN_DG1 | CHAMBERS | BIOMASS | HOUSTON | 2002 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9
TRINITY OAKS LFG |  | DG_KLBRG_1UNIT | DALLAS | BIOMASS | NORTH | 2011 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
WALZEM ROAD |  | DG_WALZE_4UNITS | BEXAR | BIOMASS | SOUTH | 2002 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8
WESTSIDE |  | DG_WSTHL_3UNITS | PARKER | BIOMASS | NORTH | 2010 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8
Operational Capacity Total (Coal, Gas, Nuclear, Biomass, Solar) | [6 empty] | 66358 | 66358 | 66358 | 66358 | 65508 | 65508 | 65508 | 65508 | 65508 | 65508
Operational Resources (Hydro)
AMISTAD HYDRO 1 |  | AMISTAD_AMISTAG1 | VAL VERDE | HYDRO | SOUTH | 1983 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9
AMISTAD HYDRO 2 |  | AMISTAD_AMISTAG2 | VAL VERDE | HYDRO | SOUTH | 1983 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9
AUSTIN HYDRO 1 |  | AUSTPL_AUSTING1 | TRAVIS | HYDRO | SOUTH | 1940 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
AUSTIN HYDRO 2 |  | AUSTPL_AUSTING2 | TRAVIS | HYDRO | SOUTH | 1940 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
BUCHANAN HYDRO 1 |  | BUCHAN_BUCHANG1 | LLANO | HYDRO | SOUTH | 1938 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
BUCHANAN HYDRO 2 |  | BUCHAN_BUCHANG2 | LLANO | HYDRO | SOUTH | 1938 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
BUCHANAN HYDRO 3 |  | BUCHAN_BUCHANG3 | LLANO | HYDRO | SOUTH | 1950 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
DENISON DAM 1 |  | DNDAM_DENISOG1 | GRAYSON | HYDRO | NORTH | 1944 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
DENISON DAM 2 |  | DNDAM_DENISOG2 | GRAYSON | HYDRO | NORTH | 1948 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
FALCON HYDRO 1 |  | FALCON_FALCONG1 | STARR | HYDRO | SOUTH | 1954 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
FALCON HYDRO 2 |  | FALCON_FALCONG2 | STARR | HYDRO | SOUTH | 1954 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
FALCON HYDRO 3 |  | FALCON_FALCONG3 | STARR | HYDRO | SOUTH | 1954 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
GRANITE SHOALS HYDRO 1 |  | WIRTZ_WIRTZ_G1 | BURNET | HYDRO | SOUTH | 1951 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
GRANITE SHOALS HYDRO 2 |  | WIRTZ_WIRTZ_G2 | BURNET | HYDRO | SOUTH | 1951 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
INKS HYDRO 1 |  | INKSDA_INKS_G1 | LLANO | HYDRO | SOUTH | 1938 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
MARBLE FALLS HYDRO 1 |  | MARBFA_MARBFAG1 | BURNET | HYDRO | SOUTH | 1951 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
MARBLE FALLS HYDRO 2 |  | MARBFA_MARBFAG2 | BURNET | HYDRO | SOUTH | 1951 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
MARSHALL FORD HYDRO 1 |  | MARSFO_MARSFOG1 | TRAVIS | HYDRO | SOUTH | 1941 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
MARSHALL FORD HYDRO 2 |  | MARSFO_MARSFOG2 | TRAVIS | HYDRO | SOUTH | 1941 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
MARSHALL FORD HYDRO 3 |  | MARSFO_MARSFOG3 | TRAVIS | HYDRO | SOUTH | 1941 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
WHITNEY DAM HYDRO |  | WND_WHITNEY1 | BOSQUE | HYDRO | NORTH | 1953 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
WHITNEY DAM HYDRO 2 |  | WND_WHITNEY2 | BOSQUE | HYDRO | NORTH | 1953 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
CANYON |  | CANYHY_CANYHYG1 | COMAL | HYDRO | SOUTH | 1989 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
EAGLE PASS HYDRO |  | EAGLE_HY_EAGLE_HY1 | MAVERICK | HYDRO | SOUTH | 2005 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
LAKEWOOD TAP |  | DG_LKWDT_2UNITS | GONZALES | HYDRO | SOUTH | 1931 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8
LEWISVILLE |  | DG_LWSVL_1UNIT | DENTON | HYDRO | NORTH | 1991 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2
MCQUEENEY |  | DG_MCQUE_5UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7
SCHUMANSVILLE |  | DG_SCHUM_2UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6
Operational Capacity Total (Hydro) | [6 empty] | 540.7 | 540.7 | 540.7 | 540.7 | 540.7 | 540.7 | 540.7 | 540.7 | 540.7 | 540.7
Hydro Capacity Contribution (Top 20 Hours) |  | HYDRO_CAP_CONT |  |  |  |  | 63.6 | 63.6 | 63.6 | 63.6 | 63.6 | 63.6 | 63.6 | 63.6 | 63.6 | 63.6
Operational Capacity Total (Including Hydro) | [6 empty] | 66421.6 | 66421.6 | 66421.6 | 66421.6 | 65571.6 | 65571.6 | 65571.6 | 65571.6 | 65571.6 | 65571.6
Private-Use Network Capacity Contribution (Top 20 Hours) |  | PUN_CAP_CONT |  | GAS |  |  | 4318 | 4318 | 4318 | 4318 | 4318 | 4318 | 4318 | 4318 | 4318 | 4318
Wind Resources
ANACACHO WIND | 12INR0072 | ANACACHO_ANA | KINNEY | WIND | SOUTH | 2012 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8
BARTON CHAPEL WIND | 06INR0021 | BRTSW_BCW1 | JACK | WIND | WEST | 2007 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
BLUE SUMMIT WIND 5 | 12INR0075 | BLSUMMIT_BLSMT1_5 | WILBARGER | WIND | WEST | 2013 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
BLUE SUMMIT WIND 6 | 12INR0075 | BLSUMMIT_BLSMT1_6 | WILBARGER | WIND | WEST | 2013 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4
BOBCAT BLUFF WIND | 08INR0049 | BCATWIND_WIND_1 | ARCHER | WIND | NORTH | 2012 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
BUFFALO GAP WIND FARM 1 | 04INR0015 | BUFF_GAP_UNIT1 | TAYLOR | WIND | WEST | 2006 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6
BUFFALO GAP WIND FARM 2_1 | 06INR0037 | BUFF_GAP_UNIT2_1 | TAYLOR | WIND | WEST | 2007 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5
BUFFALO GAP WIND FARM 2_2 | 06INR0037 | BUFF_GAP_UNIT2_2 | TAYLOR | WIND | WEST | 2007 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117
BUFFALO GAP WIND FARM 3 | 07INR0030 | BUFF_GAP_UNIT3 | TAYLOR | WIND | WEST | 2008 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2
BULL CREEK WIND PLANT U1 | 07INR0037 | BULLCRK_WND1 | BORDEN | WIND | WEST | 2009 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88
BULL CREEK WIND PLANT U2 | 07INR0037 | BULLCRK_WND2 | BORDEN | WIND | WEST | 2009 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
CALLAHAN WIND | 04INR0013 | CALLAHAN_WND1 | CALLAHAN | WIND | WEST | 2004 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114
CAMP SPRINGS WIND 1 | 06INR0038 | CSEC_CSECG1 | SCURRY | WIND | WEST | 2007 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5
CAMP SPRINGS WIND 2 | 07INR0040 | CSEC_CSECG2 | SCURRY | WIND | WEST | 2007 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
CAPRICORN RIDGE WIND 1 | 07INR0018 | CAPRIDGE_CR1 | STERLING | WIND | WEST | 2007 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5
CAPRICORN RIDGE WIND 2 | 07INR0041 | CAPRIDGE_CR3 | STERLING | WIND | WEST | 2008 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186
CAPRICORN RIDGE WIND 3 | 07INR0041 | CAPRIDGE_CR2 | STERLING | WIND | WEST | 2007 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5
CAPRICORN RIDGE WIND 4 | 08INR0063 | CAPRIDG4_CR4 | COKE/STERLING | WIND | WEST | 2008 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5
CEDRO HILL WIND 1 | 09INR0082 | CEDROHIL_CHW1 | WEBB | WIND | SOUTH | 2010 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
CEDRO HILL WIND 2 | 09INR0083 | CEDROHIL_CHW2 | WEBB | WIND | SOUTH | 2010 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
CHAMPION WIND FARM | 07INR0045d | CHAMPION_UNIT1 | NOLAN AND MITCHELL | WIND | WEST | 2008 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5
DESERT SKY WIND FARM 1 |  | INDNENR_INDNENR | PECOS | WIND | WEST | 2002 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84
DESERT SKY WIND FARM 2 |  | INDNENR_INDNENR_2 | PECOS | WIND | WEST | 2002 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5
ELBOW CREEK WIND PROJECT | 08INR0053 | ELB_ELBCREEK | HOWARD | WIND | WEST | 2008 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7
FOREST CREEK WIND FARM | 05INR0019 | MCDLD_FCW1 | GLASSCOCK | WIND | WEST | 2007 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2
GOAT WIND | 07INR0028 | GOAT_GOATWIND | STERLING | WIND | WEST | 2008 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
GOAT WIND 2 | 07INR0028b | GOAT_GOATWIN2 | STERLING | WIND | WEST | 2010 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6
GOLDTHWAITE WIND 1 | 11INR0013 | GWEC_GWEC_G1 | MILLS | WIND | NORTH | 2014 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6
GREEN MOUNTAIN WIND (BRAZOS) U1 | 03INR0020 | BRAZ_WND_WND1 | SCURRY/BORDEN | WIND | WEST | 2003 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99
GREEN MOUNTAIN WIND (BRAZOS) U2 | 03INR0020 | BRAZ_WND_WND2 | SCURRY/BORDEN | WIND | WEST | 2003 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
HACKBERRY WIND FARM | 04INR0011e | HWF_HWFG1 | SHACKELFORD | WIND | WEST | 2008 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5
HORSE HOLLOW WIND 1 | 05INR0015 | H_HOLLOW_WND1 | TAYLOR | WIND | WEST | 2005 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 213
HORSE HOLLOW WIND 2 | 05INR0018 | HHOLLOW2_WIND1 | TAYLOR | WIND | WEST | 2006 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184
HORSE HOLLOW WIND 3 | 06INR0040 | HHOLLOW3_WND_1 | TAYLOR | WIND | WEST | 2006 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5
HORSE HOLLOW WIND 4 | 06INR0040 | HHOLLOW4_WND1 | TAYLOR | WIND | WEST | 2006 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115
INADALE WIND | 07INR0045b | INDL_INADALE1 | NOLAN | WIND | WEST | 2008 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6
INDIAN MESA WIND FARM | 00INR0022 | INDNNWP_INDNNWP | PECOS COUNTY | WIND | WEST | 2001 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5
KING MOUNTAIN NE | 00INR0025 | KING_NE_KINGNE | UPTON | WIND | WEST | 2001 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3
KING MOUNTAIN NW | 00INR0025 | KING_NW_KINGNW | UPTON | WIND | WEST | 2001 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3
KING MOUNTAIN SE | 00INR0025 | KING_SE_KINGSE | UPTON | WIND | WEST | 2001 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3
KING MOUNTAIN SW | 00INR0025 | KING_SW_KINGSW | UPTON | WIND | WEST | 2001 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3
LANGFORD WIND POWER | 10INR0026 | LGD_LANGFORD | TOM GREEN | WIND | WEST | 2009 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
LONE STAR WIND 1 (MESQUITE) | 04INR0011 | LNCRK_G83 | SHACKELFORD | WIND | WEST | 2006 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
LONE STAR WIND 2 (POST OAK) U1 | 04INR0011a | LNCRK2_G871 | SHACKELFORD | WIND | WEST | 2007 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
LONE STAR WIND 2 (POST OAK) U2 | 04INR0011a | LNCRK2_G872 | SHACKELFORD | WIND | WEST | 2007 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
LORAINE WINDPARK I | 09INR0047 | LONEWOLF_G1 | MITCHELL | WIND | WEST | 2009 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5
LORAINE WINDPARK II | 09INR0047 | LONEWOLF_G2 | MITCHELL | WIND | WEST | 2009 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51
LORAINE WINDPARK III | 09INR0047 | LONEWOLF_G3 | MITCHELL | WIND | WEST | 2011 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5
LORAINE WINDPARK IV | 09INR0047 | LONEWOLF_G4 | MITCHELL | WIND | WEST | 2011 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
MCADOO WIND FARM | 08INR0028 | MWEC_G1 | DICKENS | WIND | WEST | 2008 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
NOTREES WIND FARM 1 | 07INR0005 | NWF_NWF1 | WINKLER/ECTOR | WIND | WEST | 2009 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6
NOTREES WIND FARM 2 | 07INR0005 | NWF_NWF2 | WINKLER/ECTOR | WIND | WEST | 2009 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OCOTILLO WIND FARM | 04INR0017 | OWF_OWF | HOWARD | WIND | WEST | 2008 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8
PANHANDLE WIND 1 U1 | 14INR0030a_2 | PH1_UNIT1 | CARSON | WIND | PANHANDLE | 2014 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2
PANHANDLE WIND 1 U2 | 14INR0030a_2 | PH1_UNIT2 | CARSON | WIND | PANHANDLE | 2014 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2
PANHANDLE WIND 2 U1 | 14INR0030b | PH2_UNIT1 | CARSON | WIND | PANHANDLE | 2014 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7
PANHANDLE WIND 2 U2 | 14INR0030b | PH2_UNIT2 | CARSON | WIND | PANHANDLE | 2014 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92
PANTHER CREEK 1 | 07INR0022 | PC_NORTH_PANTHER1 | HOWARD | WIND | WEST | 2008 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5
PANTHER CREEK 2 | 08INR0037 | PC_SOUTH_PANTHER2 | HOWARD | WIND | WEST | 2008 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5
PANTHER CREEK 3 | 11INR0015 | PC_SOUTH_PANTHER3 | HOWARD | WIND | WEST | 2009 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5
PECOS WIND (WOODWARD 1) | 01INR0035 | WOODWRD1_WOODWRD1 | PECOS | WIND | WEST | 2001 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5
PECOS WIND (WOODWARD 2) | 01INR0035 | WOODWRD2_WOODWRD2 | PECOS | WIND | WEST | 2001 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2
PYRON WIND FARM | 07INR0045a | PYR_PYRON1 | SCURRY AND FISHER | WIND | WEST | 2008 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249
RED CANYON WIND | 05INR0017 | RDCANYON_RDCNY1 | BORDEN | WIND | WEST | 2006 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84
ROSCOE WIND FARM | 07INR0045e | TKWSW1_ROSCOE | NOLAN | WIND | WEST | 2008 | 209 | 209 | 209 | 209 | 209 | 209 | 209 | 209 | 209 | 209
SAND BLUFF WIND FARM | 05INR0019 | MCDLD_SBW1 | GLASSCOCK | WIND | WEST | 2008 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
SENATE WIND PROJECT | 08INR0011 | SENATEWD_UNIT1 | JACK | WIND | WEST | 2012 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
SHERBINO I WIND | 06INR0012a | KEO_KEO_SM1 | PECOS | WIND | WEST | 2008 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
SHERBINO 2 WIND | 06INR0012b | KEO_SHRBINO2 | PECOS | WIND | WEST | 2011 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
SILVER STAR WIND | 03INR0034 | FLTCK_SSI | EASTLAND | WIND | NORTH | 2008 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SNYDER WIND FARM | 04INR0020 | ENAS_ENA1 | SCURRY | WIND | WEST | 2007 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63
SOUTH TRENT WIND FARM | 07INR0029 | STWF_T1 | NOLAN & TAYLOR | WIND | WEST | 2008 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2
SPINNING SPUR WIND TWO | 13INR0048 | SSPURTWO_WIND_1 | OLDHAM | WIND | PANHANDLE | 2014 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161
STANTON WIND ENERGY | 07INR0010 | SWEC_G1 | MARTIN | WIND | WEST | 2008 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
SWEETWATER WIND 1 | 01INR0036 | SWEETWND_WND1 | NOLAN | WIND | WEST | 2003 | 36.6 | 36.6 | 36.6 | 36.6 | 36.6 | 36.6 | 36.6 | 36.6 | 36.6 | 36.6
SWEETWATER WIND 2A | 01INR0036 | SWEETWN2_WND24 | NOLAN | WIND | WEST | 2006 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9
SWEETWATER WIND 2B | 01INR0036 | SWEETWN2_WND2 | NOLAN | WIND | WEST | 2004 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5
SWEETWATER WIND 3A | 01INR0036 | SWEETWN3_WND3A | NOLAN | WIND | WEST | 2011 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5
SWEETWATER WIND 3B | 01INR0036 | SWEETWN3_WND3B | NOLAN | WIND | WEST | 2011 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5
SWEETWATER WIND 4-5 | 07INR0023 | SWEETWN4_WND5 | NOLAN | WIND | WEST | 2007 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2
SWEETWATER WIND 4-4B | 07INR0023 | SWEETWN4_WND4B | NOLAN | WIND | WEST | 2007 | 103.7 | 103.7 | 103.7 | 103.7 | 103.7 | 103.7 | 103.7 | 103.7 | 103.7 | 103.7
SWEETWATER WIND 4-4A | 07INR0023 | SWEETWN4_WND4A | NOLAN | WIND | WEST | 2007 | 117.8 | 117.8 | 117.8 | 117.8 | 117.8 | 117.8 | 117.8 | 117.8 | 117.8 | 117.8
TEXAS BIG SPRING WIND a |  | SGMTN_SIGNALMT | HOWARD | WIND | WEST | 1999 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7
TEXAS BIG SPRING WIND b |  | SGMTN_SIGNALM2 | HOWARD | WIND | WEST | 1999 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
TRENT WIND FARM | 01INR0038 | TRENT_TRENT | NOLAN | WIND | WEST | 2001 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
TRINITY HILLS WIND 1 | 08INR0062 | TRINITY_TH1_BUS1 | YOUNG | WIND | NORTH | 2012 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5
TRINITY HILLS WIND 2 | 08INR0062 | TRINITY_TH1_BUS2 | YOUNG | WIND | NORTH | 2012 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5
TURKEY TRACK WIND ENERGY CENTER | 07INR0011 | TTWEC_G1 | NOLAN | WIND | WEST | 2008 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5
WEST TEXAS WIND ENERGY |  | SW_MESA_SW_MESA | UPTON/CROCKETT COUNTIES | WIND | WEST | 1999 | 74.2 | 74.2 | 74.2 | 74.2 | 74.2 | 74.2 | 74.2 | 74.2 | 74.2 | 74.2
WHIRLWIND ENERGY | 07INR0003 | WEC_WECG1 | FLOYD | WIND | NORTH | 2007 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
WHITETAIL WIND ENERGY PROJECT | 11INR0091 | EXGNWTL_WIND_1 | WEBB AND DUVAL | WIND | SOUTH | 2012 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
WKN MOZART WIND | 09INR0061 | MOZART_WIND_1 | KENT & STONEWALL COUNTY | WIND | WEST | 2012 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
WOLF RIDGE WIND | 07INR0034 | WHTTAIL_WR1 | COOKE | WIND | NORTH | 2008 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5
TSTC WEST TEXAS WIND |  | DG_ROSC2_1UNIT | NOLAN | WIND | WEST | 2008 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Wind Capacity Total (Non-Coastal Counties) | [6 empty] | 10023 | 10023 | 10023 | 10023 | 10023 | 10023 | 10023 | 10023 | 10023 | 10023
GULF WIND I | 05INR0015a | TGW_T1 | KENEDY | WIND-C | SOUTH | 2010 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6
GULF WIND II | 05INR0015a | TGW_T2 | KENEDY | WIND-C | SOUTH | 2010 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6
LOS VIENTOS WIND I | 11INR0033 | LV1_LV1A | WILLACY/CAMERON | WIND-C | SOUTH | 2013 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1
LOS VIENTOS WIND II | 11INR0033 | LV1_LV1B | WILLACY/CAMERON | WIND-C | SOUTH | 2013 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6
MAGIC VALLEY WIND (REDFISH) 1A | 10INR0060 | REDFISH_MV1A | WILLACY | WIND-C | SOUTH | 2012 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8
MAGIC VALLEY WIND (REDFISH) 1B | 10INR0060 | REDFISH_MV1B | WILLACY | WIND-C | SOUTH | 2012 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5
PAPALOTE CREEK WIND FARM | 08INR0012a | PAP1_PAP1 | SAN PATRICIO | WIND-C | SOUTH | 2009 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9
PAPALOTE CREEK WIND FARM II | 08INR0012b | COTTON_PAP2 | SAN PATRICIO | WIND-C | SOUTH | 2010 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1
PENASCAL WIND 1 | 06INR0022a | PENA_UNIT1 | KENEDY | WIND-C | SOUTH | 2009 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8
PENASCAL WIND 2 | 06INR0022b | PENA_UNIT2 | KENEDY | WIND-C | SOUTH | 2009 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6
PENASCAL WIND 3 | 06INR0022b | PENA3_UNIT3 | KENEDY | WIND-C | SOUTH | 2011 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8
HARBOR WIND |  | DG_NUECE_6UNITS | NUECES | WIND-C | SOUTH | 2012 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
Wind Capacity Total (Coastal Counties) | [6 empty] | 1680.4 | 1680.4 | 1680.4 | 1680.4 | 1680.4 | 1680.4 | 1680.4 | 1680.4 | 1680.4 | 1680.4
Wind Capacity Total Total | [6 empty] | 11703.4 | 11703.4 | 11703.4 | 11703.4 | 11703.4 | 11703.4 | 11703.4 | 11703.4 | 11703.4 | 11703.4
Reliability Must-Run (RMR) Capacity |  | RMR_CAP_CONT |  | GAS |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DC-Tie Resources
EAGLE PASS TIE |  | DC_S | MAVERICK |  | SOUTH |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
EAST TIE |  | DC_E | FANNIN |  | NORTH |  | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
LAREDO VFT TIE |  | DC_L | WEBB |  | SOUTH |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
NORTH TIE |  | DC_N | WILBARGER |  | WEST |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
SHARYLAND RAILROAD TIE |  | DC_R | HIDALGO |  | SOUTH |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
SHARYLAND RAILROAD TIE (FUTURE) |  | DC_R2 | HIDALGO |  | SOUTH |  | 20 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
DC-Ties Total | [6 empty] | 1120 | 1250 | 1250 | 1250 | 1250 | 1250 | 1250 | 1250 | 1250 | 1250
DC-Ties Capacity Contribution (Top 20 Hours) |  | DCTIE_CAP_CONT |  | OTHER |  |  | 494.8 | 494.8 | 494.8 | 494.8 | 494.8 | 494.8 | 494.8 | 494.8 | 494.8 | 494.8
Switchable Resources
KIAMICHI ENERGY FACILITY 1CT101 | 03INR0012 | KMCHI_1CT101 | PITTSBURG | GAS | NORTH | 2003 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
KIAMICHI ENERGY FACILITY 1CT201 | 03INR0012 | KMCHI_1CT201 | PITTSBURG | GAS | NORTH | 2003 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
KIAMICHI ENERGY FACILITY 1ST | 03INR0012 | KMCHI_1ST | PITTSBURG | GAS | NORTH | 2003 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307
KIAMICHI ENERGY FACILITY 2CT101 | 03INR0012 | KMCHI_2CT101 | PITTSBURG | GAS | NORTH | 2003 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
KIAMICHI ENERGY FACILITY 2CT201 | 03INR0012 | KMCHI_2CT201 | PITTSBURG | GAS | NORTH | 2003 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
KIAMICHI ENERGY FACILITY 2ST | 03INR0012 | KMCHI_2ST | PITTSBURG | GAS | NORTH | 2003 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307
TENASKA-FRONTIER CTG 1 | 00PSR4 | FTR_FTR_G1 | GRIMES | GAS | HOUSTON | 2000 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
TENASKA-FRONTIER CTG 2 | 00PSR4 | FTR_FTR_G2 | GRIMES | GAS | HOUSTON | 2000 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
TENASKA-FRONTIER CTG 3 | 00PSR4 | FTR_FTR_G3 | GRIMES | GAS | HOUSTON | 2000 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
TENASKA-FRONTIER STG 4 | 00PSR4 | FTR_FTR_G4 | GRIMES | GAS | HOUSTON | 2000 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400
TENASKA-GATEWAY CTG 1 | 01INR0019 | TGCCS_CT1 | RUSK | GAS | NORTH | 2001 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162
TENASKA-GATEWAY CTG 2 | 01INR0019 | TGCCS_CT2 | RUSK | GAS | NORTH | 2001 | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 179
TENASKA-GATEWAY CTG 3 | 01INR0019 | TGCCS_CT3 | RUSK | GAS | NORTH | 2001 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
TENASKA-GATEWAY STG 4 | 01INR0019 | TGCCS_UNIT4 | RUSK | GAS | NORTH | 2001 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389
FRONTERA GENERATION CTG 1 |  | FRONTERA_FRONTEG1 | HIDALGO | GAS | SOUTH | 1999 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170
FRONTERA GENERATION CTG 2 |  | FRONTERA_FRONTEG2 | HIDALGO | GAS | SOUTH | 1999 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170
FRONTERA GENERATION STG |  | FRONTERA_FRONTEG3 | HIDALGO | GAS | SOUTH | 2000 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184
Switchable Capacity Total | [6 empty] | 3702 | 3702 | 3702 | 3702 | 3702 | 3702 | 3702 | 3702 | 3702 | 3702
Switchable Capacity Unavailable to ERCOT |  | SWITCH_UNAVAIL |  | GAS |  |  | -470 | -824 | -824 | -824 | -824 | -524 | -524 | -524 | -524 | -524
Available Mothball Capacity based on Owner's Return Probability |  | MOTH_AVAIL |  | COAL |  |  | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58
Planned Resources with Executed SGIA, Air Permit, GHG Permit and Water Rights
TEXAS CLEAN ENERGY PROJECT | 13INR0023 |  | ECTOR | COAL | WEST | 2019 | 0 | 0 | 0 | 0 | 240 | 240 | 240 | 240 | 240 | 240
PANDA TEMPLE II CTG1 | 10INR0020b | PANDA_T2_TMPL2CT1 | BELL | GAS | NORTH | 2015 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5
PANDA TEMPLE II CTG2 | 10INR0020b | PANDA_T2_TMPL2CT2 | BELL | GAS | NORTH | 2015 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5
PANDA TEMPLE II STG | 10INR0020b | PANDA_T2_TMPL2ST1 | BELL | GAS | NORTH | 2015 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6
FGE TEXAS I | 16INR0010 |  | MITCHELL | GAS | WEST | 2017 | 0 | 0 | 799 | 799 | 799 | 799 | 799 | 799 | 799 | 799
ANTELOPE STATION IC & CTG | 13INR0028 |  | HALE | GAS | PANHANDLE | 2016 | 0 | 359 | 359 | 359 | 359 | 359 | 359 | 359 | 359 | 359
GOLDSMITH PEAKERS | 14INR0039 |  | ECTOR | GAS | WEST | 2015 | 340.8 | 340.8 | 340.8 | 340.8 | 340.8 | 340.8 | 340.8 | 340.8 | 340.8 | 340.8
LA PALOMA ENERGY CENTER | 16INR0004 |  | CAMERON | GAS | SOUTH | 2016 | 0 | 0 | 730 | 730 | 730 | 730 | 730 | 730 | 730 | 730
PHR PEAKERS | 14INR0038 |  | GALVESTON | GAS | HOUSTON | 2015 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390
SKY GLOBAL POWER ONE | 16INR0057 |  | COLORADO | GAS | SOUTH | 2016 | 0 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51
WHITE CAMP SOLAR (WCSOLAR1_100PV) | 11INR0094 |  | KENT | SOLAR | WEST | 2015 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
PECOS BARILLA SOLAR (HOVEY_UNIT1) | 12INR0059 |  | PECOS | SOLAR | WEST | 2014 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
OCI ALAMO 5 | 15INR0036 |  | UVALDE | SOLAR | SOUTH | 2015 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105
Planned Capacity Total (Not Wind) | [6 empty] | 1736.4 | 2146.4 | 3675.4 | 3675.4 | 3915.4 | 3915.4 | 3915.4 | 3915.4 | 3915.4 | 3915.4
Planned Wind Resources with Executed SGIA
STEPHENS RANCH WIND 1 (SRWE1_UNIT1) | 12INR0034a |  | BORDEN | WIND | WEST | 2014 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211
STEPHENS RANCH WIND 2 | 12INR0034b |  | BORDEN | WIND | WEST | 2015 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
MARIAH WIND a | 13INR0010a |  | PARMER | WIND | PANHANDLE | 2015 | 0 | 232 | 232 | 232 | 232 | 232 | 232 | 232 | 232 | 232
MIAMI WIND 1 (MIAM1_G1-2) | 14INR0012a |  | GRAY | WIND | PANHANDLE | 2014 | 289 | 289 | 289 | 289 | 289 | 289 | 289 | 289 | 289 | 289
MARIAH WIND b | 13INR0010b |  | PARMER | WIND | PANHANDLE | 2015 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
MIDWAY FARMS WIND | 11INR0054 |  | SAN PATRICIO | WIND-C | SOUTH | 2016 | 0 | 0 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161
LONGHORN ENERGY CENTER (LHORN_N_UNIT1-2) | 14INR0023 |  | BRISCOE | WIND | WEST | 2015 | 0 | 361 | 361 | 361 | 361 | 361 | 361 | 361 | 361 | 361
GRANDVIEW (CONWAY) 1 (GRANDVW1_GV1A-B) | 13INR0005a |  | CARSON | WIND | PANHANDLE | 2014 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211
GRANDVIEW (CONWAY) 2 | 13INR0005b |  | CARSON | WIND | PANHANDLE | 2015 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389
SOUTH CLAY WINDFARM | 11INR0079a |  | CLAY | WIND | WEST | 2015 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
BAFFIN (PENASCAL WIND FARM 3) (BAFFIN_UNIT1-2) | 06INR0022c |  | KENEDY | WIND-C | SOUTH | 2014 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202
MARIAH WIND c | 13INR0010c |  | PARMER | WIND | PANHANDLE | 2016 | 0 | 0 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168
MESQUITE CREEK WIND (MESQCRK_WND1-2) | 09INR0051 |  | BORDEN | WIND | WEST | 2015 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211
GUNSIGHT MOUNTAIN | 08INR0018 |  | HOWARD | WIND | WEST | 2015 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
BRISCOE WIND FARM | 14INR0072 |  | BRISCOE | WIND | WEST | 2015 | 0 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
CAMERON COUNTY WIND | 11INR0057 |  | CAMERON | WIND-C | SOUTH | 2015 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
COMANCHE RUN WIND | 12INR0029 |  | SWISHER | WIND | PANHANDLE | 2016 | 0 | 0 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
CPV RATTLESNAKE DEN PH 1 | 13INR0020a |  | GLASSCOCK | WIND | WEST | 2015 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211
CPV RATTLESNAKE DEN PH 2 | 13INR0020b |  | GLASSCOCK | WIND | WEST | 2016 | 0 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158
GREEN PASTURES WIND (GPASTURE_WIND_I & II) | 12INR0070 |  | KNOX | WIND | WEST | 2015 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
HEREFORD WIND (HRFDWIND_WIND_G & V) | 13INR0059a |  | CASTRO | WIND | PANHANDLE | 2014 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
JUMBO ROAD WIND (HRFDWIND_JRDWIND1-2) | 13INR0059b |  | CASTRO | WIND | PANHANDLE | 2015 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
KEECHI WIND 138 KV JOPLIN (KEECHI_U1) | 14INR0049_2 |  | JACK | WIND | NORTH | 2014 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102
LOGANS GAP WIND I | 13INR0050 |  | COMANCHE | WIND | NORTH | 2015 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
LOS VIENTOS III (LV3_UNIT_1) | 13INR0052 |  | STARR | WIND | SOUTH | 2015 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
MIAMI WIND 1b | 14INR0012b |  | GRAY | WIND | PANHANDLE | 2015 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111
PAMPA WIND PROJECT | 12INR0018 |  | GRAY | WIND | PANHANDLE | 2017 | 0 | 0 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
PATRIOT (PETRONILLA) WIND | 11INR0062 |  | NUECES | WIND-C | SOUTH | 2015 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
ROUTE66 WIND | 14INR0032a |  | RANDALL | WIND | PANHANDLE | 2015 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
SENDERO WIND ENERGY PROJECT | 12INR0068 |  | JIM HOGG | WIND | SOUTH | 2015 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
SOUTH PLAINS WIND I | 14INR0025a |  | FLOYD | WIND | WEST | 2015 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
SOUTH PLAINS WIND II | 14INR0025b |  | FLOYD | WIND | WEST | 2015 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
SPINNING SPUR WIND THREE | 14INR0053 |  | OLDHAM | WIND | PANHANDLE | 2015 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194
WINDTHORST 2 (WNDTHST2_UNIT1) | 13INR0057 |  | ARCHER | WIND | WEST | 2014 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
WAKE WIND ENERGY | 14INR0047 |  | DICKENS | WIND | WEST | 2015 | 299 | 299 | 299 | 299 | 299 | 299 | 299 | 299 | 299 | 299
CAPROCK WIND | 10INR0009 |  | CASTRO | WIND | PANHANDLE | 2015 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
JAVELINA WIND ENERGY | 13INR0055 |  | ZAPATA | WIND | SOUTH | 2015 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250
LOS VIENTOS IV | 15INR0037 |  | STARR | WIND | SOUTH | 2015 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
LOS VIENTOS V | 15INR0021 |  | STARR | WIND | SOUTH | 2015 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
PALO DURO WIND | 15INR0050 |  | DEAF SMITH | WIND | PANHANDLE | 2015 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203
PANHANDLE WIND 3 | 14INR0030c |  | CARSON | WIND | PANHANDLE | 2015 | 0 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248
PULLMAN ROAD WIND | 15INR0079 |  | RANDALL | WIND | PANHANDLE | 2015 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
SALT FORK WIND | 14INR0062 |  | GRAY | WIND | PANHANDLE | 2015 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
SCANDIA WIND d | 13INR0010d |  | PARMER | WIND | PANHANDLE | 2015 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
SCANDIA WIND e | 13INR0010e |  | PARMER | WIND | PANHANDLE | 2015 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
SCANDIA WIND f | 13INR0010f |  | PARMER | WIND | PANHANDLE | 2016 | 0 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
Planned Wind Capacity Total | [6 empty] | 6554 | 8503 | 10032 | 10032 | 10032 | 10032 | 10032 | 10032 | 10032 | 10032
Planned Wind Capacity Sub-total (Non-Coastal Counties) | [6 empty] | 6009 | 7958 | 9326 | 9326 | 9326 | 9326 | 9326 | 9326 | 9326 | 9326
Planned Wind Capacity Sub-total (by Coastal County)
|  | CAMERON_NEW_WIND | CAMERON | WIND | SOUTH |  | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
|  | WILLACY_NEW_WIND | WILLACY | WIND | SOUTH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | KENEDY_NEW_WIND | KENEDY | WIND | SOUTH |  | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202
|  | KLEBERG_NEW_WIND | KLEBERG | WIND | SOUTH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | NUECES_NEW_WIND | NUECES | WIND | SOUTH |  | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
|  | SAN_PATRICIO_NEW_WIND | SAN PATRICIO | WIND | SOUTH |  | 0 | 0 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161
|  | REFUGIO_NEW_WIND | REFUGIO | WIND | SOUTH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | ARANSAS_NEW_WIND | ARANSAS | WIND | SOUTH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | CALHOUN_NEW_WIND | CALHOUN | WIND | SOUTH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | MATAGORDA_NEW_WIND | MATAGORDA | WIND | SOUTH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | BRAZORIA_NEW_WIND | BRAZORIA | WIND | HOUSTON |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Planned Wind Capacity Sub-total (All Coastal Counties) | [6 empty] | 545 | 545 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706
Mothballed Capacity
GREENS BAYOU CTG 82 |  | GBY_GBYGT82 | HARRIS | GAS | HOUSTON | 1976 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58
NORTH TEXAS CTG 1 |  | NTX_NTX_1 | PARKER | GAS | NORTH | 1958 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
NORTH TEXAS CTG 2 |  | NTX_NTX_2 | PARKER | GAS | NORTH | 1958 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
NORTH TEXAS CTG 3 |  | NTX_NTX_3 | PARKER | GAS | NORTH | 1963 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
PERMIAN BASIN SES U6 |  | PBSES_UNIT6 | WARD | GAS | WEST | 1973 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530
SILAS RAY CTG 5 |  | SILASRAY_SILAS_5 | CAMERON | GAS | SOUTH | 1953 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
VALLEY SES U1 |  | VLSES_UNIT1 | FANNIN | GAS | NORTH | 1962 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174
VALLEY SES U2 |  | VLSES_UNIT2 | FANNIN | GAS | NORTH | 1967 | 520 | 520 | 520 | 520 | 520 | 520 | 520 | 520 | 520 | 520
VALLEY SES U3 |  | VLSES_UNIT3 | FANNIN | GAS | NORTH | 1971 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375
J T DEELY U1 (MOTHBALLED) |  | CALAVERS_JTD1_M | BEXAR | COAL | SOUTH | 2018 | 0 | 0 | 0 | 0 | 430 | 430 | 430 | 430 | 430 | 430
J T DEELY U2 (MOTHBALLED) |  | CALAVERS_JTD2_M | BEXAR | COAL | SOUTH | 2018 | 0 | 0 | 0 | 0 | 420 | 420 | 420 | 420 | 420 | 420
S R BERTRON CTG 2 |  | SRB_SRBGT_2 | HARRIS | GAS | HOUSTON | 1967 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
S R BERTRON U1 |  | SRB_SRB_G1 | HARRIS | GAS | HOUSTON | 1958 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118
S R BERTRON U2 |  | SRB_SRB_G2 | HARRIS | GAS | HOUSTON | 1956 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174
S R BERTRON U3 |  | SRB_SRB_G3 | HARRIS | GAS | HOUSTON | 1959 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211
S R BERTRON U4 |  | SRB_SRB_G4 | HARRIS | GAS | HOUSTON | 1960 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211
V H BRAUNIG STG U2 |  | BRAUNIG_VHB2 | BEXAR | GAS | SOUTH | 1968 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230
Total Mothballed Capacity | [6 empty] | 2699 | 2699 | 2699 | 2699 | 3549 | 3549 | 3549 | 3549 | 3549 | 3549
Seasonal Mothballed Capacity
MARTIN LAKE U3 |  | MLSES_UNIT3 | RUSK | COAL | NORTH | 1979 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820
MONTICELLO U1 |  | MNSES_UNIT1 | TITUS | COAL | NORTH | 1974 | 580 | 580 | 580 | 580 | 580 | 580 | 580 | 580 | 580 | 580
MONTICELLO U2 |  | MNSES_UNIT2 | TITUS | COAL | NORTH | 1975 | 580 | 580 | 580 | 580 | 580 | 580 | 580 | 580 | 580 | 580
Total Seasonal Mothballed Capacity | [6 empty] | 1980 | 1980 | 1980 | 1980 | 1980 | 1980 | 1980 | 1980 | 1980 | 1980
Retiring Capacity Unavailable to ERCOT (since May 2014)
APPLIED ENERGY |  | APD_APD_G1 | HARRIS | COAL | HOUSTON | 1986 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140
ATKINS CTG 3 |  | ATKINS_ATKINSG3 | BRAZOS | GAS | NORTH | 1954 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
ATKINS CTG 4 |  | ATKINS_ATKINSG4 | BRAZOS | GAS | NORTH | 1958 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
ATKINS CTG 5 |  | ATKINS_ATKINSG5 | BRAZOS | GAS | NORTH | 1965 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
ATKINS CTG 6 |  | ATKINS_ATKINSG6 | BRAZOS | GAS | NORTH | 1969 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
DELAWARE MOUNTAIN WIND FARM | 99INR0004 | KUNITZ_WIND_NWP | CULBERSON COUNTY | WIND | WEST | 1999 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5
KUNITZ WIND - WINDPOWER PARTNERS 1994 |  | KUNITZ_WIND_LGE | CULBERSON COUNTY | WIND | WEST | 1995 | 39.8 | 39.8 | 39.8 | 39.8 | 39.8 | 39.8 | 39.8 | 39.8 | 39.8 | 39.8
Total Retiring Capacity Unavailable to ERCOT | [6 empty] | 317.3 | 317.3 | 317.3 | 317.3 | 317.3 | 317.3 | 317.3 | 317.3 | 317.3 | 317.3
Excluded Resources, per notification from developer
COBISA-GREENVILLE | 06INR0006 |  | HUNT | GAS | NORTH | 2017 | 0 | 0 | 2023 | 2023 | 2023 | 2023 | 2023 | 2023 | 2023 | 2023
Excluded Resources, pending water rights
PONDERA KING POWER PROJECT | 10INR0022 |  | HARRIS | GAS | HOUSTON | 2017 | 0 | 0 | 925 | 925 | 925 | 925 | 925 | 925 | 925 | 925

## WinterFuelTypes
Winter Fuel Types - ERCOT
Fuel type is based on the primary fuel. Capacity contribution of the wind resources is included at 19% for Non-Coastal and 36% for Coastal counties. Private Use Network, Hydro and Non-Synchronous Tie resources are included based on the three-year average historical capability for each Winter Season 20 peak load hours. Non-Synchronous Tie resources are categorized as Other. Mothballed resource capacity is excluded except for Available Mothball Capacity based on Owner's Return Probability.
In MW
Fuel_Type | Capacity_Pct | 2015/2016 | 2016/2017 | 2017/2018 | 2018/2019 | 2019/2020 | 2020/2021 | 2021/2022 | 2022/2023 | 2023/2024 | 2024/2025
Biomass | 100% | 235.3 | 235.3 | 235.3 | 235.3 | 235.3 | 235.3 | 235.3 | 235.3 | 235.3 | 235.3
Coal | 100% | 17425 | 17425 | 17425 | 17425 | 16815 | 16815 | 16815 | 16815 | 16815 | 16815
Gas | 100% | 52450.6 | 52506.6 | 54035.6 | 54035.6 | 54035.6 | 54335.6 | 54335.6 | 54335.6 | 54335.6 | 54335.6
Nuclear | 100% | 5164 | 5164 | 5164 | 5164 | 5164 | 5164 | 5164 | 5164 | 5164 | 5164
Other | 100% | 494.8 | 494.8 | 494.8 | 494.8 | 494.8 | 494.8 | 494.8 | 494.8 | 494.8 | 494.8
Hydro | 11.8% | 63.8026 | 63.8026 | 63.8026 | 63.8026 | 63.8026 | 63.8026 | 63.8026 | 63.8026 | 63.8026 | 63.8026
Wind | 19% | 3046.08 | 3416.39 | 3676.31 | 3676.31 | 3676.31 | 3676.31 | 3676.31 | 3676.31 | 3676.31 | 3676.31
Wind-C | 36% | 801.144 | 801.144 | 859.104 | 859.104 | 859.104 | 859.104 | 859.104 | 859.104 | 859.104 | 859.104
Solar | 100% | 393.8 | 393.8 | 393.8 | 393.8 | 393.8 | 393.8 | 393.8 | 393.8 | 393.8 | 393.8
Storage | 100% | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7
Total |  | 80108.2266 | 80534.5366 | 82381.4166 | 82381.4166 | 81771.4166 | 82071.4166 | 82071.4166 | 82071.4166 | 82071.4166 | 82071.4166
In Percentages
Fuel_Type |  | 2015/2016 | 2016/2017 | 2017/2018 | 2018/2019 | 2019/2020 | 2020/2021 | 2021/2022 | 2022/2023 | 2023/2024 | 2024/2025
Biomass |  | 0.2937% | 0.2922% | 0.2856% | 0.2856% | 0.2878% | 0.2867% | 0.2867% | 0.2867% | 0.2867% | 0.2867%
Coal |  | 21.75% | 21.64% | 21.15% | 21.15% | 20.56% | 20.49% | 20.49% | 20.49% | 20.49% | 20.49%
Gas |  | 65.47% | 65.2% | 65.59% | 65.59% | 66.08% | 66.21% | 66.21% | 66.21% | 66.21% | 66.21%
Nuclear |  | 6.446% | 6.412% | 6.268% | 6.268% | 6.315% | 6.292% | 6.292% | 6.292% | 6.292% | 6.292%
Other |  | 0.6177% | 0.6144% | 0.6006% | 0.6006% | 0.6051% | 0.6029% | 0.6029% | 0.6029% | 0.6029% | 0.6029%
Hydro |  | 0.07965% | 0.07922% | 0.07745% | 0.07745% | 0.07803% | 0.07774% | 0.07774% | 0.07774% | 0.07774% | 0.07774%
Wind |  | 3.802% | 4.242% | 4.463% | 4.463% | 4.496% | 4.479% | 4.479% | 4.479% | 4.479% | 4.479%
Wind-C |  | 1% | 0.9948% | 1.043% | 1.043% | 1.051% | 1.047% | 1.047% | 1.047% | 1.047% | 1.047%
Solar |  | 0.4916% | 0.489% | 0.478% | 0.478% | 0.4816% | 0.4798% | 0.4798% | 0.4798% | 0.4798% | 0.4798%
Storage |  | 0.04207% | 0.04185% | 0.04091% | 0.04091% | 0.04121% | 0.04106% | 0.04106% | 0.04106% | 0.04106% | 0.04106%
Total |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%