October 2014 ERCOT Monthly Operations Report

Reliability and Operations Subcommittee Meeting

December 4, 2014

Table of Contents

1.	Report Highlights	1

2.	Frequency Control	2

2.1.	Frequency Events	2

2.2.	Responsive Reserve Events	3

2.3.	Load Resource Events	3

3.	Reliability Unit Commitment	3

4.	Wind Generation as a Percent of Load	4

5.	Congestion Analysis	5

5.1.	Notable Constraints for October	5

5.2.	Generic Transmission Constraint Congestion	6

5.3.	Manual Overrides for October	7

5.4.	Congestion Costs for Calendar Year 2014	7

6.	System Events	8

6.1.	ERCOT Peak Load	8

6.2.	Load Shed Events	8

6.3.	Stability Events	8

6.4.	Notable PMU Events	8

6.5.	TRE/DOE Reportable Events	8

6.6.	New/Updated Constraint Management Plans	9

6.7.	New/Modified/Removed SPS	9

6.8.	New Procedures/Forms/Operating Bulletins	9

7.	Emergency Conditions	9

7.1.	OCNs	9

7.2.	Advisories	9

7.3.	Watches	9

7.4.	Emergency Notices	9

8.	Application Performance	10

8.1.	TSAT/VSAT Performance Issues	10

8.2.	Communication Issues	10

9.	Net-Forecast Bias Applied to NSRS Procurement for November 2014	10

10.	Appendix A: Real-Time Constraints	11

# Report Highlights

- The unofficial ERCOT peak for October was 58,421 MW.

- There were six frequency events in October. PMU data indicates the ERCOT system transitioned well in each case.

- There were six instances where Responsive Reserves were deployed. Five of them were the result of frequency events.

- There ten RUC Commitments in October for local congestion and voltage support.

- The level of SCED congestion increased slightly in October. This was primarily due to unseasonably warm temperatures during the first part of the month and ongoing outages.

- There was one system even event this month when ERCOT shed greater than 100 MW of firm load in the Rio Grande Valley following a forced outage. The event is briefly summarized in section 6 of this report and a full report from ERCOT will be forthcoming.

- ERCOT Applications performed well throughout the month. There were no issues in October.

# Frequency Control

## Frequency Events

The ERCOT Interconnection experienced six frequency events in October, five of which resulted from Resource trips. The average event duration was approximately 18 seconds.

When analyzing frequency events, ERCOT evaluates PMU data according to industry standards. Events with an oscillating frequency of less than 1 Hz are considered to be inter-area, while higher frequencies indicate local events. Industry standards specify that damping ratio for inter-area oscillations should be 3.0% or greater. All events listed below indicate the ERCOT system met these standards and transitioned well after each disturbance. Further details on the Resource trip events can be seen in the Performance Disturbance Compliance Working Group report.

A summary of the frequency events is provided below:

| Date and Time | Max/Min Frequency (Hz) | Duration of Event (seconds) | PMU Data |  | Comments |
| --- | --- | --- | --- | --- | --- |
|  |  |  | Oscillation Mode | Damping Ratio |  |
| 10/8/2014 15:51 | 59.863 | 29 | 0.647 Hz 0.673 Hz | 15.9% 12.2% | Plant trip with approximately 665 MW |
| 10/8/2014 16:53 | 60.127 | 8 | No significant oscillation modes captured |  | Firm load shed |
| 10/9/2014 13:29 | 59.827 | 24 | 0.627 Hz | 11.9% | Unit trip with approximately 754 MW |
| 10/13/2014 8:27 | 59.879 | 6 | 0.670 Hz | 8.21% | Plant trip with approximately 568 MW |
| 10/24/2014 21:55 | 59.88 | 7 | No significant oscillation modes captured |  | Plant trip with approximately 296 MW |
| 10/29/2014 12:06 | 59.865 | 36 | 0.640 Hz | 14.0% | Plant trip with approximately 582 MW |

(Note: the duration of the frequency events is defined to be the time at which the frequency was outside the range of 60±0.1 Hz)

## Responsive Reserve Events

There were six events where Responsive Reserve MWs were released to SCED in October.  The events highlighted in blue were related to frequency events reported in section 2.1 above.

| Date and Time Released to SCED | Date and Time Recalled | Duration of Event | Maximum MWs Released | Comments |
| --- | --- | --- | --- | --- |
| 10/8/14 15:51:48 | 10/8/14 15:57:16 | 0:05:28 | 599.21 |  |
| 10/9/14 13:29:32 | 10/9/14 13:34:32 | 0:05:00 | 826.46 |  |
| 10/12/14 16:00:24 | 10/12/14 16:03:12 | 0:02:48 | 360.54 | Unit trip with approximately 469 MW |
| 10/13/14 8:27:40 | 10/13/14 8:30:28 | 0:02:48 | 256.18 |  |
| 10/24/14 21:56:00 | 10/24/14 21:59:24 | 0:03:24 | 557.4 |  |
| 10/29/14 12:06:34 | 10/29/14 12:09:22 | 0:02:48 | 256.96 |  |

## Load Resource Events

There were no load resource deployment events in October.

# Reliability Unit Commitment

ERCOT reports on Reliability Unit Commitments (RUC) on a monthly basis. Commitments are reported grouped by operating day and weather zone. The total number of hours committed is the sum of the hours for all the units in the specified region. Additional information on RUC commitments can be found on the MIS secure site at Grid  Generation  Reliability Unit Commitment.

There were no DRUC commitments in October.

| HRUC Commitments |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Resource Location | # of Resources | Operating Day | # Hours Committed | Total MWhs | Reason for commitment |
| Southern | 1 | 10/1/2014 | 1 | 54 | Local Congestion |
| S. Central | 1 | 10/2/2014 | 1 | 48 | Capacity |
| Southern | 1 | 10/2/2014 | 2 | 81 | Local Congestion |
| Southern | 1 | 10/7/2014 | 1 | 38 | Local Congestion |
| Southern | 2 | 10/9/2014 | 5 | 239 | Valley Import |
| N. Central | 1 | 10/12/2014 | 1 | 584 | Voltage Support |
| N. Central | 1 | 10/13/2014 | 6 | 3,516 | Voltage Support |
| Southern | 1 | 10/22/2014 | 2 | 107 | Local Congestion |
| N. Central | 1 | 10/27/2014 | 6 | 3,565 | Voltage Support |

# Wind Generation as a Percent of Load

# Congestion Analysis

The number of congestion events experienced by the ERCOT system increased slightly in October due to unseasonably warm temperatures at the beginning of the month and ongoing outages. There were two days of activity on the Valley Import Generic Transmission Constraints (GTC) in October.

## Notable Constraints for October

Nodal protocol section 3.20 specifies that ERCOT shall identify transmission constraints that are active or binding three or more times within a calendar month. As part of this process, ERCOT reports congestion that meets this criterion to ROS. In addition ERCOT also highlights notable constraints that have an estimated congestion rent exceeding $1,000,000 for a calendar month. These constraints are detailed in the table below. Rows highlighted in blue indicate the congestion was affected by one or more outages. For a list of all constraints activated in SCED for the month of October, please see Appendix A at the end of this report.

| Contingency | Overload | # of Days Constraint Active | Estimated Congestion Rent | Transmission Project |
| --- | --- | --- | --- | --- |
| Apache Tnp - Caddo Sw Sta Tnp 138 kV | Heights Tnp HEIGHAT1 138/69 kV | 5 | $37,735,236 |  |
| La Palma - Rio Hondo 138 kV | Rio Hondo - East Rio Hondo 138 kV | 14 | $23,911,165 |  |
| La Palma - Rio Hondo 138 kV | Harlingen Switch - Oleander 138 kV | 11 | $21,711,468 |  |
| Moss Switch - Holt Switch 138 kV | Moss Switch - Westover 138 kV | 8 | $19,893,286 | 14TPIT0053 |
| Holt Switch - Bakke and Andrews North 138 kV | Holt Switch - Emma Tap 69 kV | 4 | $7,095,621 | 15TPIT0058, 14TPIT0118 |
| DCKT Flewellen - Obrien and Maso Road 138 kV | Hockley - Betka 138 kV | 3 | $4,056,607 | 3682A, 3682B, 3682C |
| DCKT West Levee Switch - 800/900 Network 138 kV | East Levee Switch - Reagan Street 138 kV (3410_A) | 2 | $3,397,892 | 2013-R6, 16TPIT0061 |
| Salty - Sandow Switch 138 kV | Gilleland - Pflugerville 138 kV | 2 | $3,314,000 | 16TPIT0062 |
| Palmhurst Sub - North Edinburg 138 kV | Duke - Aderhold Sub 138 kV | 1 | $2,544,830 |  |
| Barber Lake Swtich - Morgan Creek Ses 138 kV (14030) | Barber Lake Swtich - Morgan Creek Ses 138 kV (14035) | 1 | $1,998,063 | 15TPIT0087 |
| DCKT Randolph - Weiderstein and Fratt - Parkway Lcra 138 kV | Ball Park - Fern 138 kV | 2 | $1,759,588 |  |
| DCKT Victoria - Victoria Dupont Switch 138 kV | Lolita - Formosa 138 kV | 1 | $1,748,477 |  |
| Koch Up River - Gila 138 kV | Gila - Hiway 9 138 kV (GILA_HIWAY_2) | 5 | $1,497,970 |  |
| Poacks - City of College Station 138 kV Switch 138 kV | City of College Station 138 kV Switch - Cssc 138 kV | 1 | $1,376,473 |  |
| DCKT Navarro - Limestone 345 kV | Jewett - Big Brown Ses 345 kV (40_A) | 2 | $1,355,348 | 4298 |
| Willow Valley Switch MR1H 345/138 kV | Norwood Switch - Chancellor Row 138 kV (3416_A) | 1 | $1,308,551 | 2013-R44, 2013-R6, 16TPIT0061 |
| DCKT H O Clarke - Dunlavy and Heights 69 kV | Hyde Park - Dunlavy 69 kV | 1 | $1,202,176 | 14TPIT3389 |
| Winks Sub - No Trees Switch 138 kV | Holt Switch - Amoco Midland Farms Tap 138 kV | 1 | $1,098,662 | 15TPIT0092 |
| DCKT Chambers - King and Cedar Bayou - Jordan 345 kV | Langston - Brine 138 kV | 4 | $667,357 |  |
| DCKT Roanoke Switch - West Denton and Lewisville Switch - Krum West Switch 345 kV | Lewisville Switch - Jones Streen Tnp 138 kV | 4 | $566,278 | 4282 |
| DCKT Lon Hill - North Edinburg 345 kv and Orange Grove Switching Station 138 kV | Rio Hondo - Burns Sub 138 kV | 4 | $389,354 |  |
| DCKT South Channel - Pair and Shell 138 kV | Conial - Waburn 138 kV | 3 | $241,925 | 14TPIT0121 |
| DCKT Lon Hill - North Edinburg 345 kv and Orange Grove Switching Station 138 kV | Lon Hill - Smith 69 kV | 3 | $227,042 | 16TPIT0026 |
| Uvalde Aep - Odlaw Switchyard 138 kV | Hamilton Road - Maverick 138 kV | 3 | $118,209 | 16TPIT0024 |
| DCKT Dowlap - Morgans Point and Airpro - Shell 138 | Deer Park - Cardiff 138 kV | 5 | $87,825 |  |
| DCKT Ferguson - Granite Mountain and Wirtz - Starcke - Paleface 138 kV | Wirtz - Flat Rock Lcra 138 kV | 6 | $80,360 |  |
| Orange Grove Switching Station - Lon Hill 138 kV | Lon Hill - Smith 69 kV | 3 | $54,896 | 16TPIT0026 |
| Cottonwood Road Switch - Loftin 69 kV | Shannon - Post Oak Switch 69 kV | 7 | $51,229 | 15TPIT0011 |
| Laquinta - Lobo 138 kV | Bruni 138_69_1 138/69 kV | 3 | $44,069 |  |
| DCKT Singleton - Tomball 345 kV | Singleton - Zenith 345 kV (SNGZEN99) | 3 | $16,020 | 3937 |
| Aspermont Aep - Spur 138 kV | Wolfgang - Rotan 69 kV | 3 | $8,027 |  |
| Scurry Switch - Sun Switch 138 kV | Wolfgang - Rotan 69 kV | 3 | $1,303 |  |

## Generic Transmission Constraint Congestion

There were 2 days of activity on the Valley Import GTC in October. The West – North, North – Houston, and SOP110 GTCs were not activated during the month.

## Manual Overrides for October

| Date | # of Resources with an Override | Number of SCED Intervals | Reason | Type |
| --- | --- | --- | --- | --- |
| 10/8/2014 | 3 | 37 | Transmission Emergency Notice | LDL to Max |
| 10/17/2014 | 1 | 15 | Basecase | LDL Override |
| 10/20/2014 | 1 | 20 | Preposturing for planned outage | HDL Override |

## Congestion Costs for Calendar Year 2014

The following table represents the top twenty active constraints for the calendar year to date based on the estimated congestion rent attributed to the congestion. ERCOT updates this list on a monthly basis.

| Contingency | Binding Element | # of 5-min SCED Intervals | Estimated Congestion Rent | Transmission Project |
| --- | --- | --- | --- | --- |
| Lytton Springs LY_AT2 345/138 kV | Lytton Springs LY_AT1 345/138 kV | 1,997 | $55,956,002 |  |
| Skywest - Spraberry Switch 138 kV, Skywest - Salt Flat Road 138 kV, and Salt Mine - Barber Lake Switch 138 kV | Midland East - Pecan Grove 138 kV | 3,738 | $46,790,259 | 14TPIT0052 |
| Apache Tnp - Caddo Sw Sta Tnp 138 kV | Heights Tnp HEIGHAT1 138/69 kV | 1,521 | $36,991,758 |  |
| La Palma - Rio Hondo 138 kV, DCKT Rio Hondo - North Edinburg 345 kV and Harlingen Switch 138 kV | Harlingen Switch - Oleander 138 kV | 1,159 | $26,943,341 |  |
| Tejas Tnp - Greenbelt Tnp 138 kV | Heights Tnp HEIGHAT2 138/69 kV | 1,104 | $26,926,033 |  |
| Midland East Axfmr 1 (3) 345/138 kV, Moss Switch Axfmr 1 345/138 kV, and Midland East - Moss Switch - Odessa Ehv Switch 345 kV | Odessa North Sd3 138 kV | 5,310 | $23,944,433 | 2012-R3, 2012-R4 |
| La Palma - Rio Hondo 138 kV, Los Fresnos - Loma Alta Sub 138 kV | Rio Hondo - East Rio Hondo 138 kV | 1,613 | $23,683,772 |  |
| Moss Switch - Holt Switch 138 kV | Moss Switch - Westover 138 kV | 1,088 | $19,511,591 | 14TPIT0053 |
| DCKT Flewellen - Obrien and Maso Road 138 kV, DCKT Singleton - Zenith 345 kV | Hockley - Betka 138 kV | 773 | $15,850,200 | TPIT Project 3682A, 3682B |
| Orange Grove Switching Station - Lon Hill 138 kV, DCKT Lon Hill - North Edinburg 345 kv and Orange Grove Switching Station 138 kV, and Lon Hill 345_138_2 (3) 345/138 kV | Lon Hill - Smith 69 kV | 8,596 | $14,052,406 | 16TPIT0026, 2012-R18 |
| Basecase | Valley Import | 576 | $11,853,636 |  |
| DCKT Jewett - Singleton 345 kV | Twin Oak Switch - Gibbons Creek 345 kV | 273 | $10,912,808 |  |
| McNeil Lcra - Gilleland 138 kV, Hutto Switch Axfmr 1 (3) 345/138 kV, Salty - Sandow Switch 138 kV, and DCKT Austrop - Sandow Switch 345 kV | Hutto Switch - Round Rock Northeast 138 kV (1661_B) | 425 | $10,033,349 | 16TPIT0062 |
| DCKT Paris Switch - Valley Ses and Valley South 345 kV | Paris Switch AXFMR1 (3) 345/138 kV | 1,738 | $9,940,305 | 14TPIT0093 |
| DCKT Gabriel - Glasscock LCRA and Rivery 138 kV, Glasscock LCRA - Gabriel 138 kV, and DCKT Gabriel - Bell County - Hutto Switch 138 kV | Marshall Ford - Lago Vista 138 kV | 209 | $9,871,526 | 15TPIT0061 |
| Koch Up River - Gila 138 kV | Gila - Hiway 9 138 kV (GILA_HIWAY_2) | 27,638 | $8,622,377 |  |
| Key Sub - Willow Valley Switch 138 kV and Winks Sub - No Trees Switch 138 kV | Holt Switch - Amoco Midland Farms Tap 138 kV | 475 | $7,974,086 | 15TPIT0092 |
| DCKT Wa Parish - Jeanetta 345 kV | Smithers - Bellaire 345 kV | 1,058 | $7,870,155 |  |
| Alice - Kingsville 138 kV, Kingsville - Lon Hill 138 kV, Nelson Sharpe - Lon Hill 345 kV | Lon Hill - Calallen Sub 69 kV | 912 | $7,699,219 | 12TPIT0181, 2012-R13 |
| Laquinta - Lobo 138 kV | Bruni 138_69_1 138/69 kV | 11,006 | $7,075,506 | 13TPIT0148 |

# System Events

## ERCOT Peak Load

The unofficial ERCOT peak load for the month was 58,421 MW and occurred on October 1 during the hour ending 17:00.

## Load Shed Events

There was one Load Shed Event in the Rio Grande Valley this month. Refer to section 6.5 below for more information.

## Stability Events

None

## Notable PMU Events

ERCOT analyzes PMU data for any significant system disturbances that do not fall into the Frequency Events category reported in section 2.1. The results are summarized in this section once the analysis has been completed.

There were no reportable events in October.

## TRE/DOE Reportable Events

ERCOT experienced one reportable system event this month. On October 8, ERCOT shed greater than 100 MW of firm load in the Rio Grande Valley following a forced outage. An OE-417 report was filed at the time of the event and a formal report from ERCOT on the event will be forthcoming.

## New/Updated Constraint Management Plans

There was one new RAP in October: Laquinta – Lobo 138 kV Single Circuit line was implemented on 10/31/2014.

## New/Modified/Removed SPS

None

## New Procedures/Forms/Operating Bulletins

| Date | Document | Description |
| --- | --- | --- |
| 10/1/2014 | Power Operations Bulletin 683 | DC Tie Desk V1 Rev 30 |
| 10/1/2014 | Power Operations Bulletin 684 | Real Time Desk V1 Rev 32 |
| 10/1/2014 | Power Operations Bulletin 685 | Reliability Unit Commitment Desk V1 Rev 26 |
| 10/1/2014 | Power Operations Bulletin 686 | Resource Desk V1 Rev 30 |
| 10/1/2014 | Power Operations Bulletin 687 | Shift Supervisor Desk V1 Rev 29 |
| 10/1/2014 | Power Operations Bulletin 688 | Transmission and Security Desk V1 Rev 34 |

# Emergency Conditions

## OCNs

None

## Advisories

None

## Watches

None

## Emergency Notices

| Date and Time | Description |
| --- | --- |
| 10/8/2014 16:12 | ERCOT issued an Emergency Notice for a transmission emergency in the Rio Grande Valley due to forced outages causing low voltages. |
| 10/8/2014 19:13 | ERCOT ended the Emergency Notice for a transmission emergency in the Rio Grande Valley due to forced outages causing low voltages. |
| 10/9/2014 07:02 | ERCOT issued an Emergency Notice for a transmission emergency in the Rio Grande Valley due Reliability Margins below 95 MW. |
| 10/9/2014 09:41 | ERCOT ended the Emergency Notice for a transmission emergency in the Rio Grande Valley due Reliability Margins below 95 MW. |

# Application Performance

ERCOT system applications performed well in October. There were no issues to report.

## TSAT/VSAT Performance Issues

None

## Communication Issues

None

# Net-Forecast Bias Applied to NSRS Procurement for November 2014

Each month, ERCOT calculates a net Forecast Bias pursuant to the ERCOT Ancillary Services Methodology for procurement of Non-Spinning Reserve Service (NSRS).  The table below indicates the amount of net Forecast Bias that was applied to the NSRS procurement for specified blocks of time for the month of November, 2014.

| Blocks | Negative Net Load Forecast Average Error - By Weather Zone for the 5 Largest Zones |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Coast | East | North Central | South Central | Southern |
| 1-2 | 0 | 0 | 0 | 0 | 0 |
| 3-6 | 0 | 0 | 0 | 0 | 0 |
| 7-10 | 0 | 0 | 0 | 0 | 0 |
| 11-14 | 0 | 0 | 0 | 0 | 0 |
| 15-18 | 0 | 0 | 0 | 0 | 0 |
| 19-22 | 0 | 0 | 0 | 0 | 0 |
| 23-24 | 0 | 0 | 0 | 0 | 0 |

# Appendix A: Real-Time Constraints

The following is a complete list of constraints activated in SCED for the month of October. Full contingency descriptions can be found in the Standard Contingencies List located on the MIS secure site at Grid  Generation  Reliability Unit Commitment.

| Contingency | Constrained Element | From Station | To Station | # of Days Constraint Active |
| --- | --- | --- | --- | --- |
| SLA_RIO8 | RIOHND_ERIOHND_1 | RIOHONDO | MV_RIOHO | 14 |
| SLA_RIO8 | HARLNS_OLEAND1_1 | HARLNSW | OLEANDER | 11 |
| SNCWMO38 | 6475__E | MOSSW | WOVER | 8 |
| SCRDLOF9 | POS_SHAN_1 | SHANNON | POSTOKSW | 7 |
| DFERPAL8 | 38T365_1 | WIRTZ | FLATRO | 6 |
| DDOLAZ_8 | CA_DE_96_A | DE | CA | 5 |
| SAPACAD8 | HEIGHTTN_HAT1 | HEIGHTTN | HEIGHTTN | 5 |
| SKOCNU28 | GILA_HIWAY_2_1 | GILA | HIWAY_9 | 5 |
| DCHBJOR5 | BRNLAN86_A | LAN | BRN | 4 |
| DLONOR58 | S104A_1 | RIOHONDO | MV_BURNS | 4 |
| DRNKKRW5 | 590__A | LWSSW | LWVJS | 4 |
| SMDFHLT8 | 6596__F | HLTSW | EMATP | 4 |
| DFL_MAR8 | BETHK_66_A | HK | BET | 3 |
| DLONOR58 | LON_HI_SMITH1_1 | LON_HILL | SMITH | 3 |
| DSC_SL28 | CO_WAS84_A | CO | WAS | 3 |
| DTB_SNG5 | SNGZEN99_A | SNG | ZEN | 3 |
| SBRAUVA8 | HAMILT_MAVERI1_1 | HAMILTON | MAVERICK | 3 |
| SLAQLOB8 | BRUNI_69_1 | BRUNI | BRUNI | 3 |
| SORNLON8 | LON_HI_SMITH1_1 | LON_HILL | SMITH | 3 |
| SSCUSUN8 | ROTN_WOLFGA1_1 | WOLFGANG | ROTN | 3 |
| SSPUASP8 | ROTN_WOLFGA1_1 | WOLFGANG | ROTN | 3 |
| BASE CASE | VALIMP |  |  | 2 |
| DCALSKY8 | E1_M1_1 | M1 | E1 | 2 |
| DCRLLSW5 | 590__A | LWSSW | LWVJS | 2 |
| DDL_KR_8 | JTSKR_53_A | KR | JTS | 2 |
| DFRAPAR8 | F4_Z4_1 | Z4 | F4 | 2 |
| DJFSFT_8 | DPWLYD70_A | LYD | DPW | 2 |
| DKG_RNS5 | DPWLYD70_A | LYD | DPW | 2 |
| DNAVLEG5 | 40__A | JEWET | BBSES | 2 |
| DPRSVLY5 | PRSSW_MR1H | PRSSW | PRSSW | 2 |
| DWLV89N8 | 3410__A | ELVSW | REGST | 2 |
| DWR_EB28 | EL_CAM_LANCTY1_1 | LANCTYPM | EL_CAMPO | 2 |
| SFORYEL8 | FORTMA_MASN1_1 | FORTMA | MASN | 2 |
| SLCSTH25 | 505__A | THSES | SAMSW | 2 |
| SLOBSAN5 | 13998T485_1 | FRONTERA | GOODWIN | 2 |
| SLOBSAN5 | FREER_SAN_DI1_1 | SAN_DIEG | FREER | 2 |
| SSALSND8 | 1666__B | GILLCR | PFLGV | 2 |
| BASE CASE | LGD_SANTIA1_1 | LGD | SANTIAGO | 1 |
| BASE CASE | MOSSW_MR1H | MOSSW | MOSSW | 1 |
| BASE CASE | SNYDER_WKN_BK1_1 | ENAS | WKN_BKR | 1 |
| DAUSLOS5 | CKT_3122_1 | FPPYD2 | HOLMAN | 1 |
| DCBYRN28 | EXNLH_03_A | EXN | LH | 1 |
| DDL_HOC8 | AF_STF09_A | STF | AF | 1 |
| DFERGRA8 | 38T365_1 | WIRTZ | FLATRO | 1 |
| DGIBSNG5 | 260_A_1 | JEWET | SNG | 1 |
| DHKBCRL5 | 1140__C | DFWD1 | DFWCE | 1 |
| DHOCDN_9 | DN_HP_32_A | HP | DN | 1 |
| DLHSCNR8 | 3650__A | LHSES | SATP1 | 1 |
| DLONOR58 | LASPUL_RIOHON1_1 | LASPULGA | RIOHONDO | 1 |
| DLONOR58 | RIOHONDO_AT1H | RIOHONDO | RIOHONDO | 1 |
| DMARZOR5 | 293T304_1 | CIBOLO | SCHERT | 1 |
| DNAVLEG5 | 50__A | JEWET | BBSES | 1 |
| DNAVWTR5 | 30__A | BBSES | RCHBR | 1 |
| DNAVWTR5 | 35040__A | NAVARRO | VENSW | 1 |
| DNEDPAL8 | ADERHO_DUKE1_1 | DUKE | ADERHOLD | 1 |
| DPHR_AL5 | CA_DE_96_A | DE | CA | 1 |
| DSKYMAR5 | 293T304_1 | CIBOLO | SCHERT | 1 |
| DVICV_D8 | FORMOS_LOLITA1_1 | LOLITA | FORMOSA | 1 |
| DWAP_OB5 | DV_HT_24_A | HT | DV | 1 |
| SABSBLU8 | ABNW_CALLAH1_1 | CALLAHAN | ABNW | 1 |
| SAJORI25 | CELANE_KLEBER1_1 | CELANEBI | KLEBERG | 1 |
| SAJORI25 | CELANE_N_SHAR1_1 | N_SHARPE | CELANEBI | 1 |
| SALIKIN8 | FALFUR_69A1 | FALFUR | FALFUR | 1 |
| SBOSELM5 | 1030__B | BOSQUESW | RGH | 1 |
| SBRBMGS8 | 14035__A | MGSES | BRBSW | 1 |
| SCHABSP9 | CEDH_69_1 | CEDH | CEDH | 1 |
| SCHYWIN8 | 6090__D | HLTSW | AMMFT | 1 |
| SCOLBAL8 | DRSY_SANA_T1_1 | SANA_TAP | DRSY | 1 |
| SCRDLOF9 | JOY_POST_1 | POSTOKSW | JOY | 1 |
| SCVNCBY8 | CD_TAP87_1 | CD | CD | 1 |
| SDAFAUS8 | CKT_1027_1 | DUNLAP | DECKER | 1 |
| SJNSWNT8 | SYC_CORY_1 | SYCAMORE | CORYELCO | 1 |
| SKEYWLV8 | 6610__D | BSPSW | BSCTP | 1 |
| SLOBSAN5 | LAQUIN_LOBO1_1 | LAQUINTA | LOBO | 1 |
| SLOBSAN5 | MINES__NLARSW1_1 | NLARSW | MINES_RD | 1 |
| SLOLFOR8 | CHOCBA_GOHLKE1_1 | CHOCBAYU | GOHLKE | 1 |
| SL_4RAY8 | RAYBURN_69_2 | RAYBURN | RAYBURN | 1 |
| SMCEABS8 | ABNW_ELYT1_1 | ABNW | ELYT | 1 |
| SMDFHLT8 | 6101__B | WINKS | CHEYT | 1 |
| SMDFHLT8 | LMESA_FMR1 | LMESA | LMESA | 1 |
| SMDOPHR5 | G138_10C_1 | FRDSWOOD | SEMINOLE | 1 |
| SMV_NED8 | ADERHO_DUKE1_1 | DUKE | ADERHOLD | 1 |
| SOXYIN28 | I_DUPP_I_DUPS2_1 | I_DUPP1 | I_DUPSW | 1 |
| SPOACSS8 | CSSWCS-CSSC_1 | CSSWCS | CSSC | 1 |
| SSPUASP8 | JATN_SPUR_1C_1 | GIRA_TAP | DKEC | 1 |
| SSPUASP8 | GIRA_T_SPUR1_1 | SPUR | GIRA_TAP | 1 |
| SSPUASP8 | SPUR_69_1 | SPUR | SPUR | 1 |
| SVICCO28 | COLETO_VICTOR2_1 | COLETO | VICTORIA | 1 |
| SWILJA28 | WISECNTY_JCKCN_1 | JACKCNTY | WISECNTY | 1 |
| SWINPBS8 | MOSSW_MR1H | MOSSW | MOSSW | 1 |
| SWRDYN8 | NEWTGF04_A | TGF | NEW | 1 |
| XASP89 | MUNDAY_MUNDAY1_1 | MUNDAYST | MUNDAYR2 | 1 |
| XCDH58 | 6325__C | SHRSW | PRKRW | 1 |
| XGAR158 | CKT_1027_1 | DUNLAP | DECKER | 1 |
| XLOB58 | 13998T485_1 | FRONTERA | GOODWIN | 1 |
| XLWS58 | 1065__L | EULES | GRHWY | 1 |
| XMDL58 | MOSSW_MR1H | MOSSW | MOSSW | 1 |
| XMOS258 | 6345__B | GNTSW | SPRTP | 1 |
| XPH2R58 | PHR_AT1L | PHR | PHR | 1 |
| XPH3R58 | PHR_AT1L | PHR | PHR | 1 |
| XPHR358 | PHR_AT1L | PHR | PHR | 1 |
| XRIO358 | ADERHO_DUKE1_1 | DUKE | ADERHOLD | 1 |
| XSA2C89 | CONCHO_FMR1 | CONCHO | CONCHO | 1 |
| XSTA89 | 6144__A | STASW | BSPRW | 1 |
| XWLV158 | 3416__A | NORSW | CHROW | 1 |