## Slide 1: PDCWG Report to ROS January 8, 2015
Chair: Sydney L. Niemeyer
Vice-Chair: Don Blackburn

## Slide 2: PDCWG Meeting December 15, 2014
18 members attended the meeting.
BAL-001-TRE-1 update:
  Performance measures begin April 1, 2015. TRE or ERCOT will notify GO’s when and how to declare which generators will begin R6, R7, R9 and R10. This must include 50% of generators if located at a multi-generator site starting April 1.
  RARF changes for Governor settings should be submitted in February or sooner for any changes to meet this standard for this first group.

## Slide 3: Meeting Continued
Disturbance Reports:
  ERCOT added Inertia data to the disturbance reports for events beginning in November.
  ERCOT added Power Augmentation data for all Combined Cycle plants to the November events.
  Reviewed the following frequency event reports:
    Oct 9, 2014 @ 13:29
      Five generators providing RRS had less than expected response.
      All other generators with low performance were thought to have only augmented power available.

## Slide 4: Disturbance Reports
Oct 13, 2014 @ 08:27
  Four generators with RRS had less than expected response.
  One non RRS generator had less than expected response.
Nov 21, 2014 @ 05:13
  Two generators with RRS had less than expected response.

## Slide 5: Disturbance Reports
Nov 28, 2014 @ 20:11
  Two generators with RRS had less than expected response.
  Two non RRS generators had less than expected response.
Inertia Data tracking.
  Total Inertia
  High speed frequency data will be provided on events below 59.850 Hz.
  Delta time in seconds between Point A and Point C, time to reach the nadir.

## Slide 6: ERCOT Frequency Control Report November 2014
Sydney Niemeyer NRG Energy
December 11, 2014

## Slide 7: Ercot frequency control
BAL-001 CPS 1 & 2 Performance, RMS 1 and Frequency Profile

## Slide 14
CPS1 12 Month Rolling Average = 163.28

## Slide 19
60.010 <= HZ < 60.015

## Slide 21: Frequency profile comparison 2008 through 2014
Each year’s frequency profile is compared to the 2014 frequency profile.

## Slide 28: ERCOT Time error and time correction
Time Error History

## Slide 29: Notes
Time error values from NRG True Time device can be slightly different from ERCOT’s Time Error but the daily delta times should be accurate.

## Slide 30: Time Error Corrections
One slow Time Error Correction was executed in November.
In November, other than the day with the TEC, nine days had positive time error.
Five slow Time Error Corrections were executed in December.
In December, other than the days with the TECs, two days had positive time error.

## Slide 34
Time Correction History

## Slide 37: Ercot primary frequency response performance
BAL-003-1 Interconnection Frequency Response and Bias Measure.

## Slide 38
ERCOT Primary Frequency Response – BAL-003-1
2015 Bias and Frequency Response Measure

## Slide 39
2015 BAL-003-1 Performance to R1
R1 Present Interconnection Minimum Frequency Response Requirement: -413 MW/0.1 Hz
Using the Median Measure

## Slide 40
2016 BAL-003-1 Performance to R1

## Slide 41: Ercot total energy and wind production
Total ERCOT Energy and Total Energy Production from Wind Resources.