## Slide 1: ERCOT Update BAL-001-TRE-1 Implementation
Matt Mereness
ROS Meeting
January 8, 2015

## Slide 2: BAL-001-TRE-1 Discussion outline
What is it?
Who does it impact?
When is it?
Where are the reports?
Appendix

## Slide 3: What is BAL-001-TRE-1
BAL-001-TRE-1 is a NERC Standard being implemented this year which generally creates:
Requirements for Generation Owners:
  Specifies Droop and Deadband settings (details in Appendix)
  Rolling 12-month performance requirements for generation resources
  Notify ERCOT (via QSE) within 30 minutes if governor is out of service
Requirements for the Balancing Authority/ERCOT:
  Public posting of Frequency Measurable Event occurrences
  Calculation changes for Frequency Response measurements
  Calculation of 12-month rolling performance averages for each Generator

## Slide 4: Who does BAL-001-TRE-1 impact
    As already required per Protocols, all registered Generation Resources are expected to have governors in service and comply with Droop and Deadband settings as well as meet performance requirements, with the exception of
  4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL-001-TRE-01
  4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01
  4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard [i.e. currently exempted older wind farms]

## Slide 5: When? Timeline for BAL-001-TRE-1
3/24/2015
RARFs and “50% declaration” filed with ERCOT

## Slide 6: When? Timeline for BAL-001-TRE-1
    Submission deadlines to ERCOT for the first 50% of the generation portfolio for compliance measurement are March 24, 2015 (RARF and Declaration)
    RARFs reflecting changes to Droop and Deadband setting should always be communicated to ERCOT as soon as they are changed at the generation resource (can be done early for any resources), but no later than March 24, 2015 for the 50% of portfolio to be measured for compliance
    “Declaring” which generation resources are part of the 50% to be measured in the portfolio is also due on Mach 24, 2015.
      ERCOT is developing template/listing of GOs/Resources to email in February
      GenOwner GenResource Compliant for Measurement 4/1/2015
      Gen X Coal-1 Yes
      Gen X Coal-2 No
      GOs are required to send the completed declaration list of generators to ERCOT Client Services via email at ClientServices@ercot.com by March 24, 2015

## Slide 7: When? Timeline for BAL-001-TRE-1
      ERCOT will use the 7 days between March 24 - April 1 to configure in system and outreach for missing Generators
All NERC registered Generation Owners with more than one unit/facility are required to change at least 50% of its generating units/facilities Governor Deadband (tighter for most units) and Droop settings
  50% is number of generation resources (not MW weighted)
  If only one registered generation resource, can defer to Oct 1, 2015
“Generator RARF forms” were amended and released to all applicable resources
  For stand-alone Steam Turbines, throttle pressure curve data was solicited using 13 new fields in pre-populated RARFs with information provided in response to ERCOT’s RFI.
        All remaining generation resources are to be compliant by Oct 1, 2015

## Slide 8: Where are the Reports?
ERCOT will begin posting reports supporting BAL-001-TRE-1 on April 1, 2015
ERCOT is adding five new report links to the Market Information System (MIS). Three public reports can also be viewed on ERCOT.com website.
EMIL ID | Product Name | Frequency | Posting Classification | Report Type ID | MIS Landing Page | ERCOT.COM Landing Page
NP12-261-M | Frequency Measurable Events in ERCOT Interconnection | Weekly | Public | 13450 | Compliance | http://www.ercot.com/mktinfo/reports/index.html
NP12-262-M | Initial and Sustained Primary Frequency Response Unit Performance | Monthly | Certified-PDCWG | 13451 | PDCWG | 
NP12-263-M | Initial and Sustained Primary Frequency Response 12-month rolling average Unit Performance | Monthly | Certified- QSE/RE | 13452 | Compliance | 
NP12-264-M | ERCOT Interconnection Minimum Frequency Response Computation Methodology | Annual | Public | 13453 | Compliance | http://www.ercot.com/mktinfo/reports/index.html
NP12-265-M | ERCOT Interconnection combined Frequency Response Performance | Monthly | Public | 13454 | Compliance | http://www.ercot.com/mktinfo/reports/index.html

## Slide 9: Access to Reports
No Digital Certificate is needed to view public reports.
Unit 12-month rolling average performance report is confidential and accessible to the entities that represent the unit.
Initial and Sustained Primary Frequency Response Unit Performance report during each FME is posted to PDCWG page on Market Information System (MIS)
  To view the reports on PDCWG page, market participant should be PDCWG member and need to have a Digital Certificate with “ICE_M_VIEW_PDCWG” added to the current roles.
  If “ICE_M_VIEW_PDCWG” is not seen in the current roles, please contact MarketInfoServices@ercot.com to verify the NDA and/or USA to have the “ICE_M_VIEW_PDCWG” role added.

## Slide 10: In conclusion…
ERCOT will be reaching out to Generation Owners for declaration of which 50% of their portfolio should be measured.
  ERCOT will send listing in February (working with TexasRE to create list)
  Generation Owners will complete declaration list and send to ClientServices@ercot.com by 3/24/2015
Generation Owners should be updating their RARFs when any Droop/Deadband changes are made and submit through regular process with 3/24/15 deadline for those to be measured April 1.
All changes should be completed for measurement on April 1 when new reporting begins.
Any questions?

## Slide 11
Appendix

## Slide 12: Appendix
R6. Each GO shall set its Governor parameters as follows:
6.1. Governor Deadband Settings:
6.2. Governor Droop Settings

## Slide 13
Appendix - BAL-001-TRE-1 Conceptual Design

## Slide 14
Appendix- BAL-001-TRE Project Timeline
To be implemented in two phases
  Phase 1 – Targets updating MIS, RARF & MPIM
    Key Dates - 10/3/14 thru 12/10/14
  Phase 2 – Targets updating EMS & PDC reports
    Key Dates - 12/22/14 thru 2/15/15
Tasks Accomplished to Date- 2014
  10/31 - Phase 1 System Changes have been migrated to iTest
  11/3 – RFI For Steam Pressure Due
  12/11 – Phase 1 System Changes Migrate to Prod
  12/22 – Phase 2 Development kick off
Upcoming Key Dates- 2015
  1/12 – Phase 2 Migration to iTest
  2/1 – Post FMEs to MIS
7
/
24
/
2014
2
/
24
/
2015
8
/
1
9
/
1
10
/
1
11
/
1
12
/
1
1
/
1
2
/
1
Phase
–
1
(
R
6
)
MIS
,
RARF
,
MPIM
Phase
–
2
(
R
1
)
EMS
,
PDC Reports
RRGRR 004- Steam Pressure Curve & K-Factor
Today
7
/
24/14
Project Start
11
/
1
NFRC in EMS
10
/
3
Dev Start
10
/
31
Migrate to iTest
RFI Due
11
/
3
11
/
11
1
/
12
Migrate to iTest
2
/
15
Migrate to Prod
8
/
15
RRGRR
Submitted
2
/
24/15
Project Closed
12
/
22
Dev Start
12
/
10
Migrate to Prod
10
/
2
RFI Sent
9
/
25
RRGRR
TAC Apprv