## Slide 1
2015 RTP Update
January, 2015

## Slide 2: Outline
2015 RTP Overview
2015 RTP Scope
2015 RTP Input Assumptions
Next steps

## Slide 3: 2015 RTP Overview: Cases studied
Summer peak reliability basecase for years 2016, 2018, 2020, and 2021
Off-peak (min load) reliability basecase for 2018
Sensitivity cases for summer peak cases of years 2016 and 2020
Sensitivity cases for off-peak case for 2018.

## Slide 4: 2015 RTP Overview: Analysis
SCOPF
Contingency analysis (Single event)
Multiple element contingency analysis
  G(generator)-1+N-1
  X(transformer)-1+N-1
  N-1-1 and cascade analysis
Short circuit analysis
Analysis of sensitivity cases
Economic analysis

## Slide 5: RTP Scope
RTP scope and process document and responses to comments are posted on the RPG meeting page
Outstanding items on the RTP Scope document
  Details regarding short circuit analysis
  Details regarding sensitivity cases
Noteworthy updates from 2014 scope
  Updated performance criteria per TPL-001-4
  Dynamic ratings to be used in reliability analysis

## Slide 6: Dynamic Ratings in Reliability Analysis
Weather Zone | 90th percentile temperature (°F)
Coast | 102.4
East | 106.2
Far West | 110.4
North Central | 108.4
North | 109.0
South Central | 105.5
South | 104.0
West | 107.3
90th percentile temperature for each weather zone was derived based on 30 years of temperature data (1984-2013)
Temperature data based on historical data from ERCOT databases

## Slide 7: RTP Load by weather zone
Year | Coast | East | North | North Central | South Central | South | West | Far West | NCP Total
2016 | 26,084 | 2,771 | 1,749 | 26,300 | 13,094 | 6,540 | 2,257 | 3,124 | 81,920
2018 | 26,883 | 2,822 | 1,803 | 27,003 | 13,803 | 6,913 | 2,314 | 3,453 | 84,994
2020 | 27,522 | 2,894 | 1,848 | 27,690 | 14,479 | 7,284 | 2,390 | 3,656 | 87,763
2021 | 27,766 | 2,921 | 1,764 | 28,034 | 14,845 | 7,470 | 2,429 | 3,764 | 88,993
RTP weather zone load based on the ‘higher-of’ SSWG summer peak weather zone load and ERCOT 90th percentile load forecast
Zones where ERCOT 90th percentile forecast is higher are presented in red font
Note: Weather zone loads expressed in MW

## Slide 8: Next steps
Create and publish RTP reliability start cases
Conduct N-1 SCOPF and contingency analysis
Post contingency definitions and resulting violations
Corrective action plans such as transmission upgrades or additions will be tested in collaboration with respective transmission owners
Create and post N-1 Secure case
Conduct G-1+N-1 and X-1+N-1 screen and identify corrective action plans to address violations

## Slide 9: Questions?

## Slide 10: Appendix

## Slide 11: SSWG load
Year | Coast | East | North | North Central | South Central | South | West | Far West | NCP Total
2016 | 26,084 | 2,771 | 1,749 | 24,695 | 13,094 | 6,397 | 2,257 | 3,124 | 80,171
2017 | 26,446 | 2,795 | 1,766 | 24,968 | 13,447 | 6,475 | 2,280 | 3,322 | 81,499
2018 | 26,883 | 2,822 | 1,803 | 25,322 | 13,803 | 6,792 | 2,314 | 3,453 | 83,191
2019 | 27,228 | 2,849 | 1,826 | 25,604 | 14,131 | 6,802 | 2,352 | 3,565 | 84,356
2020 | 27,522 | 2,894 | 1,848 | 25,910 | 14,479 | 7,078 | 2,390 | 3,656 | 85,777
2021 | 27,766 | 2,921 | 1,764 | 26,314 | 14,845 | 7,222 | 2,429 | 3,764 | 87,024
Load based on October 2014 SSWG Data Set B cases
Includes self served load, does not include losses
Note: Weather zone loads expressed in MW

## Slide 12: ERCOT 90th percentile load forecast
Year | Coast | East | North | North Central | South Central | South | West | Far West | NCP Total
2016 | 23,133 | 2,347 | 1,573 | 26,300 | 11,977 | 6,540 | 2,015 | 2,715 | 76,601
2017 | 23,335 | 2,354 | 1,563 | 26,654 | 12,060 | 6,728 | 2,035 | 2,832 | 77,561
2018 | 23,537 | 2,360 | 1,554 | 27,003 | 12,141 | 6,913 | 2,054 | 2,949 | 78,511
2019 | 23,739 | 2,367 | 1,544 | 27,348 | 12,221 | 7,099 | 2,074 | 3,065 | 79,456
2020 | 23,937 | 2,373 | 1,534 | 27,690 | 12,300 | 7,284 | 2,094 | 3,181 | 80,393
2021 | 24,141 | 2,380 | 1,525 | 28,034 | 12,378 | 7,470 | 2,114 | 3,297 | 81,338
Includes self served load, does not include losses
Note: Weather zone loads expressed in MW

## Slide 13: Wind dispatch output levels
Dispatch based on confidence-percentile analysis
Hours with high loads were selected (Hours were ERCOT load higher than 95th percentile
Wind output levels in the basecase based on 15th percentile output levels, but not to exceed levels based on 25th percentile level
Weather Zone | Basecase | Dispatch Not to exceed
Coast | 1% | 4%
East | - | -
North | 3% | 8%
North Central | 1% | 3%
South Central | 2% | 4%
Southern | 10% | 18%
West | 3% | 7%

## Slide 14: New generation per PG 6.9 requirements
Project Name | In-service Date | Capacity Added* (MW) | Fuel | County | TDSP | Weather Zone
Baytown Chiller | 6/1/2015 | 270 | Gas | Chambers | Centerpoint | COAST
PHR Peakers | 11/30/2015 | 390 | Gas | Galveston | Centerpoint | COAST
Panda Temple 2 G | 8/1/2015 | 790 | Gas | Bell | Oncor | NORTH
Antelope Station | 6/1/2016 | 359** | Gas | Hale | Sharyland | NORTH
Goldsmith Peakers | 6/1/2015 | 341 | Gas | Ector | Oncor | WEST
Keechi Wind 138 kV Joplin | 1/5/2015 | 102 | Wind | Jack | BRAZOS | NORTH
Grandview Phase II (Conway Windfarm) | 10/1/2015 | 389 | Wind | Carson | Shalyland | NORTH
Jumbo Road Wind | 4/15/2015 | 300 | Wind | Castro | Sharyland | NORTH
Route66 Wind | 8/15/2015 | 150 | Wind | Randall | Sharyland | NORTH
Spinning Spur Wind Three | 5/31/2015 | 194 | Wind | Oldham | Sharyland | NORTH
Midway Wind | 12/28/2016 | 161 | Wind | San Patricio | AEP | SOUTH
Cameron County Wind | 9/1/2015 | 165 | Wind | Cameron | STEC | SOUTH
Patriot (Petronilla) Wind | 8/15/2015 | 178 | Wind | Nueces | AEP | SOUTH
Sendero Wind | 8/31/2015 | 78 | Wind | Jim Hogg | AEP | SOUTH
Los Vientos III | 3/31/2015 | 200 | Wind | Starr | AEP | SOUTH
Javelina Wind | 12/31/2015 | 250 | Wind | Zapata | AEP | SOUTH
Los Vientos V | 12/15/2015 | 200 | Wind | Starr | AEP | SOUTH
Los Vientos IV | 12/31/2015 | 200 | Wind | Starr | AEP | SOUTH
Mesquite Creek W | 3/31/2015 | 211 | Wind | Borden | WETT | WEST
South Clay Windfarm | 6/15/2015 | 200 | Wind | Clay | ONCOR | WEST
Stephens Ranch Wind Energy Phase b | 4/1/2015 | 165 | Wind | Borden | WETT | WEST
Green Pastures W | 2/17/2015 | 300 | Wind | Knox | AEP | WEST
Rattlesnake Wind Ph 1 | 9/1/2015 | 211 | Wind | Glasscock | WETT | WEST
Longhorn Energy Center | 12/31/2015 | 361 | Wind | Briscoe | Sharyland | WEST
South Plains Wind I | 7/31/2015 | 200 | Wind | Floyd | Sharyland | WEST
South Plains II | 12/1/2015 | 150 | Wind | Floyd | Sharyland | WEST
Wake Wind | 11/1/2015 | 299 | Wind | Dickens | WETT | WEST
Briscoe Wind | 12/31/2015 | 150 | Wind | Briscoe | Sharyland | WEST
*Based on Generator Interconnection data
**Capacity not available to ERCOT throughout summer