| NOGRR Number | 139 | NOGRR Title | Under/Over-Frequency Relaying Requirements |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Recommended Approval |
| Date of Decision |  | January 26, 2015 |  |  |
| Proposed Effective Date |  | To be determined. |  |  |
| Priority and Rank Assigned |  | To be determined. |  |  |
| Nodal Operating Guide Sections Requiring Revision |  | 2.6, Requirements for Under-Frequency Relaying 2.6.2, Generators |  |  |
| Other Binding Documents Requiring Revision or Related Revision Requests |  | None. |  |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) adds over-frequency relaying requirements and clarifies under-frequency and over-frequency relay set-points so that Generation Resources know what is expected. Over-frequency relay set points criteria was approved by North American Electric Reliability Corporation (NERC) in March 2014 under Standard PRC-024, Generator Frequency and Voltage Protective Relay Settings. |  |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) |  |  |
| Procedural History |  | - On 9/30/14, NOGRR139 and an associated Impact Analysis were posted. - On 10/8/14, Calpine comments were posted. - On 10/21/14, Luminant comments were posted. - On 10/22/14, the Operations Working Group (OWG) considered NOGRR139. - On 11/14/14, Austin Energy comments were posted. - On 1/26/15, OWG again considered NOGRR139. |  |  |
| OWG Decision |  | On 10/22/14, OWG was in consensus to table NOGRR139. On 1/26/15, OWG was in consensus to recommend approval of NOGRR139 as amended by the 11/14/14 Austin Energy comments. |  |  |
| Summary of OWG Discussion |  | On 10/22/14, OWG tabled NOGRR139 to allow for additional review. On 1/26/15, there was no discussion. |  |  |

| Business Case |  |
| --- | --- |
| Qualitative Benefits | - This NOGRR aligns the ERCOT Operating Guides with a recently approved NERC requirement; all generators in the ERCOT region are impacted. |
| Quantitative Benefits |  |
| Impact to Market Segments |  |
| Credit Implications |  |
| Other |  |

| Sponsor |  |
| --- | --- |
| Name | Ajay Pappu / Isabel Flores |
| E-mail Address | vpappu@ercot.com / iflores@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-3168 / 512-248-6531 |
| Cell Number |  |
| Market Segment | Not applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Brian Manning |
| E-Mail Address | Brian.manning@ercot.com |
| Phone Number | 512-248-3937 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| Calpine 100814 | Proposed changes to align the language with NERC Reliability Standard PRC-024-1. |
| Luminant 102114 | Proposed changes to clarify the language. |
| Austin Energy 111414 | Proposed changes to clarify the language. |

Revised Proposed Guide Language

2.6	Requirements for Under-Frequency and Over-Frequency Relaying

2.6.2	Generators

(1)	If under-frequency relays are installed and activated to trip the unit, these relays shall be set such that the automatic removal of individual Generation Resources from the ERCOT System meets the following requirements:

| Frequency Range | Delay to Trip |
| --- | --- |
| Above 59.4 Hz | No automatic tripping (Continuous operation) |
| Above 58.4 Hz up to And including 59.4 Hz | Not less than 9 minutes |
| Above 58.0 Hz up to And including 58.4 Hz | Not less than 30 seconds |
| Above 57.5 Hz up to And including 58.0 Hz | Not less than 2 seconds |
| 57.5 Hz or below | No time delay required |

(2)	If over-frequency relays are installed and activated to trip the unit, they shall be set such that the automatic removal of individual Generation Resources from the ERCOT System meets the following requirements:

This Operating Guide is not intended to conflict with the plant operator’s responsibility to protect Generation Resources from potentially damaging operating conditions. This Operating Guide is not intended to conflict with the plant operator’s responsibility to protect Generation Resources from potentially damaging

| Frequency Range | Delay to Trip |
| --- | --- |
| Below 60.6 Hz down to and including 60 Hz | No automatic tripping (Continuous operation) |
| Below 61.6 Hz down to and including 60.6 Hz | Not less than 9 minutes |
| Below 61.8 Hz down to and including 61.6 Hz | Not less than 30 seconds |
| 61.8 Hz or above | No time delay required |

(3)		The Resource Entity that owns Generation Resources that are unable to comply shall provide to ERCOT an explanation of the limitations including, but not limited to, study results or manufacturer’s advice.