| NOGRR Number | 136 | NOGRR Title | Verifying QSE Capability to Operate in CFC |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Approved |
| Date of Decision |  | February 26, 2015 |  |  |
| Effective Date |  | March 1, 2015 |  |  |
| Priority and Rank Assigned |  | Not applicable. |  |  |
| Nodal Operating Guide Sections Requiring Revision |  | 1.4, Definitions 2.2.4.3, ERCOT Loss of AGC |  |  |
| Other Binding Documents Requiring Revision or Related Revision Requests |  | Nodal Protocol Revision Request (NPRR) 646, Emergency Operations Settlement for CFC (formerly “Emergency Operations Settlement for CFC Testing”) |  |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) establishes a process for ERCOT to conduct Constant Frequency Control (CFC) tests to ensure that Qualified Scheduling Entities (QSEs) can provide this service if ERCOT loses its ability to control system frequency; and removes the CFC definition from the Nodal Operating Guide due to the definition being incorporated into the Protocols via associated NPRR646. |  |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |  |
| Procedural History |  | - On 7/30/14, NOGRR136 and an Impact Analysis were posted. - On 8/13/14, ERCOT comments were posted. - On 8/13/14, Luminant comments were posted. - On 8/19/14, the Operations Working Group (OWG) considered NOGRR136. - On 10/22/14, OWG again considered NOGRR136. - On 11/19/14, OWG considered the 10/22/14 OWG Report and Impact Analysis for NOGRR136. - On 1/8/15, ROS considered NORGRR136. - On 1/29/15, TAC considered NOGRR136. - On 2/26/15, TAC again considered NOGRR136. |  |  |
| OWG Decision |  | On 8/19/14, the OWG was in consensus to table NOGRR136 for one month. On 10/22/14, the OWG was in consensus to recommend approval of NOGRR136 as amended by the 8/13/14 Luminant comments. On 11/19/14, OWG was in consensus to endorse and forward to ROS the 10/22/14 OWG Report and Impact Analysis for NOGRR136. |  |  |
| Summary of OWG Discussion |  | On 8/19/14, the OWG tabled NOGRR136 pending WMS review of associated NPRR646. On 10/22/14, there was no discussion. On 11/19/14, there was no discussion. |  |  |
| ROS Decision |  | On 1/8/15, ROS unanimously voted to recommend approval of NOGRR136 as recommended by OWG in the 11/19/14 OWG Report. All Market Segments were present for the vote. |  |  |
| Summary of ROS Discussion |  | On 1/8/15, there was no discussion. |  |  |
| TAC Decision |  | On 1/29/15, TAC unanimously voted to table NOGRR136. All Market Segments were present for the vote. On 2/26/15, TAC unanimously voted to approve NOGRR136 as recommended by ROS in the 1/8/15 ROS Report. All Market Segments were present for the vote. |  |  |
| Summary of TAC Discussion |  | On 1/29/15, it was noted that NOGRR136 should be tabled pending ERCOT Board approval of the associated NPRR646. On 2/26/15, there was no discussion. |  |  |

| Business Case |  |
| --- | --- |
| Qualitative Benefits | - Helps to ensure QSEs can perform in CFC mode. |
| Quantitative Benefits |  |
| Impact to Market Segments |  |
| Other |  |

| Sponsor |  |
| --- | --- |
| Name | Sandip Sharma |
| E-mail Address | ssharma@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-4298 |
| Cell Number |  |
| Market Segment | Not applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Lindsay Butterfield |
| E-Mail Address | Lindsay.butterfield@ercot.com |
| Phone Number | 512-248-6521 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| ERCOT 081314 | Corrected baseline. |
| Luminant 081314 | Proposed revising the allotted timeframe for a QSE to switch to CFC mode from two minutes to five minutes to allow adequate time for the transition. |

Proposed Guide Language Revision

- 1.4	Definitions

2.2.4.3	ERCOT Loss of AGC

(1)	ERCOT has back-up facilities in place for loss of control systems.  In the event that these backup facilities also fail to perform, ERCOT shall direct a QSE providing regulation to implement Constant Frequency Control (CFC) for the duration of the control loss.  ERCOT will direct the QSE providing CFC to enter the appropriate bias into their control system.  If a QSE on CFC develops a problem with regulating room, ERCOT will order additional regulation energy from another QSE to create regulation room.

(2)	ERCOT shall conduct unannounced testing to verify a QSE’s capability to operate in CFC mode.  Only QSEs with at least 350 MW of spinning reserve room will be tested.  QSEs shall be tested at least once every three years.  At a time determined solely by ERCOT, ERCOT will direct the QSE to operate under CFC mode. Once instructed by ERCOT, the QSE will have five minutes to switch to CFC mode.  The duration of this test shall be no more than 15 minutes.  ERCOT shall maintain the list of QSEs that have successfully demonstrated their capability to operate in CFC mode.