## Products+Services
Name | Acronym / Resource Type | Service Type | Begin Date | End Date | Minimum Eligible Resource Size | Minimum Reduction Amount | Aggregation Allowed | Response Required | Primary Driver | Trigger Logic | Total Demand Response Contribution Limit (%) | Minimum Sustained Response Period | Maximum Sustained Response Period | Maximum Deployments per Availability Window | Obligation Period | Availability Window | Demand Resource Availability Measurement | Transparency of Requirements (Demonstrated through ISO/RTO Web Link) | Resource-Specific | Bulk | Self | Service Provider (SP) | Load Serving Entity (LSE) | Scheduling Entity (SE) | Designated Dispatch Entity (DDE) | Transmission / Distribution Service Provider (TDSP) | Metering Authority (MA) | Enrollment & Qualification | Forward Scheduling & Award Notification | Deployment | Real-Time Communications | (After-The-Fact) Measurement & Performance Evaluation | Advance Notification(s) | Ramp Period | Sustained Response Period | Recovery Period | Telemetry Requirement | Telemetry Accuracy | Telemetry Reporting Interval | Other Telemetry Measurements | Communication Protocol | Governor Control Equivalent | On-Site Generation Telemetry Requirement | After-the-Fact Metering Requirement | Meter Accuracy | Clock/Time Accuracy | Details of Meter/Equipment Standards | Meter Data Reporting Deadline | Meter Data Reporting Interval | Validating, Editing & Estimating (VEE) Method | On-Site Generation Meter Requirement | Performance Evaluation Type (see next tab)
Emergency Response Service --10 minutes | ERS-10 | Capacity | Active | None | 100 kW | 100 kW | Yes | Mandatory | Reliability | Operational Procedure | N / A | N / A | 12 hours | N / A | ERS Time Periods Awarded | ERS Time Periods Awarded | Calculated after the Commitment Period | http://www.ercot.com/services/programs/load/eils/ |  |  |  | QSE | Competitive Retailer or Non-Opt-In Entity (not relevant to DR) | QSE | QSE | TDSP | TDSP or Licensed Professional Engineer | Electronic File Submission | Electronic Form via Email | Verbal Dispatch Instruction & XML Message | N / A | EDI Transaction or Form submission (Multiple Formats) | None | 10 Minutes | As Dispatched / Recalled | 10 Hours | No | N / A | N / A | N / A | N / A | N / A | N / A | Yes | ± 2 % | 5% relative to NIST Atomic Clock | MW Accuracy: PUCT Subst. R. 25.121 referencing ANSI C12; Guidelines for non-IDR metered Load aggregations posted as separate document at http://www.ercot.com/services/programs/load/eils/ | Contract Term End + 35 Days | 15 Minutes | Standard VEE by meter-reading entity | 15-minute metering for ERS Generators | Regression / Mid 8 of 10 / Matching Day Pair / Control Group / Alternate Baseline
Emergency Response Service -- 30 minutes | ERS-30 | Capacity | Active | None | 100 kW | 100 kW | Yes | Mandatory | Reliability | Operational Procedure | N / A | N / A | 12 hours | N / A | ERS Time Periods Awarded | ERS Time Periods Awarded | Calculated after the Commitment Period | http://www.ercot.com/services/programs/load/eils/ |  |  |  | QSE | Competitive Retailer or Non-Opt-In Entity (not relevant to DR) | QSE | QSE | TDSP | TDSP or Licensed Professional Engineer | Electronic File Submission | Electronic Form via Email | Verbal Dispatch Instruction & XML Message | N / A | EDI Transaction or Form submission (Multiple Formats) | None | 30 Minutes | As Dispatched / Recalled | 10 Hours | No | N / A | N / A | N / A | N / A | N / A | N / A | Yes | ± 2 % | 5% relative to NIST Atomic Clock | MW Accuracy: PUCT Subst. R. 25.121 referencing ANSI C12; Guidelines for non-IDR metered Load aggregations posted as separate document at http://www.ercot.com/services/programs/load/eils/ | Contract Term End + 35 Days | 15 Minutes | Standard VEE by meter-reading entity | 15-minute metering for ERS Generators | Regression / Mid 8 of 10 / Matching Day Pair / Control Group / Alternate Baseline
Weather-Sensitive ERS-10 or ERS-30 | ERS Weather-Sensitive Load (resource type) | Capacity | Active | None | 500 kW | 500kW | Yes | Mandatory | Reliability | Operational Procedure | N / A | N / A | 3 hours | 8 | Jun - Sept | Hours Ending 14 to 20 | Calculated after the Commitment Period | http://www.ercot.com/services/programs/load/eils/ |  |  |  | QSE | Competitive Retailer or Non-Opt-In Entity (not relevant to DR) | QSE | QSE | TDSP | TDSP or Licensed Professional Engineer | Electronic File Submission | Electronic Form via Email | Verbal Dispatch Instruction & XML Message (group dispatch) | N / A | EDI Transaction or Form submission (Multiple Formats) | None | 10 Minutes or 30 Minutes | As Dispatched / Recalled | N / A | No | N / A | N / A | N / A | N / A | N / A | N / A | Yes | ± 2 % | 5% relative to NIST Atomic Clock | MW Accuracy: PUCT Subst. R. 25.121 referencing ANSI C12; Guidelines for non-IDR metered Load aggregations posted as separate document at http://www.ercot.com/services/programs/load/eils/ | Contract Term End + 35 Days | 15 Minutes | Standard VEE by meter-reading entity | N / A | Regression / Control Group
Non-Controllable Load Resources providing Responsive Reserve Service -- Under Frequency Relay Type | LR-RRS (UFR Type) | Reserve | Active | None | 100 kW | 100 kW | No | Mandatory | Reliability | Operational Procedure or Automatic Response | 50% of total RRS procurement | N / A | N / A | N / A | Scheduled Interval (hourly) | Scheduled Interval (hourly) | Telemetry | http://www.ercot.com/services/programs/load/ |  |  |  | Resource Entity | Competitive Retailer or Non-Opt-In Entity (not relevant to DR) | QSE | QSE | TDSP | TDSP | Electronic File Submission | Web Page [MIS] / XML Notification [MIS] | Verbal Dispatch Instruction & XML Message / Under-Freq. Relay Trip | ICCP | EDI Transaction | None | 10 Minutes (Verbal) 30 Cycles (Relay) | As Dispatched / Recalled | 3 Hours | Yes | ± 3 % | 2 Seconds | Multiple Data Points including UFR Status and Breaker Status | ICCP | N / A | N / A | Yes | ± 2 % | 5% relative to NIST Atomic Clock | MW Accuracy: PUCT Subst. R. 25.121 referencing ANSI C12; UFRs must be set no lower than 59.7 Hz and must be set to trip for a frequency drop of no more than 20 cycles | Monthly | 15 Minutes | Standard VEE by meter-reading entity | N / A | LR-RRS (NCLR)
Controllable Load Resources providing Responsive Reserve Service | LR-RRS (CLR Type) | Reserve | 2014-06-01 | None | 100 kW | 100 kW | No | Mandatory | Reliability | Operational Procedure or Automatic Response | N / A | N / A | N / A | N / A | Scheduled Interval (hourly) | Scheduled Interval (hourly) | Telemetry | http://www.ercot.com/services/programs/load/ |  |  |  | Resource Entity | Competitive Retailer or Non-Opt-In Entity (not relevant to DR) | QSE | QSE | TDSP | TDSP | Electronic File Submission | Web Page [MIS] / XML Notification [MIS] | Governor-type Response & Automatic System Dispatch / Verbal Dispatch Instruction & XML Message | ICCP | EDI Transaction | None | Continuous primary frequency response, similar to generator governor action; and 10 minutes (1 minute to release capacity to SCED) | As Dispatched / Following SCED Base Points until Recalled | N / A | Yes | ± 3 % | 2 Seconds | Multiple Data Points | ICCP | Yes | N / A | Yes | ± 2 % | 5% relative to NIST Atomic Clock | MW Accuracy: PUCT Subst. R. 25.121 referencing ANSI C12; Governor-type response requirements described at http://www.ercot.com/services/programs/load/ | Monthly | 15 Minutes | Standard VEE by meter-reading entity | N / A | ERCOT-BPD and 1 of the following for qualification to provide Reserves: ERCOT-Regression / ERCOT-Mid 8 of 10 / ERCOT-Matching Day Pair / ERCOT Control Group
Controllable Load Resources providing Non-Spinning Reserve Service | CLR-Non-Spin | Reserve | 2014-06-01 | None | 100 kW | 100 kW | Yes | Mandatory | Reliability | Operational Procedure | N / A | N / A | N / A | N / A | Scheduled Interval (hourly) | Scheduled Interval (hourly) | Telemetry | http://www.ercot.com/services/programs/load/ |  |  |  | Resource Entity | Competitive Retailer or Non-Opt-In Entity (not relevant to DR) | QSE | QSE | TDSP | TDSP | Electronic File Submission | Web Page [MIS] / XML Notification [MIS] | XML Message | ICCP | EDI Transaction | None | 30 minutes (20 minutes to release capacity to SCED) | As Dispatched / Following SCED Base Points until Recalled | N / A | Yes | ± 3 % | 2 Seconds | Multiple Data Points | ICCP | N / A | N / A | Yes | ± 2 % | 5% relative to NIST Atomic Clock | MW Accuracy: PUCT Subst. R. 25.121 referencing ANSI C12. | Monthly | 15 Minutes | Standard VEE by meter-reading entity | N / A | ERCOT-BPD and 1 of the following for qualification to provide Reserves: ERCOT-Regression / ERCOT-Mid 8 of 10 / ERCOT-Matching Day Pair / ERCOT Control Group
Controllable Load Resources providing Regulation Service | CLR-Reg | Regulation | Active | None | 100 kW | 100 kW | No | Mandatory | Reliability | Automatic Response | N / A | N / A | N / A | N / A | Scheduled Interval (hourly) | Scheduled Interval (hourly) | Telemetry | http://www.ercot.com/services/programs/load/ |  |  |  | Resource Entity | Competitive Retailer or Non-Opt-In Entity (not relevant to DR) | QSE | QSE | TDSP | TDSP | Electronic File Submission | Web Page [MIS] / XML Notification [MIS] | Governor-type Response & Automatic Generation Control-type dispatch | ICCP | EDI Transaction | None | Effectively Immediate | Primary Frequency Response Continuous / AGC as Dispatched / Recalled | N / A | Yes | ± 3 % | 2 Seconds | Multiple Data Points | ICCP | Yes | N / A | Yes | ± 2 % | 5% relative to NIST Atomic Clock | MW Accuracy: PUCT Subst. R. 25.121 referencing ANSI C12; AGC and Governor-type response requirements described at http://www.ercot.com/services/programs/load/ | Monthly | 15 Minutes | Not Applicable to Regulation Service | N / A | CLR-Regulation
Controllable Load Resources providing Energy via SCED Dispatch | CLR - Energy Only | Energy | 2014-06-01 | None | 100 kW | 100 kW | Yes | Mandatory | Economic | Base Point Instruction when Energy Price ≥ Energy Bid Price | N / A | N / A | N / A | N / A | Any SCED-dispatched Intervals | Any Intervals with Active Bids in SCED | Telemetry | http://www.ercot.com/services/programs/load/ |  |  |  | Resource Entity | Competitive Retailer or Non-Opt-In Entity (not relevant to DR) | QSE | QSE | TDSP | TDSP | Electronic File Submission | Web Page [MIS] / XML Notification [MIS] | ICCP | ICCP | EDI Transaction | None | 5 minutes | 5 minutes | N / A | Yes | ± 3 % | 2 Seconds | Multiple Data Points | ICCP | N / A | N / A | Yes | ± 2 % | 5% relative to NIST Atomic Clock | MW Accuracy: PUCT Subst. R. 25.121 referencing ANSI C12. | Monthly | 15 Minutes | Standard VEE by meter-reading entity | N / A | CLR-BPD

## Performance Evaluation
PERFORMANCE EVALUATION METHODS |  | Baseline Information |  |  |  |  | Event Information |  |  |  | Special Processing
NAME (Cross-Reference to previous tab) | Performance Evaluation Type (NAESB Standards) | Baseline Window | Calculation Type | Exclusion Rules | Baseline Adjustments | Adjustment Window | Use of Real-Time Telemetry | Use of After-The-Fact Metering | Performance Window | Measurement Type | Highly-Variable Load Logic | On-Site Generation Requirements
Regression | Baseline Type-I | 12+ months of historical data | Model built using historical meter data | None | Event day adjustment (scalar based on load point) | Deployment minus 3 Hours (2 Hour Duration) | No | Yes | Sustained Response Period | 15-minute Interval Data Recorder compared to model | None | None (On-site generation is not prohibited but performance is measured via Load reduction)
Middle 8-of-10 | Baseline Type-I | 10 most recent like days (weekday vs. weekend/holiday) | Average | Exclude highest and lowest of the 10 most recent like days | Event day adjustment (scalar based on load point) | Deployment minus 3 Hours (2 Hour Duration) | No | Yes | Sustained Response Period | 15-minute Interval Data Recorder compared to model | None | None (On-site generation is not prohibited but performance is measured via Load reduction)
Matching Day Pair | Baseline Type-I | 12+ months of historical data | Model built using best matching event day and day preceding event day from prior 12 months | None | Event day adjustment (scalar based on load point) | Deployment minus 3 Hours (2 Hour Duration) | No | Yes | Sustained Response Period | 15-minute Interval Data Recorder compared to model | None | None (On-site generation is not prohibited but performance is measured via Load reduction)
Control Group | Baseline Type-I | N / A | Compare actual metered Load to control group sample average. | None | None | None | No | Yes | Sustained Response Period | 15-minute Interval Data Recorder compared to Control Group | None | None
Alternate Baseline | Maximum Base Load | N / A | N / A | N / A | N / A | N / A | No | Yes | Sustained Response Period | 15-minute Interval Data Recorder compared to model | This model is specifically designed for highly variable loads | None (On-site generation is not prohibited but performance is measured via Load reduction)
LR-RRS (NCLR) | Meter Before / Meter After | 5 Minutes | Compare actual telemetered Load to 5-minute average telemetered Load prior to event | None | None | None | Yes | Yes | Sustained Response Period | Telemetry (2-second) backed by 15-minute IDR meter data | None | None (On-site generation is not prohibited but performance is measured via Load reduction)
CLR-Regulation | Meter Before / Meter After | 4 Seconds | Compare actual telemetered Load to dispatched set point | None | None | None | Yes | No | Any hours obligated in Regulation-Up or Regulation-Down Service | Telemetry (2-second) | None | None
CLR-BPD (Base Point Deviations) | (ERCOT-specific real-time evaluation) | N / A | Compare telemetered load to SCED base point instructions. | None | None | None | Yes | Yes (for telemetry validation) | Any SCED Intervals (maximum 5 minutes each) in which the Resource is active in SCED | Telemetry (2-second) | None | None