## Slide 1
ERCOT Under Frequency Load Shed Testing
May 2015

## Slide 2: Time line for 2014 UFLS Survey
Below is a list of dates and activities reflecting the timeline and coordination of the 2014 survey:
04/10/2014 - ERCOT email notification sent by Client Services to TSP/DSP Authorized Representatives
04/23/2014 - ERCOT announcement of survey timeline and effort to OWG
05/13/2014 - Survey test day
06/13/2014 - Survey results due back to ERCOT
September/October- Results compiled and being reported to OWG/ROS/TAC

## Slide 3: Results of 2014 UFLS Survey
The results of the requirement were successful and are reflected below:
Frequency response block | Minimum Requirement | Survey measurement
Block 1 response at 59.3 | 5% | 6.7%
Block 2 response at 58.9 | 10% | 11.3%
Block 3 response at 58.5 | 10% | 11.8%
Total | 25% | 29.8%
ERCOT Reliability and Compliance contacted several participants to request that the 5%, 10%, 10% breakdown be adhered to with reconfiguration of loads. Some participants met the 25% total but had more load in the 5% or one of the 10% brackets and not quite 10% in the other bracket

## Slide 4: UNDER FREQUENCY LOAD SHED TESTING FOR 2015
ERCOT is proposing an UNDER FREQUENCY LOAD SHED TEST be scheduled for 11:00 May 12, 2015.
The objective of the test is meet the requirements of ERCOT Nodal Operating Guides 2.6.1 (1) and (2)
ERCOT will require each entity to have the load separated into 5%, 10%, and 10%, blocks as prescribed in OG 2.6.1(1) with a minimum of 25% of the entities’ load behind UFLS relays, as shown on the following slide .

## Slide 5
2.6.1
Automatic Firm Load Shedding
(1)
At least 25% of the ERCOT System Load that is not equipped with high
-
set under
-
frequency relays shall be equipped at all times with provisions for automatic under
-
frequency load shedding. The und
er
-
frequency relays shall be set to provide
L
oad
relief as follows:
Frequency Threshold
Load Relief
59.3 Hz
5% of the ERCOT System Load
(Total 5%)
58.9 Hz
An additional 10% of the ERCOT System Load
(Total 15%)
58.5 Hz
An additional 10% of the ERCOT Syst
em Load
(Total 25%)
UNDER FREQUENCY LOAD SHED TESTING FOR 2015

## Slide 6
UNDER FREQUENCY LOAD SHED TESTING FOR 2015
ERCOT proposed testing schedule
February 19, 2015 present to OWG
March 5, 2015 present to ROS
April 1, 2015 ERCOT email notification to be sent by Client Service to TSP/DSP Authorized Representatives
May 12, 2015 11:00 AM survey test time and day
June 12, 2015 Survey results due back to ERCOT
Compile results and report to OWG/ROS/TAC August/October 2015

## Slide 7
Registered Entity |  |  |  |  |  |  |  |  |  | 
Date/Time of Survey | 5/12/2015, 11:00 AM |  |  |  |  |  |  |  |  | 
Size and location of customer load, or percentage of connected load, to be interrupted. |  |  | Frequency set points. |  |  |  |  |  |  | Any other schemes that are part of or impact the UFLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, and Special Protection Systems. Also please indicate any other ERCOT-registered Transmission/Distribution Service Providers (TDSPs) whose load is represented by your company in this survey
 |  |  | Block 1 |  | Block 2 |  | Block 3 |  |  | 
 |  |  | 5% minimum |  | 10% minimum |  | 10% minumim |  |  | 
 |  |  | 59.3 Hz |  | 58.9 Hz |  | 58.5 Hz |  |  | 
Load Area | Total Area Load (MW) |  | Load Dropped for Block 1 (MW) | % Load Dropped for Block 1 | Load Dropped for Block 2 (MW) | % Load Dropped for Block 2 | Load Dropped for Block 3 (MW) | % Load Dropped for Block 3 |  | Comments
Total | 0 |  | 0 | 0.0% | 0 | 0.0% | 0 | 0.0% |  | 
 |  |  |  |  | Total percentage |  |  |  |  | 
 |  |  |  |  | #DIV/0! |  |  |  |  | 

## Slide 8: UNDER FREQUENCY LOAD SHED TESTING FOR 2015
Any Suggestions
and /or
Questions