## Slide 1
2014 Loss of Load Probability Assessment for NERC
April, 2015

## Slide 2: Outline
Background
Modeling Assumptions
Multi-zone Study Topology
Probabilistic Modeling Methodology
Results

## Slide 3: Background
The study fulfills the NERC requirement to perform a Probabilistic Risk Assessment in association with the annual Long Term Reliability Assessment (LTRA).
Purpose of the study is to derive reliability metrics including Expected Unserved Energy (EUE) and Loss of Load Hours (LOLH) for the years 2016 and 2018.
The study is not intended to determine a target or minimum planning reserve margin such as required in the Protocols.
Adopted the modeling framework and assumptions used for the Brattle EORM study
  Modeling performed by Astrape Consulting using their reliability analysis and hourly production cost system, SERVM (Strategic Energy & Risk Valuation Model)

## Slide 4: General Assumptions
Loads/resources based on May 2014 CDR
Energy-Limited Resource Modeling
  PUNS, Demand Response, Price-responsive Demand (PRD), Hydro all modeled based on January 2014 EORM Study methodology; however, capacities were updated. Historical market prices and response magnitudes were used to develop an appropriate supply curve for PUNs and PRD classes of resources.
  Wind/PV modeled with hourly profiles based on weather year
Notes: PRD – Price Responsive Demand

## Slide 5: Multi-zone Study Topology
*The Other/Houston transfer capability was increased to 5,191MW for the 2018 study year.
Notes: Load and generation capacity modeled for external regions are based on publically available data. The load forecast varies with weather years.

## Slide 6: Probabilistic Modeling Methodology
Multi-Weather-Year Analysis
  11 Weather Years (2002-2013 excluding 2008); 2011 given 1% chance of occurrence with all other years given equal probability
    Load: synthetic load shapes representing historical weather
    Hydro: historical monthly hydro energies applied
    Wind/Solar: synthetic profiles representing historical weather

## Slide 7: Probabilistic Modeling Methodology
Load Forecast Error Multipliers | Probability %
0.96 | 7.9%
0.98 | 24%
1 | 36%
1.02 | 24%
1.04 | 7.9%
Load Growth Uncertainty and Probability
  5 Economic Load Growth Multipliers (0.96, 0.98, 1, 1.02, 1.04)

## Slide 8: Probabilistic Modeling Methodology
Generator Outage
  Full, partial, and maintenance outages based on five years of historical NERC GADS (Generating Availability Data System) data
  100 Monte Carlo unit outage draws for each load scenario
Total Monte Carlo simulations for each scenario = 11 load shapes * 5 load forecast error multipliers * 100 draws = 5,500 runs of hourly chronological unit commitment and economic dispatch for each study year

## Slide 9: Results
 | LOLH | EUE | EUE/Net Energy for Load
 | hours/yr | MWh | ppm
ERCOT_Aggregated | 0.32 | 251.98 | 0.72
Other | 0.06 | 79.70 | 
Houston | 0.08 | 57.62 | 
Valley | 0.29 | 114.66 | 
 | LOLH | EUE | EUE/Net Energy for Load
 | hours/yr | MWh | ppm
ERCOT_Aggregated | 0.34 | 285.59 | 0.79
Other | 0.09 | 134.87 | 
Houston | 0.04 | 25.59 | 
Valley | 0.32 | 125.13 | 
2016
2018
Range of EUE/Net Energy for load is 0 - 18.74 ppm
Range of LOLH is 0 - 5.88 hours/yr

## Slide 10: Appendix -- Transfer Capability Analysis

## Slide 11: Houston Transfer Capability Analysis
Two 2013 RTP cases used to estimate the interface limits
  2016 SE summer peak case
  2018 SE summer peak case with the Limestone-Gibbons Creek-Zenith 345 kV double circuit project
AC Transfer analysis under N-1 was performed to estimate the transfer limits into Houston for the 2016 and 2018 cases
  Measured the transfer limit (the sum of pre-contingency flows) on the major 345 kV import path into Houston at the thermal violation
Then, the interface limits between the bubbles modeled in the 2014 LOLP study were estimated by subtracting the MW amount of the STP units from the AC transfer limit since the LOLP study assumed the STP units inside the Houston bubble zone.

## Slide 12: Houston Transfer Capability Analysis
Thermal overload is more limiting than Voltage stability
About 45 key contingencies were tested, which were identified as critical contingencies during the Houston Import Project RPG review.
Case | Limit Due to Thermal Overload |  |  | 
 | Limiting Contingency | Limiting Element | AC Transfer Limits into Houston (MW) | Estimated Interface Limits of Houston Bubble Zone for the 2014 LOLP study (AC Transfer Limit - STP Capacity)
2016 SE Case | Singleton-Tomball & Roans-Kuykendahl | Singleton-Zenith 345 kV lines | 5628 | 2904
2018 SE Case | Singleton-Tomball & Roans Prairie-Bobville | Singleton-Zenith 345 kV lines | 7915 | 5191

## Slide 13: Valley Transfer Capability Analysis
AC Transfer analysis under N-1 was performed to estimate the transfer limits into the Valley under expected 2017 summer peak conditions
  The 2017 SE summer peak case from the 2012 RTP was used to estimate the interface limits
  Measured the transfer limit (the sum of pre-contingency flows) on all 345 kV and 138 kV import paths into the Valley
Transfer Capability Analysis:
  Thermal overload was observed to be more limiting than Voltage stability under N-1