## Slide 1
Real-Time Transmission Congestion Management & Market Effects
Chad Thompson, Manager, Operations Support, ERCOT
Jeff Gilbertson, Sr Market Operations Analyst, ERCOT

## Slide 2: Objectives
Identify what defines a constraint in the ERCOT system.
Identify which ERCOT application dispatches generation to resolve constraint overloads.
Identify the types of Constraint Management Plans as detailed in the ERCOT Nodal Protocols.

## Slide 3: Objectives
Identify the time-frame in which all Congestion Management Plans are intended to resolve loading below Emergency Ratings.
Identify where Congestion Management Plans are posted to the Market
Identify the ERCOT application whose goal is to minimize generation costs while also respecting transmission constraints.

## Slide 4: Objectives
Identify when the transmission network is “invisible” to Security Constrained Economic Dispatch (SCED).
Identify the condition when a constraint Shadow Price is zero dollars ($0)

## Slide 5
Congestion Management:
Real-Time
Chad Thompson

## Slide 6: Congestion Basics
Equipment Ratings
  Normal/Continuous
  Emergency/2-Hour
  Loadshed/15-Minute
Dynamic Line Ratings
  Temperature-adjusted based on ambient temperature
  TSPs submit a static ratings table that is tied to the ERCOT weather forecast
  TSPs also have the option to submit a rating via ICCP telemetry – MVA, Amps, Temperature
All Autotransformers and Transmission lines have 3 ratings in the model; some may be the same

## Slide 7: Congestion Basics

## Slide 8: Congestion Basics
ERCOT Operates to “N-1” Contingency Criteria
Contingencies include the loss of Autotransformers, Transmission Lines and Generation Units
N-1 congestion *generally* based on the Emergency Rating
  Base Case congestion based on the Normal Rating
What is a constraint?
  An N-1 contingency and overloaded transmission element pair
  A base case, or real-time transmission element overload

## Slide 9: Constraint Management
How are constraints identified?
  ERCOT executes its State Estimator and performs a Real-Time Contingency Analysis (RTCA) every 5 minutes
  RTCA produces a list of constraints which is updated every time it executes
How are constraints used?
  ERCOT executes a Security Constrained Economic Dispatch (SCED) market every 5 minutes
  SCED dispatches generation to resolve constraint overloads
  Only those constraints passed from RTCA into SCED are considered in congestion management

## Slide 10: Constraint Management
Does this mean that not all constraints are activated?
What are the criteria for activating constraints?
  Correct modeling, telemetry, & solution
  Not redundant
  Not Private Use Network Equipment
  2 % or greater Generator Shift Factor*
  Constraint Management Plans (CMP)
    “Only those constraints passed from RTCA into SCED are considered in congestion management”

## Slide 11: Constraint Management
How can I find out why a constraint was not activated?
  MIS Secure Area under Grid  Transmission  Real-Time Operations

## Slide 12: Constraint Management
What’s a Constraint Management Plan?
  A transmission switching action that is developed to ensure overall grid reliability in the event a given contingency occurs
  CMPs are intended to supplement SCED, while maximizing transmission capacity when possible

## Slide 13: Constraint Management
What’s a Constraint Management Plan?
  Currently 4 types of CMPs as detailed in Section 2.1 Definitions of the ERCOT Nodal Protocols
    Mitigation Plan
    Pre-Contingency Action Plan (PCAP)
    Remedial Action Plan (RAP)
    Temporary Outage Action Plan (TOAP)
  All CMPs are intended to resolve loading to below Emergency Ratings, with restoration of normal operating conditions within two hours

## Slide 14: Constraint Management
Mitigation Plan
  Post-contingency actions
  May include load shed
  Constraints managed to their Emergency Ratings
  Not Modeled in ERCOT Systems
Pre-Contingency Action Plan (PCAP)
  Pre-contingency actions
  Do not include load shed
  Constraints managed to their Emergency Ratings
  Not Modeled in ERCOT Systems

## Slide 15: Constraint Management
Remedial Action Plan (RAP)
  Post-contingency actions
  Do not include load shed
  Constraints managed to their 15-Minute Ratings
  Modeled in ERCOT Systems
Temporary Outage Action Plan (TOAP)
  Post-contingency actions
  May include load shed
  Constraints managed to their Emergency Ratings
  Not Modeled in ERCOT Systems
  “Mitigation Plan for the duration of an outage”

## Slide 16: Constraint Management
Contingency Details
Overloaded Elements
Corrective Actions
Additional Details
Administrative Details

## Slide 17: Constraint Management
Where are CMPs Posted?
  MIS Secure Area under Grid  Long-Term Planning  Special Protection Systems and Remedial Action Plans

## Slide 18
Congestion Management:
Market Effects
Jeff Gilbertson

## Slide 19: Topics Covered
Security Constrained Economic Dispatch (SCED) inputs and outputs
Constraint Scenarios
Data relationships

## Slide 20: SCED Inputs and Outputs
Security Constrained Economic Dispatch (SCED)
  Goal: Minimize generation cost while also respecting transmission constraints (“security constrained”)
Inputs
  Generation to be Dispatched (GTBD)
  Generator offer curves
  Generator limits (Low/High Dispatch Limits)
  Generator current power output
  Active transmission constraints (cont’d)

## Slide 21: SCED Inputs and Outputs
Active transmission constraints
  Contingency and monitored element pair names
  Monitored element (“constraint”) post-contingency flow
  Constraint limit
  Maximum shadow price
  Resource shift factors
This is all SCED knows about the ERCOT transmission network!

## Slide 22: SCED Inputs and Outputs
Transmission Constraint Shadow Price (SCED output)
  Change in cost of system dispatch for a 1 MW change in monitored element limit
Maximum Shadow Price (SCED input)
  Prevents wide price spread when constraint is not resolvable or very difficult to resolve
BASE CASE | $5,000 |  | 138 kV | $3,500
345 kV | $4,500 |  | 69 kV | $2,800

## Slide 23: SCED Inputs and Outputs
Resource Shift Factor
  Change of flow on monitored element due to 1MW change of output of Resource
    Value range: -1 to 1
    Positive shift factor : flow on monitored element increases as generation increases
    Negative shift factor: flow on monitored element decreases as generation increases

## Slide 24: SCED Inputs and Outputs
Resource Shift Factor
  Magnitude of shift factor indicative of number of paths Resource output has to flow
  Greater magnitude shift factors:
    Resource located on a radial path from monitored element; and/or
    Resource located close to monitored element

## Slide 25: SCED Inputs and Outputs
Outputs
  Resource Base points (sent only to Resource)
  Locational Marginal Prices (LMPs) – cost to serve additional 1MW of load at a location
    Consistent with base points
      LMP higher than offer curve price, base point instructs resource to increase output
      LMP lower than offer curve price, base point instructs resource to decrease output
  Constraint solution flow

## Slide 26: SCED Inputs and Outputs
Where is SCED constraint data posted?
  MIS Secure Area under Markets  Real-Time Market

## Slide 27: Constraint Scenarios
No active constraints
  Transmission network “invisible” to SCED
  Dispatch is like using an “offer stack”
    Resources dispatched to meet GTBD
    Less expensive resources fully dispatched to High Dispatch Limit (HDL)
    More expensive resources dispatched to Low Dispatch Limit (LDL)
    Resources in between LDL and HDL are “marginal” and set one system-wide Locational Marginal Price (LMP)
  No congestion costs

## Slide 28: Constraint Scenarios
Active constraint(s) that are not binding in SCED
  By dispatching inexpensive resources first, the resulting post-contingency flow on constraints is less than limit
  No congestion costs; one system-wide LMP
  Again, dispatch is like using an “offer stack”

## Slide 29: Constraint Scenarios
Active constraint(s) that are binding in SCED
  Dispatch based on economics alone would result in post-contingency flow above transmission limit
  More expensive resources must be dispatched higher and less expensive resources dispatched lower in order to respect the limit
  Flow change on constraint is (solution resource output – initial resource output) * shift factor for each resource
  Power balance must be maintained, so resource level adjustments must balance each other out

## Slide 30: Constraint Scenarios
Active constraint(s) that are binding in SCED
  Binding constraints have a non-zero “shadow price”
  The shadow price is the price sensitivity of the transmission constraint
  If transmission limit was 1MW lower, what would that mean in terms of cost?
    Since we are already starting at the most economic solution at the limit, the less expensive resources would need to produce less and more expensive resources would need to produce more
  Results in different LMPs throughout the system

## Slide 31: Constraint Scenarios
Active constraint(s) that are violated in SCED
  Transmission limit is NOT respected
  Occurs because:
    there are no resources that can be dispatched to resolve the constraint
    the cost to resolve the constraint is very high
  Remember, flow is post-contingency flow. Actual monitored element flow is not allowed to go above limit.

## Slide 32: Constraint Scenarios
Conditions for transmission congestion
  At least one transmission constraint is active
  SCED dispatch results in post-contingency flow on the monitored element at or above the constraint limit

## Slide 33: Data Relationships
Relationship between constraint flow and constraint shadow price
Scenario | Flow | Shadow Price
Not binding | < limit | $0
Binding | = limit | > $0 and < Max SP
Irresolvable/ violated | > limit | Max Shadow Price

## Slide 34: Data Relationships
Relationship between shadow price, shift factors, and LMP
LMP = System Lambda - (shift factor * shadow price) - (shift factor * shadow price)…
(shift factor * shadow price) subtracted for each constraint

## Slide 35: Data Relationships
Example:
System Lambda is $50
Resource A has a shift factor of 0.2 to constraint A
Constraint A shadow price is $100
LMP = System Lambda – (shift factor * shadow price)
LMP = $50 – (0.2 * $100) = $50-$20 = $30

## Slide 36
Questions?

## Slide 37: Questions
A constraint in the ERCOT system is defined as
  An N-1 contingency and overloaded transmission element pair
  A base case, or real-time transmission element overload
  All of the above

## Slide 38: Questions
Which ERCOT application dispatches generation to resolve constraint overloads?
  SCED
  RTCA
  VSAT
  VSS

## Slide 39: Questions
Which of the following Constraint Management Plans are detailed in the ERCOT Nodal Protocols:
  Mitigation Plan (MP)
  Pre-Contingency Action Plan (PCAP)
  Remedial Action Plan (RAP)
  All of the above

## Slide 40: Questions
Within what time-frame which all Congestion Management Plans are intended to resolve loading below Emergency Ratings?
  2-hours
  4-hours
  24-hours
  Doesn’t matter as long as resolved

## Slide 41: Questions
Where are Congestion Management Plans posted to the Market?
  MIS Restricted
  MIS Public
  MIS General
  MIS Secure

## Slide 42: Questions
Which ERCOT application’s goal is to minimize generation costs while also respecting transmission constraints?
  GTBD
  RTCA
  SCED
  SASM

## Slide 43: Questions
Under what condition is the transmission network “invisible” to Security Constrained Economic Dispatch (SCED)?
  No Active Constraints
  Active Constraints
  Binding Constraints
  Non-Binding Constraints

## Slide 44: Questions
Under what condition would a Shadow Price of zero dollars ($0) be calculated?
  Constraint flow is < limit
  Constraint flow is = limit
  Constraint flow is > limit
  None of the above