## Slide 1
Synchrophasors
Advanced Network Applications
ERCOT Operations Training Seminar
2015

## Slide 2: Objectives
Upon completing this course, you will be able to:
Identify the technology used for Synchrophasors and how Synchrophasor Data is different from traditional SCADA
Recognize the benefits of Synchrophasor Technology in managing the power grid
Identify how Synchrophasor Data is used to detect oscillations in the system
Identify how Synchrophasor Data is used in Event Analysis
Identify generator model validation methodology using Synchrophasor Data

## Slide 3: What is a Voltage Phasor ?
*Source: Electric Power Group
http://www.animations.physics.unsw.edu.au/jw/phasor-addition.html#sub5

## Slide 4: Power Flow Function of Phase Angle Difference
*Source: Electric Power Group

## Slide 5: Phasor Technology Infrastructure
*Source: Electric Power Group

## Slide 6: Phasor Vs. SCADA Measurements
*Source: Electric Power Group
ATTRIBUTE | SCADA | SYNCHROPHASORS
Resolution | 1 sample every 2-4 seconds | 10-60 samples per second
Measured Quantities | Magnitude Only | Magnitude & Phase Angle
Time Synchronization | No | Yes
Focus | Local utility monitoring & control | Wide area monitoring & control

## Slide 7: Observability - SCADA vs. PMUs
*Source: Electric Power Group

## Slide 8: Observability - SCADA vs. PMUs

## Slide 9: Objectives
Upon completing this course, you will be able to:
Identify the technology used for Synchrophasors and how Synchrophasor Data is different from traditional SCADA
Recognize the benefits of Synchrophasor Technology in managing the power grid
Identify how Synchrophasor Data is used to detect oscillations in the system
Identify how Synchrophasor Data is used in Event Analysis
Identify generator model validation methodology using Synchrophasor Data

## Slide 10: Phasor Technology Uses
*Source: Electric Power Group

## Slide 11: Major Blackout Events – Lessons Learned
*Source: Electric Power Group

## Slide 12: Major Blackout Events – Lessons Learned
*Source: Electric Power Group

## Slide 13: How Synchrophasors Could Have Helped
Synchrophasors allow system operators to monitor angle differences on defined interfaces
Alarms may be set to alert operators of growing angle differences and grid stress
Operators may take action by re-dispatching generation or shedding load to reduce angle difference

## Slide 14: The ERCOT Synchrophasor (PMU) Project

## Slide 15: Number of PMUs in CCET Project (as of Nov 2014)
Total 76 PMUs @ 35 Locations
  AEP: 54
  ONCOR: 17
  Sharyland: 5
Chart: PMUs Installed
| 40787 | 40817 | 40848 | 40878 | 40909 | 40940 | 40969 | 41000 | 41030 | 41061 | 41091 | 41122 | 41153 | 41183 | 41214 | 41244 | 41275 | 41306 | 41334 | 41365 | 41395 | 41426 | 41456 | 41487 | 41518 | 41548 | 41579 | 41609 | 41640 | 41671 | 41699 | 41730 | 41760 | 41791 | 41821 | 41852 | 41883 | 41913 | 41944
# of PMUs | 12 | 12 | 12 | 12 | 12 | 13 | 15 | 15 | 16 | 18 | 22 | 26 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 29 | 34 | 39 | 42 | 48 | 52 | 56 | 61 | 67 | 69 | 69 | 69 | 69 | 69 | 72 | 76 | 76 | 76

## Slide 16: The Synchrophasor Data Communication Network

## Slide 17: ERCOT ROS Synchrophasor Task Force
PMTF Deliverables
Synchrophasor Technology Assessment
  Addresses the major questions posed to the PMTF by ROS
  Includes an overall summary of key recommendations
Synchrophasor Communication Handbook
  Provides guidance for connecting new PMUs to ERCOT’s network
Draft Nodal Operating Guide Section 6 language
  Recommends language to formalize the placement and usage of PMUs within ERCOT
  Status of NOGRR

## Slide 18: How Synchrophasor Data Is Being Used
System Oscillations
Event Analysis
Generator Model Validation/Tuning

## Slide 19: Objectives
Upon completing this course, you will be able to:
Identify the technology used for Synchrophasors and how Synchrophasor Data is different from traditional SCADA
Recognize the benefits of Synchrophasor Technology in managing the power grid
Identify how Synchrophasor Data is used to detect oscillations in the system
Identify how Synchrophasor Data is used in Event Analysis
Identify generator model validation methodology using Synchrophasor Data

## Slide 20: Oscillation Detection & Damping

## Slide 21: RTDMS Dashboard

## Slide 22: Characterizing Oscillations - Frequency and Damping
*Source: Electric Power Group
Well Damped: 5%
or Higher Damping
Poorly Damped:
3% - 5% Damping
Growing Oscillations:
Less than 3% or Negative Damping

## Slide 23: Example of Oscillation Event
RTDMS system was used to detect oscillations and
take corrective measures to mitigate them
ERCOT operations contacted the plant operator at the
Wind Farm to determine the cause of the oscillations
It was discovered that some updates were made to the
settings for the system controller which matched the
time of initial observation of the oscillations
After ERCOT informed the Wind Farm Operations about the oscillations, they pulled back the updates which stopped the oscillations. After that, no oscillations were observed even when the plant was generating above 50 MWs

## Slide 24: RTDMS Oscillation Demo

## Slide 25: Objectives
Upon completing this course, you will be able to:
Identify the technology used for Synchrophasors and how Synchrophasor Data is different from traditional SCADA
Recognize the benefits of Synchrophasor Technology in managing the power grid
Identify how Synchrophasor Data is used to detect oscillations in the system
Identify how Synchrophasor Data is used in Event Analysis
Identify generator model validation methodology using Synchrophasor Data

## Slide 26: Event Analysis Reports
  Can be used to support (future) PRC-002-2 Disturbance monitoring and reporting requirements
Four metrics analyzed for each event with frequency dropping to 59.9 Hz and below
  System frequency and frequency excursion
    Location with largest frequency deviation
  System Voltage
    Location with the largest voltage swing
  Relative Angle (measured with respect to a reference PMU)
    Location with the largest relative angle swing
  Modes of small-signal oscillation
    Prony/HTLS Algorithm
The Phasor Grid Dynamics Analyzer (PGDA) application provided by the Electric Power Group (EPG) is used for this analysis.

## Slide 27: EPG’s Phasor Grid Dynamics Analyzer
Fig. 1 System Frequency Captured by the PMU’s

## Slide 28: EPG’s Phasor Grid Dynamics Analyzer
Fig. 2 Voltage magnitude measured by the PMU with largest voltage swing

## Slide 29: EPG’s Phasor Grid Dynamics Analyzer
Fig. 3 Relative Voltage angle measured by the PMU with largest angular swing

## Slide 30: EPG’s Phasor Grid Dynamics Analyzer
Fig. 4 Ring-down analysis
0.67 Hz mode
8.21% damping
Dominant Mode
Dominant mode

## Slide 31: Objectives
Upon completing this course, you will be able to:
Identify the technology used for Synchrophasors and how Synchrophasor Data is different from traditional SCADA
Recognize the benefits of Synchrophasor Technology in managing the power grid
Identify how Synchrophasor Data is used to detect oscillations in the system
Identify how Synchrophasor Data is used in Event Analysis
Identify generator model validation methodology using Synchrophasor Data

## Slide 32: Generator Model Validation
PMU’s can be used to satisfy model validation requirements set in NERC standards MOD-026-1 and MOD-027-1
PMU’s provide high accuracy measurements for comparison against simulation, which may be accomplished with unit online
Automation of the process using software tools greatly eases the workload associated with matching simulation models with measured response.
Result is a good dynamic model for a Generator/Excitation System that matches the actual equipment in the field and is validated through online testing

## Slide 33: Generator Model Validation
Post Event Analysis
  Re-create the oscillations as captured by the PMU using simulation tools such as MATLAB and Powertech Tools
  Identify the cause and solutions to mitigate the oscillations
Benchmarking of the tuned model using PMU data

## Slide 34: Generator Model Validation
Proposed tuning based on simulation studies

## Slide 35: Summary
What is Synchrophasor Technology
  Phasors and PMUs
  Difference between Synchrophasors and SCADA
Benefits of Synchrophasors
  Wide-Area Visualization
  Higher resolution than SCADA for better observability
  Provides ability to assess grid stress due to angle differences
  Allows for better dynamic modeling
Current Synchrophasor Deployment in ERCOT
  76 PMU’s installed in 35 locations
  Status of PMTF and NOGRR
Current Use Cases
  Oscillation Detection & Damping
  Event Analysis and Reporting
  Generator Model Validation

## Slide 36
Questions?

## Slide 37: Q&A
Question 1:
Which of the following statements regarding Synchrophasors and SCADA is correct:
  Synchrophasor Technology is a replacement for SCADA
  SCADA and Synchrophasors both have time synchronization with GPS
  SCADA has slow scan rates when compared to Synchrophasors
  SCADA and Synchrophasors are both capable of measuring voltage and current phase angles

## Slide 38: Q&A
Question 2:
Synchrophasor Technology is useful for the following:
  Wide area visualization
  Monitoring oscillations
  c) Assess grid stress
  d) All of the above

## Slide 39: Q&A
Question 3:
The following waveform indicates :
a) Well Damped Oscillations
b) Poorly Damped Oscillations
c) Growing Oscillations
d) None of the above
Time
Magnitude

## Slide 40: Q&A
Question 4:
For Post-Event Analysis, Synchrophasor Data can be used to:
  Locate the area with the largest frequency deviation
  Locate the areas with the largest voltage magnitude and angle swing
  Determine dominant modes of oscillations associated with the event
  All of the above

## Slide 41: Q&A
Question 5:
Synchrophasor Technology is useful for the following:
  a) Generator Model Validation
  b) To increase the generator output
  c) To improve generator efficiency
  To get maximum revenue from the generator