## Summary
Release Date: May 4, 2015
PRELIMINARY
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Fall 2015
SUMMARY
The ERCOT Region is expected to have sufficient installed generating capacity to serve forecasted peak demands in the upcoming fall season (October- November 2015).
For the fall season, expected new planned capacity additions include the gas-fired project, Ector County Energy Center G (341 MW fall rating, and formerly called Goldsmith Peakers), as well as 1,771 nameplate MW of wind with a peak average capacity contribution of 285 MW. The peak wind capacity was derived by applying the new methodology for peak average capacity percentages approved by the ERCOT Board of Directors in October 2014. These values are currently 12 percent for non-coastal resources and 56 percent for coastal resources.
Due to recent rainfall, the three R.W. Miller gas-fired steam units (fall capacity rating of 403 MW) previously on extended outage due to insufficient cooling water are now expected to be available for the fall season. Based on ERCOT's drought risk analysis, no other changes to unit capacities due to drought conditions are anticipated or reflected in the fall assessment. ERCOT will continue to monitor the potential effect of drought conditions on generation capacity.
At this time, ERCOT does not anticipate changes to available generation capacity for the fall season due to compliance with the Cross-State Air Pollution Rule (CSAPR) or Mercury and Air Toxics Standards (MATS). CSAPR came into effect on January 1, 2015, and the compliance deadline for the MATS rule for units that have not received compliance extensions is April 15, 2015. Confidential survey information gathered in March 2015 indicates that coal generators are expected to be compliant with CSAPR, and are either compliant with MATS or have received a one-year compliance extension. ERCOT continues to monitor implementation and consults with generation resource owners on their compliance plans for CSAPR, MATS and other environmental regulations.

## Scenarios
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Fall 2015 - Preliminary
Release Date: May 4, 2015
Forecasted Capacity and Demand
|  | Operational Resources (excluding wind), MW | 65624.5 | Based on current Seasonal Maximum Sustainable Limits reported through the unit registration process
|  | Switchable Capacity Total, MW | 3702 | Installed capacity of units that can interconnect with other Regions and are available to ERCOT
|  | less Switchable Capacity Unavailable to ERCOT, MW | -470 | Based on survey responses of Switchable Resource owners
|  | Mothball Resources, MW | 0 | Based on seasonal Mothball units plus Probability of Return responses of Mothball Resource owners
|  | Private Use Network Capacity Contribution, MW | 4433 | Average capability of the top 20 hours in the summer peak seasons for the past three years (2012-2014)
|  | Non-Coastal Wind Resources Capacity Contribution, MW | 1365.528 | Based on 12% of installed capacity for non-coastal wind resources per ERCOT Nodal Protocols Section 3.2.6.2.2
|  | Coastal Wind Resources Capacity Contribution, MW | 941.024 | Based on 56% of installed capacity for coastal wind resources per ERCOT Nodal Protocols Section 3.2.6.2.2
|  | RMR Resources to be under Contract, MW | 0 | No RMR Resources currently under contract
|  | Non-Synchronous Ties Capacity Contribution, MW | 371.4 | Average capability of the top 20 hours in the summer peak seasons for the past three years (2012-2014)
|  | Planned Resources (not wind) with signed IA and Air Permit, MW | 1131.1 | Based on in-service dates provided by developers of generation resources
|  | Planned Non-Coastal Wind with signed IA , MW | 320.28 | Based on in-service dates provided by developers of generation resources and 12% of installed capacity for non-coastal wind resources
|  | Planned Coastal Wind with signed IA , MW | 205.52 | Based on in-service dates provided by developers of generation resources and 56% of installed capacity for coastal wind resources
| [a] Total Resources, MW |  | 77624.352
| [b] Peak Demand, MW |  | 49709 | Fall peak forecast is based on normal weather conditions for 2002 – 2013
| [c] Reserve Capacity [a - b], MW |  | 27915.352
Range of Potential Risks
|  |  | Forecasted Summer Season Peak Load | Extreme Load / Typical Generation Outages | Extreme Load / Extreme Generation Outages
|  | Seasonal Load Adjustment |  | 8297 | 8297 | Based on a typical September peak occuring in early October
|  | Typical Maintenance Outages | 9216 | 9216 | 9216 | Based on historical average of planned outages for October through November weekdays (starting in 2010).
|  | Typical Forced Outages | 3286 | 3286 | 3286 | Based on historical average of forced outages for October through November weekdays (starting in 2010).
|  | 90th Percentile Forced Outages | 0 | 0 | 2999 | Based on historical forced outages using P90 expectation.
| [d] Total Uses of Reserve Capacity |  | 12502 | 20799 | 23798
| [e] Capacity Available for Operating Reserves (c-d), MW |  | 15413.352 | 7116.352 | 4117.352
Less than 2,300 MW indicates risk of EEA1

## Capacity
Unit Capacities - Fall
| UNIT NAME | GENERATION INTERCONNECTION PROJECT CODE | UNIT CODE | COUNTY | FUEL | ZONE | START YEAR | 2015
Operational Resources
4 | COMANCHE PEAK U1 |  | CPSES_UNIT1 | SOMERVELL | NUCLEAR | NORTH | 1990 | 1222
5 | COMANCHE PEAK U2 |  | CPSES_UNIT2 | SOMERVELL | NUCLEAR | NORTH | 1993 | 1209
6 | SOUTH TEXAS U1 |  | STP_STP_G1 | MATAGORDA | NUCLEAR | COASTAL | 1988 | 1318
7 | SOUTH TEXAS U2 |  | STP_STP_G2 | MATAGORDA | NUCLEAR | COASTAL | 1989 | 1325
8 | BIG BROWN U1 |  | BBSES_UNIT1 | FREESTONE | COAL | NORTH | 1971 | 606
9 | BIG BROWN U2 |  | BBSES_UNIT2 | FREESTONE | COAL | NORTH | 1972 | 602
10 | COLETO CREEK |  | COLETO_COLETOG1 | GOLIAD | COAL | SOUTH | 1980 | 660
11 | FAYETTE POWER U1 |  | FPPYD1_FPP_G1 | FAYETTE | COAL | SOUTH | 1979 | 603
12 | FAYETTE POWER U2 |  | FPPYD1_FPP_G2 | FAYETTE | COAL | SOUTH | 1980 | 603
13 | FAYETTE POWER U3 |  | FPPYD2_FPP_G3 | FAYETTE | COAL | SOUTH | 1988 | 444
14 | GIBBONS CREEK U1 |  | GIBCRK_GIB_CRG1 | GRIMES | COAL | NORTH | 1983 | 470
15 | J K SPRUCE U1 |  | CALAVERS_JKS1 | BEXAR | COAL | SOUTH | 1992 | 562
16 | J K SPRUCE U2 | 09INR0002 | CALAVERS_JKS2 | BEXAR | COAL | SOUTH | 2010 | 775
17 | J T DEELY U1 |  | CALAVERS_JTD1 | BEXAR | COAL | SOUTH | 1977 | 430
18 | J T DEELY U2 |  | CALAVERS_JTD2 | BEXAR | COAL | SOUTH | 1978 | 420
19 | LIMESTONE U1 |  | LEG_LEG_G1 | LIMESTONE | COAL | NORTH | 1985 | 831
20 | LIMESTONE U2 |  | LEG_LEG_G2 | LIMESTONE | COAL | NORTH | 1986 | 858
21 | MARTIN LAKE U1 |  | MLSES_UNIT1 | RUSK | COAL | NORTH | 1977 | 815
22 | MARTIN LAKE U2 |  | MLSES_UNIT2 | RUSK | COAL | NORTH | 1978 | 820
23 | MONTICELLO U3 |  | MNSES_UNIT3 | TITUS | COAL | NORTH | 1978 | 795
24 | OAK GROVE SES U1 | 09INR0006a | OGSES_UNIT1A | ROBERTSON | COAL | NORTH | 2010 | 840
25 | OAK GROVE SES U2 | 09INR0006b | OGSES_UNIT2 | ROBERTSON | COAL | NORTH | 2011 | 825
26 | OKLAUNION U1 |  | OKLA_OKLA_G1 | WILBARGER | COAL | WEST | 1986 | 650
27 | SAN MIGUEL U1 |  | SANMIGL_SANMIGG1 | ATASCOSA | COAL | SOUTH | 1982 | 391
28 | SANDOW U5 | 08INR0003 | SD5SES_UNIT5 | MILAM | COAL | SOUTH | 2010 | 600
29 | SANDY CREEK U1 |  | SCES_UNIT1 | MCLENNAN | COAL | NORTH | 2013 | 970
30 | TWIN OAKS U1 |  | TNP_ONE_TNP_O_1 | ROBERTSON | COAL | NORTH | 1990 | 158
31 | TWIN OAKS U2 |  | TNP_ONE_TNP_O_2 | ROBERTSON | COAL | NORTH | 1991 | 158
32 | W A PARISH U5 |  | WAP_WAP_G5 | FT. BEND | COAL | HOUSTON | 1977 | 659
33 | W A PARISH U6 |  | WAP_WAP_G6 | FT. BEND | COAL | HOUSTON | 1978 | 658
34 | W A PARISH U7 |  | WAP_WAP_G7 | FT. BEND | COAL | HOUSTON | 1980 | 577
35 | W A PARISH U8 |  | WAP_WAP_G8 | FT. BEND | COAL | HOUSTON | 1982 | 610
36 | A VON ROSENBERG 1 CTG 1 | 00INR0017 | BRAUNIG_AVR1_CT1 | BEXAR | GAS | SOUTH | 2000 | 155
37 | A VON ROSENBERG 1 CTG 2 | 00INR0017 | BRAUNIG_AVR1_CT2 | BEXAR | GAS | SOUTH | 2000 | 155
38 | A VON ROSENBERG 1 STG | 00INR0017 | BRAUNIG_AVR1_ST | BEXAR | GAS | SOUTH | 2000 | 170
39 | B M DAVIS CTG 3 | 09INR0038 | B_DAVIS_B_DAVIG3 | NUECES | GAS | COASTAL | 2010 | 161
40 | B M DAVIS CTG 4 | 09INR0038 | B_DAVIS_B_DAVIG4 | NUECES | GAS | COASTAL | 2010 | 161
41 | B M DAVIS STG 2 |  | B_DAVIS_B_DAVIG2 | NUECES | GAS | COASTAL | 1976 | 322
42 | BASTROP ENERGY CENTER CTG 1 | 01INR0021 | BASTEN_GTG1100 | BASTROP | GAS | SOUTH | 2002 | 157
43 | BASTROP ENERGY CENTER CTG 2 | 01INR0021 | BASTEN_GTG2100 | BASTROP | GAS | SOUTH | 2002 | 157
44 | BASTROP ENERGY CENTER STG | 01INR0021 | BASTEN_ST0100 | BASTROP | GAS | SOUTH | 2002 | 236
45 | BOSQUE COUNTY PEAKING CTG 1 | 00INR0018 | BOSQUESW_BSQSU_1 | BOSQUE | GAS | NORTH | 2000 | 157.2
46 | BOSQUE COUNTY PEAKING CTG 2 | 00INR0018 | BOSQUESW_BSQSU_2 | BOSQUE | GAS | NORTH | 2000 | 157.2
47 | BOSQUE COUNTY PEAKING CTG 3 | 00INR0018 | BOSQUESW_BSQSU_3 | BOSQUE | GAS | NORTH | 2001 | 159.5
48 | BOSQUE COUNTY PEAKING STG 4 | 00INR0028 | BOSQUESW_BSQSU_4 | BOSQUE | GAS | NORTH | 2001 | 83.3
49 | BOSQUE COUNTY PEAKING STG 5 | 08INR0046 | BOSQUESW_BSQSU_5 | BOSQUE | GAS | NORTH | 2009 | 196.6
50 | BRAZOS VALLEY CTG 1 | 01INR0031 | BVE_UNIT1 | FORT BEND | GAS | HOUSTON | 2003 | 168
51 | BRAZOS VALLEY CTG 2 | 01INR0031 | BVE_UNIT2 | FORT BEND | GAS | HOUSTON | 2003 | 168
52 | BRAZOS VALLEY STG 3 | 01INR0031 | BVE_UNIT3 | FORT BEND | GAS | HOUSTON | 2003 | 270
53 | CALENERGY (FALCON SEABOARD) CTG 1 |  | FLCNS_UNIT1 | HOWARD | GAS | WEST | 1987 | 77
54 | CALENERGY (FALCON SEABOARD) CTG 2 |  | FLCNS_UNIT2 | HOWARD | GAS | WEST | 1987 | 77
55 | CALENERGY (FALCON SEABOARD) STG 3 |  | FLCNS_UNIT3 | HOWARD | GAS | WEST | 1988 | 71
56 | CEDAR BAYOU CTG 4 |  | CBY4_CT41 | CHAMBERS | GAS | HOUSTON | 2009 | 168
57 | CEDAR BAYOU CTG 5 |  | CBY4_CT42 | CHAMBERS | GAS | HOUSTON | 2009 | 168
58 | CEDAR BAYOU STG 6 |  | CBY4_ST04 | CHAMBERS | GAS | HOUSTON | 2009 | 182
59 | COLORADO BEND ENERGY CENTER CTG 1 | 06INR0035b | CBEC_GT1 | WHARTON | GAS | SOUTH | 2007 | 84
60 | COLORADO BEND ENERGY CENTER CTG 2 | 06INR0035b | CBEC_GT2 | WHARTON | GAS | SOUTH | 2007 | 76
61 | COLORADO BEND ENERGY CENTER STG 1 | 06INR0035b | CBEC_STG1 | WHARTON | GAS | SOUTH | 2007 | 103
62 | COLORADO BEND ENERGY CENTER CTG 3 | 06INR0035a | CBEC_GT3 | WHARTON | GAS | SOUTH | 2008 | 75
63 | COLORADO BEND ENERGY CENTER CTG 4 | 06INR0035a | CBEC_GT4 | WHARTON | GAS | SOUTH | 2008 | 75
64 | COLORADO BEND ENERGY CENTER STG 2 | 06INR0035a | CBEC_STG2 | WHARTON | GAS | SOUTH | 2008 | 108
65 | CVC CHANNELVIEW CTG 1 | 02INR0004 | CVC_CVC_G1 | HARRIS | GAS | HOUSTON | 2008 | 171
66 | CVC CHANNELVIEW CTG 2 | 02INR0004 | CVC_CVC_G2 | HARRIS | GAS | HOUSTON | 2008 | 164
67 | CVC CHANNELVIEW CTG 3 | 02INR0004 | CVC_CVC_G3 | HARRIS | GAS | HOUSTON | 2008 | 164
68 | CVC CHANNELVIEW STG 5 | 02INR0004 | CVC_CVC_G5 | HARRIS | GAS | HOUSTON | 2008 | 146
69 | DEER PARK ENERGY CENTER CTG 1 | 02INR0020 | DDPEC_GT1 | HARRIS | GAS | HOUSTON | 2002 | 194
70 | DEER PARK ENERGY CENTER CTG 2 | 02INR0020 | DDPEC_GT2 | HARRIS | GAS | HOUSTON | 2002 | 206
71 | DEER PARK ENERGY CENTER CTG 3 | 02INR0020 | DDPEC_GT3 | HARRIS | GAS | HOUSTON | 2002 | 194
72 | DEER PARK ENERGY CENTER CTG 4 | 02INR0020 | DDPEC_GT4 | HARRIS | GAS | HOUSTON | 2002 | 206
73 | DEER PARK ENERGY CENTER STG | 02INR0020 | DDPEC_ST1 | HARRIS | GAS | HOUSTON | 2002 | 290
74 | DEER PARK ENERGY CENTER CTG 6 | 14INR0015 | DDPEC_GT6 | HARRIS | GAS | HOUSTON | 2014 | 179
75 | ENNIS POWER STATION CTG 2 | 01INR0008 | ETCCS_CT1 | ELLIS | GAS | NORTH | 2002 | 231
76 | ENNIS POWER STATION STG 1 | 01INR0008 | ETCCS_UNIT1 | ELLIS | GAS | NORTH | 2002 | 127
77 | FERGUSON REPLACEMENT CTG1 | 13INR0021 | FERGCC_FERGGT1 | LLANO | GAS | SOUTH | 2014 | 175.9
78 | FERGUSON REPLACEMENT CTG2 | 13INR0021 | FERGCC_FERGGT2 | LLANO | GAS | SOUTH | 2014 | 175.9
79 | FERGUSON REPLACEMENT STG | 13INR0021 | FERGCC_FERGST1 | LLANO | GAS | SOUTH | 2014 | 196.9
80 | FORNEY ENERGY CENTER CTG 11 | 01INR0007 | FRNYPP_GT11 | KAUFMAN | GAS | NORTH | 2003 | 176
81 | FORNEY ENERGY CENTER CTG 12 | 01INR0007 | FRNYPP_GT12 | KAUFMAN | GAS | NORTH | 2003 | 168
82 | FORNEY ENERGY CENTER CTG 13 | 01INR0007 | FRNYPP_GT13 | KAUFMAN | GAS | NORTH | 2003 | 168
83 | FORNEY ENERGY CENTER CTG 21 | 01INR0007 | FRNYPP_GT21 | KAUFMAN | GAS | NORTH | 2003 | 176
84 | FORNEY ENERGY CENTER CTG 22 | 01INR0007 | FRNYPP_GT22 | KAUFMAN | GAS | NORTH | 2003 | 168
85 | FORNEY ENERGY CENTER CTG 23 | 01INR0007 | FRNYPP_GT23 | KAUFMAN | GAS | NORTH | 2003 | 168
86 | FORNEY ENERGY CENTER STG 10 | 01INR0007 | FRNYPP_ST10 | KAUFMAN | GAS | NORTH | 2003 | 417
87 | FORNEY ENERGY CENTER STG 20 | 01INR0007 | FRNYPP_ST20 | KAUFMAN | GAS | NORTH | 2003 | 417
88 | FREESTONE ENERGY CENTER CTG 1 | 01INR0009 | FREC_GT1 | FREESTONE | GAS | NORTH | 2002 | 155.2
89 | FREESTONE ENERGY CENTER CTG 2 | 01INR0009 | FREC_GT2 | FREESTONE | GAS | NORTH | 2002 | 155.2
90 | FREESTONE ENERGY CENTER STG 3 | 01INR0009 | FREC_ST3 | FREESTONE | GAS | NORTH | 2002 | 177.6
91 | FREESTONE ENERGY CENTER CTG 4 | 01INR0009 | FREC_GT4 | FREESTONE | GAS | NORTH | 2002 | 155.4
92 | FREESTONE ENERGY CENTER CTG 5 | 01INR0009 | FREC_GT5 | FREESTONE | GAS | NORTH | 2002 | 155.4
93 | FREESTONE ENERGY CENTER STG 6 | 01INR0009 | FREC_ST6 | FREESTONE | GAS | NORTH | 2002 | 176.5
94 | GUADALUPE GEN STN CTG 1 | 01INR0004 | GUADG_GAS1 | GUADALUPE | GAS | SOUTH | 2000 | 158
95 | GUADALUPE GEN STN CTG 2 | 01INR0004 | GUADG_GAS2 | GUADALUPE | GAS | SOUTH | 2000 | 158
96 | GUADALUPE GEN STN CTG 3 | 01INR0004 | GUADG_GAS3 | GUADALUPE | GAS | SOUTH | 2000 | 158
97 | GUADALUPE GEN STN CTG 4 | 01INR0004 | GUADG_GAS4 | GUADALUPE | GAS | SOUTH | 2000 | 158
98 | GUADALUPE GEN STN STG 5 | 01INR0004 | GUADG_STM5 | GUADALUPE | GAS | SOUTH | 2000 | 200
99 | GUADALUPE GEN STN STG 6 | 01INR0004 | GUADG_STM6 | GUADALUPE | GAS | SOUTH | 2000 | 200
100 | HAYS ENERGY FACILITY CSG 1 | 01INR0003 | HAYSEN_HAYSENG1 | HAYS | GAS | SOUTH | 2002 | 220
101 | HAYS ENERGY FACILITY CSG 2 | 01INR0003 | HAYSEN_HAYSENG2 | HAYS | GAS | SOUTH | 2002 | 220
102 | HAYS ENERGY FACILITY CSG 3 | 01INR0003 | HAYSEN_HAYSENG3 | HAYS | GAS | SOUTH | 2002 | 225
103 | HAYS ENERGY FACILITY CSG 4 | 01INR0003 | HAYSEN_HAYSENG4 | HAYS | GAS | SOUTH | 2002 | 225
104 | HIDALGO CTG 1 | 00INR0006 | DUKE_DUKE_GT1 | HIDALGO | GAS | SOUTH | 2000 | 145
105 | HIDALGO CTG 2 | 00INR0006 | DUKE_DUKE_GT2 | HIDALGO | GAS | SOUTH | 2000 | 145
106 | HIDALGO STG | 00INR0006 | DUKE_DUKE_ST1 | HIDALGO | GAS | SOUTH | 2000 | 173
107 | JACK COUNTY GEN FACILITY CTG 1 | 05INR0010 | JACKCNTY_CT1 | JACK | GAS | NORTH | 2005 | 150
108 | JACK COUNTY GEN FACILITY CTG 2 | 05INR0010 | JACKCNTY_CT2 | JACK | GAS | NORTH | 2005 | 150
109 | JACK COUNTY GEN FACILITY STG 1 | 05INR0010 | JACKCNTY_STG | JACK | GAS | NORTH | 2005 | 285
110 | JACK COUNTY GEN FACILITY CTG 3 | 10INR0010 | JCKCNTY2_CT3 | JACK | GAS | NORTH | 2011 | 150
111 | JACK COUNTY GEN FACILITY CTG 4 | 10INR0010 | JCKCNTY2_CT4 | JACK | GAS | NORTH | 2011 | 150
112 | JACK COUNTY GEN FACILITY STG 2 | 10INR0010 | JCKCNTY2_ST2 | JACK | GAS | NORTH | 2011 | 285
113 | JOHNSON COUNTY GEN FACILITY CTG |  | TEN_CT1 | JOHNSON | GAS | NORTH | 1997 | 163
114 | JOHNSON COUNTY GEN FACILITY STG |  | TEN_STG | JOHNSON | GAS | NORTH | 1997 | 106
115 | LAMAR POWER CTG 11 | 00INR0008 | LPCCS_CT11 | LAMAR | GAS | NORTH | 2000 | 171
116 | LAMAR POWER CTG 12 | 00INR0008 | LPCCS_CT12 | LAMAR | GAS | NORTH | 2000 | 161
117 | LAMAR POWER CTG 21 | 00INR0008 | LPCCS_CT21 | LAMAR | GAS | NORTH | 2000 | 161
118 | LAMAR POWER CTG 22 | 00INR0008 | LPCCS_CT22 | LAMAR | GAS | NORTH | 2000 | 166
119 | LAMAR POWER STG 1 | 00INR0008 | LPCCS_UNIT1 | LAMAR | GAS | NORTH | 2000 | 204
120 | LAMAR POWER STG 2 | 00INR0008 | LPCCS_UNIT2 | LAMAR | GAS | NORTH | 2000 | 204
121 | LOST PINES CTG 1 | 02INR0005 | LOSTPI_LOSTPGT1 | BASTROP | GAS | SOUTH | 2001 | 178
122 | LOST PINES CTG 2 | 02INR0005 | LOSTPI_LOSTPGT2 | BASTROP | GAS | SOUTH | 2001 | 172
123 | LOST PINES STG | 02INR0005 | LOSTPI_LOSTPST1 | BASTROP | GAS | SOUTH | 2001 | 188
124 | MAGIC VALLEY CTG 1 | 00INR0009 | NEDIN_NEDIN_G1 | HIDALGO | GAS | SOUTH | 2001 | 212.5
125 | MAGIC VALLEY CTG 2 | 00INR0009 | NEDIN_NEDIN_G2 | HIDALGO | GAS | SOUTH | 2001 | 212.5
126 | MAGIC VALLEY STG | 00INR0009 | NEDIN_NEDIN_G3 | HIDALGO | GAS | SOUTH | 2001 | 254.9
127 | MIDLOTHIAN CS 1 | 00INR0012 | MDANP_CT1 | ELLIS | GAS | NORTH | 2001 | 235
128 | MIDLOTHIAN CS 2 | 00INR0012 | MDANP_CT2 | ELLIS | GAS | NORTH | 2001 | 235
129 | MIDLOTHIAN CS 3 | 00INR0012 | MDANP_CT3 | ELLIS | GAS | NORTH | 2001 | 235
130 | MIDLOTHIAN CS 4 | 00INR0012 | MDANP_CT4 | ELLIS | GAS | NORTH | 2001 | 235
131 | MIDLOTHIAN CS 5 | 02INR0008 | MDANP_CT5 | ELLIS | GAS | NORTH | 2002 | 252
132 | MIDLOTHIAN CS 6 | 02INR0008 | MDANP_CT6 | ELLIS | GAS | NORTH | 2002 | 252
133 | NUECES BAY CTG 8 | 09INR0039 | NUECES_B_NUECESG8 | NUECES | GAS | COASTAL | 2010 | 161
134 | NUECES BAY CTG 9 | 09INR0039 | NUECES_B_NUECESG9 | NUECES | GAS | COASTAL | 2010 | 161
135 | NUECES BAY STG 7 |  | NUECES_B_NUECESG7 | NUECES | GAS | COASTAL | 1972 | 322
136 | ODESSA-ECTOR GEN STN CTG 11 | 01INR0026 | OECCS_CT11 | ECTOR | GAS | WEST | 2001 | 156.4
137 | ODESSA-ECTOR GEN STN CTG 12 | 01INR0026 | OECCS_CT12 | ECTOR | GAS | WEST | 2001 | 145.4
138 | ODESSA-ECTOR GEN STN CTG 21 | 01INR0026 | OECCS_CT21 | ECTOR | GAS | WEST | 2001 | 149.9
139 | ODESSA-ECTOR GEN STN CTG 22 | 01INR0026 | OECCS_CT22 | ECTOR | GAS | WEST | 2001 | 147.5
140 | ODESSA-ECTOR GEN STN STG 1 | 01INR0026 | OECCS_UNIT1 | ECTOR | GAS | WEST | 2001 | 216
141 | ODESSA-ECTOR GEN STN STG 2 | 01INR0026 | OECCS_UNIT2 | ECTOR | GAS | WEST | 2001 | 216
142 | PANDA SHERMAN CTG1 | 10INR0021 | PANDA_S_SHER1CT1 | GRAYSON | GAS | NORTH | 2014 | 218.5
143 | PANDA SHERMAN CTG2 | 10INR0021 | PANDA_S_SHER1CT2 | GRAYSON | GAS | NORTH | 2014 | 218.5
144 | PANDA SHERMAN STG | 10INR0021 | PANDA_S_SHER1ST1 | GRAYSON | GAS | NORTH | 2014 | 353.1
145 | PANDA TEMPLE CTG1 | 10INR0020a | PANDA_T1_TMPL1CT1 | BELL | GAS | NORTH | 2014 | 218.5
146 | PANDA TEMPLE CTG2 | 10INR0020a | PANDA_T1_TMPL1CT2 | BELL | GAS | NORTH | 2014 | 218.5
147 | PANDA TEMPLE STG | 10INR0020a | PANDA_T1_TMPL1ST1 | BELL | GAS | NORTH | 2014 | 353.1
148 | PARIS ENERGY CENTER CTG 1 |  | TNSKA_GT1 | LAMAR | GAS | NORTH | 1989 | 86
149 | PARIS ENERGY CENTER CTG 2 |  | TNSKA_GT2 | LAMAR | GAS | NORTH | 1989 | 86
150 | PARIS ENERGY CENTER STG |  | TNSKA_STG | LAMAR | GAS | NORTH | 1990 | 87
151 | PASGEN CTG 2 |  | PSG_PSG_GT2 | HARRIS | GAS | HOUSTON | 2000 | 168
152 | PASGEN CTG 3 |  | PSG_PSG_GT3 | HARRIS | GAS | HOUSTON | 2000 | 168
153 | PASGEN STG 2 |  | PSG_PSG_ST2 | HARRIS | GAS | HOUSTON | 2000 | 168
154 | QUAIL RUN ENERGY CTG 1 | 06INR0036b | QALSW_GT1 | ECTOR | GAS | WEST | 2007 | 81
155 | QUAIL RUN ENERGY CTG 2 | 06INR0036b | QALSW_GT2 | ECTOR | GAS | WEST | 2007 | 81
156 | QUAIL RUN ENERGY STG 1 | 06INR0036b | QALSW_STG1 | ECTOR | GAS | WEST | 2007 | 98
157 | QUAIL RUN ENERGY CTG 3 | 06INR0036a | QALSW_GT3 | ECTOR | GAS | WEST | 2008 | 80
158 | QUAIL RUN ENERGY CTG 4 | 06INR0036a | QALSW_GT4 | ECTOR | GAS | WEST | 2008 | 80
159 | QUAIL RUN ENERGY STG 2 | 06INR0036a | QALSW_STG2 | ECTOR | GAS | WEST | 2008 | 98
160 | SAM RAYBURN CTG 7 | 03INR0014 | RAYBURN_RAYBURG7 | VICTORIA | GAS | SOUTH | 2003 | 50
161 | RIO NOGALES CTG 1 | 02INR0001 | RIONOG_CT1 | GUADALUPE | GAS | SOUTH | 2002 | 162
162 | RIO NOGALES CTG 2 | 02INR0001 | RIONOG_CT2 | GUADALUPE | GAS | SOUTH | 2002 | 162
163 | RIO NOGALES CTG 3 | 02INR0001 | RIONOG_CT3 | GUADALUPE | GAS | SOUTH | 2002 | 162
164 | RIO NOGALES STG 4 | 02INR0001 | RIONOG_ST1 | GUADALUPE | GAS | SOUTH | 2002 | 323
165 | SAM RAYBURN CTG 8 | 03INR0014 | RAYBURN_RAYBURG8 | VICTORIA | GAS | SOUTH | 2003 | 51
166 | SAM RAYBURN CTG 9 | 03INR0014 | RAYBURN_RAYBURG9 | VICTORIA | GAS | SOUTH | 2003 | 50
167 | SAM RAYBURN STG 10 | 03INR0014 | RAYBURN_RAYBURG10 | VICTORIA | GAS | SOUTH | 2003 | 40
168 | SANDHILL ENERGY CENTER CTG 5A | 03INR0033 | SANDHSYD_SH_5A | TRAVIS | GAS | SOUTH | 2004 | 161
169 | SANDHILL ENERGY CENTER STG 5C | 03INR0033 | SANDHSYD_SH_5C | TRAVIS | GAS | SOUTH | 2004 | 150
170 | SILAS RAY STG 6 |  | SILASRAY_SILAS_6 | CAMERON | GAS | COASTAL | 1962 | 20
171 | SILAS RAY CTG 9 |  | SILASRAY_SILAS_9 | CAMERON | GAS | COASTAL | 1996 | 38
172 | T H WHARTON CTG 31 |  | THW_THWGT31 | HARRIS | GAS | HOUSTON | 1972 | 57
173 | T H WHARTON CTG 32 |  | THW_THWGT32 | HARRIS | GAS | HOUSTON | 1972 | 57
174 | T H WHARTON CTG 33 |  | THW_THWGT33 | HARRIS | GAS | HOUSTON | 1972 | 57
175 | T H WHARTON CTG 34 |  | THW_THWGT34 | HARRIS | GAS | HOUSTON | 1972 | 57
176 | T H WHARTON STG 3 |  | THW_THWST_3 | HARRIS | GAS | HOUSTON | 1974 | 104
177 | T H WHARTON CTG 41 |  | THW_THWGT41 | HARRIS | GAS | HOUSTON | 1972 | 57
178 | T H WHARTON CTG 42 |  | THW_THWGT42 | HARRIS | GAS | HOUSTON | 1972 | 57
179 | T H WHARTON CTG 43 |  | THW_THWGT43 | HARRIS | GAS | HOUSTON | 1974 | 57
180 | T H WHARTON CTG 44 |  | THW_THWGT44 | HARRIS | GAS | HOUSTON | 1974 | 57
181 | T H WHARTON STG 4 |  | THW_THWST_4 | HARRIS | GAS | HOUSTON | 1974 | 104
182 | TEXAS CITY CTG A |  | TXCTY_CTA | GALVESTON | GAS | HOUSTON | 2000 | 99.1
183 | TEXAS CITY CTG B |  | TXCTY_CTB | GALVESTON | GAS | HOUSTON | 2000 | 99.1
184 | TEXAS CITY CTG C |  | TXCTY_CTC | GALVESTON | GAS | HOUSTON | 2000 | 99.1
185 | TEXAS CITY STG |  | TXCTY_ST | GALVESTON | GAS | HOUSTON | 2000 | 131.5
186 | VICTORIA POWER STATION CTG 6 | 08INR0050 | VICTORIA_VICTORG6 | VICTORIA | GAS | SOUTH | 2009 | 171
187 | VICTORIA POWER STATION STG 5 | 08INR0050 | VICTORIA_VICTORG5 | VICTORIA | GAS | SOUTH | 1963 | 132
188 | WICHITA FALLS CTG 1 |  | WFCOGEN_UNIT1 | WICHITA | GAS | WEST | 1987 | 20
189 | WICHITA FALLS CTG 2 |  | WFCOGEN_UNIT2 | WICHITA | GAS | WEST | 1987 | 20
190 | WICHITA FALLS CTG 3 |  | WFCOGEN_UNIT3 | WICHITA | GAS | WEST | 1987 | 20
191 | WICHITA FALLS STG 4 |  | WFCOGEN_UNIT4 | WICHITA | GAS | WEST | 1987 | 17
192 | WISE-TRACTEBEL POWER CTG 1 | 02INR0009 | WCPP_CT1 | WISE | GAS | NORTH | 2004 | 275
193 | WISE-TRACTEBEL POWER CTG 2 | 02INR0009 | WCPP_CT2 | WISE | GAS | NORTH | 2004 | 275
194 | WISE-TRACTEBEL POWER STG 1 | 02INR0009 | WCPP_ST1 | WISE | GAS | NORTH | 2004 | 290
195 | WOLF HOLLOW POWER CTG 1 | 01INR0015 | WHCCS_CT1 | HOOD | GAS | NORTH | 2002 | 227
196 | WOLF HOLLOW POWER CTG 2 | 01INR0015 | WHCCS_CT2 | HOOD | GAS | NORTH | 2002 | 227
197 | WOLF HOLLOW POWER STG | 01INR0015 | WHCCS_STG | HOOD | GAS | NORTH | 2002 | 286
198 | ATKINS CTG 7 |  | ATKINS_ATKINSG7 | BRAZOS | GAS | NORTH | 2016 | 20
199 | DANSBY CTG 2 |  | DANSBY_DANSBYG2 | BRAZOS | GAS | NORTH | 2004 | 48
200 | DANSBY CTG 3 | 09INR0072 | DANSBY_DANSBYG3 | BRAZOS | GAS | NORTH | 2010 | 50
201 | DECKER CREEK CTG 1 |  | DECKER_DPGT_1 | TRAVIS | GAS | SOUTH | 1989 | 49
202 | DECKER CREEK CTG 2 |  | DECKER_DPGT_2 | TRAVIS | GAS | SOUTH | 1989 | 49
203 | DECKER CREEK CTG 3 |  | DECKER_DPGT_3 | TRAVIS | GAS | SOUTH | 1989 | 49
204 | DECKER CREEK CTG 4 |  | DECKER_DPGT_4 | TRAVIS | GAS | SOUTH | 1989 | 49
205 | DECORDOVA CTG 1 |  | DCSES_CT10 | HOOD | GAS | NORTH | 1990 | 74
206 | DECORDOVA CTG 2 |  | DCSES_CT20 | HOOD | GAS | NORTH | 1990 | 73
207 | DECORDOVA CTG 3 |  | DCSES_CT30 | HOOD | GAS | NORTH | 1990 | 72
208 | DECORDOVA CTG 4 |  | DCSES_CT40 | HOOD | GAS | NORTH | 1990 | 71
209 | EXTEX LAPORTE GEN STN CTG 1 | 01INR0044 | AZ_AZ_G1 | HARRIS | GAS | HOUSTON | 2009 | 42
210 | EXTEX LAPORTE GEN STN CTG 2 | 01INR0044 | AZ_AZ_G2 | HARRIS | GAS | HOUSTON | 2009 | 42
211 | EXTEX LAPORTE GEN STN CTG 3 | 01INR0044 | AZ_AZ_G3 | HARRIS | GAS | HOUSTON | 2009 | 42
212 | EXTEX LAPORTE GEN STN CTG 4 | 01INR0044 | AZ_AZ_G4 | HARRIS | GAS | HOUSTON | 2009 | 42
213 | GREENS BAYOU CTG 73 |  | GBY_GBYGT73 | HARRIS | GAS | HOUSTON | 1976 | 54
214 | GREENS BAYOU CTG 74 |  | GBY_GBYGT74 | HARRIS | GAS | HOUSTON | 1976 | 54
215 | GREENS BAYOU CTG 81 |  | GBY_GBYGT81 | HARRIS | GAS | HOUSTON | 1976 | 54
216 | GREENS BAYOU CTG 82 |  | GBY_GBYGT82 | HARRIS | GAS | HOUSTON | 1976 | 58
217 | GREENS BAYOU CTG 83 |  | GBY_GBYGT83 | HARRIS | GAS | HOUSTON | 1976 | 64
218 | GREENS BAYOU CTG 84 |  | GBY_GBYGT84 | HARRIS | GAS | HOUSTON | 1976 | 54
219 | GREENVILLE IC ENGINE PLANT | 10INR0070 | STEAM_ENGINE_1 | HUNT | GAS | NORTH | 2010 | 8.4
220 | GREENVILLE IC ENGINE PLANT | 10INR0070 | STEAM_ENGINE_2 | HUNT | GAS | NORTH | 2010 | 8.4
221 | GREENVILLE IC ENGINE PLANT | 10INR0070 | STEAM_ENGINE_3 | HUNT | GAS | NORTH | 2010 | 8.4
222 | LAREDO CTG 4 | 08INR0064 | LARDVFTN_G4 | WEBB | GAS | SOUTH | 2008 | 94.2
223 | LAREDO CTG 5 | 08INR0064 | LARDVFTN_G5 | WEBB | GAS | SOUTH | 2008 | 94.2
224 | LEON CREEK PEAKER CTG 1 | 04INR0009 | LEON_CRK_LCPCT1 | BEXAR | GAS | SOUTH | 2004 | 48
225 | LEON CREEK PEAKER CTG 2 | 04INR0009 | LEON_CRK_LCPCT2 | BEXAR | GAS | SOUTH | 2004 | 48
226 | LEON CREEK PEAKER CTG 3 | 04INR0009 | LEON_CRK_LCPCT3 | BEXAR | GAS | SOUTH | 2004 | 48
227 | LEON CREEK PEAKER CTG 4 | 04INR0009 | LEON_CRK_LCPCT4 | BEXAR | GAS | SOUTH | 2004 | 48
228 | MORGAN CREEK CTG 1 |  | MGSES_CT1 | MITCHELL | GAS | WEST | 1988 | 77
229 | MORGAN CREEK CTG 2 |  | MGSES_CT2 | MITCHELL | GAS | WEST | 1988 | 77
230 | MORGAN CREEK CTG 3 |  | MGSES_CT3 | MITCHELL | GAS | WEST | 1988 | 77
231 | MORGAN CREEK CTG 4 |  | MGSES_CT4 | MITCHELL | GAS | WEST | 1988 | 77
232 | MORGAN CREEK CTG 5 |  | MGSES_CT5 | MITCHELL | GAS | WEST | 1988 | 77
233 | MORGAN CREEK CTG 6 |  | MGSES_CT6 | MITCHELL | GAS | WEST | 1988 | 77
234 | PEARSALL IC ENGINE PLANT A | 09INR0079a | PEARSAL2_AGR_A | FRIO | GAS | SOUTH | 2012 | 50.6
235 | PEARSALL IC ENGINE PLANT B | 09INR0079a | PEARSAL2_AGR_B | FRIO | GAS | SOUTH | 2012 | 50.6
236 | PEARSALL IC ENGINE PLANT C | 09INR0079b | PEARSAL2_AGR_C | FRIO | GAS | SOUTH | 2012 | 50.6
237 | PEARSALL IC ENGINE PLANT D | 09INR0079b | PEARSAL2_AGR_D | FRIO | GAS | SOUTH | 2012 | 50.6
238 | PERMIAN BASIN CTG 1 |  | PB2SES_CT1 | WARD | GAS | WEST | 1988 | 71
239 | PERMIAN BASIN CTG 2 |  | PB2SES_CT2 | WARD | GAS | WEST | 1988 | 70
240 | PERMIAN BASIN CTG 3 |  | PB2SES_CT3 | WARD | GAS | WEST | 1988 | 73
241 | PERMIAN BASIN CTG 4 |  | PB2SES_CT4 | WARD | GAS | WEST | 1990 | 74
242 | PERMIAN BASIN CTG 5 |  | PB2SES_CT5 | WARD | GAS | WEST | 1990 | 74
243 | R W MILLER CTG 4 |  | MIL_MILLERG4 | PALO PINTO | GAS | NORTH | 2000 | 104
244 | R W MILLER CTG 5 |  | MIL_MILLERG5 | PALO PINTO | GAS | NORTH | 2000 | 104
245 | RAY OLINGER CTG 4 | 00INR0024 | OLINGR_OLING_4 | COLLIN | GAS | NORTH | 2001 | 75
246 | SAM RAYBURN CTG 1 |  | RAYBURN_RAYBURG1 | VICTORIA | GAS | SOUTH | 1963 | 13.5
247 | SAM RAYBURN CTG 2 |  | RAYBURN_RAYBURG2 | VICTORIA | GAS | SOUTH | 1963 | 13.5
248 | SAN JACINTO SES CTG 1 |  | SJS_SJS_G1 | HARRIS | GAS | HOUSTON | 1995 | 81
249 | SAN JACINTO SES CTG 2 |  | SJS_SJS_G2 | HARRIS | GAS | HOUSTON | 1995 | 81
250 | SANDHILL ENERGY CENTER CTG 1 | 01INR0041 | SANDHSYD_SH1 | TRAVIS | GAS | SOUTH | 2001 | 47
251 | SANDHILL ENERGY CENTER CTG 2 | 01INR0041 | SANDHSYD_SH2 | TRAVIS | GAS | SOUTH | 2001 | 47
252 | SANDHILL ENERGY CENTER CTG 3 | 01INR0041 | SANDHSYD_SH3 | TRAVIS | GAS | SOUTH | 2001 | 47
253 | SANDHILL ENERGY CENTER CTG 4 | 01INR0041 | SANDHSYD_SH4 | TRAVIS | GAS | SOUTH | 2001 | 47
254 | SANDHILL ENERGY CENTER CTG 6 | 09INR0045 | SANDHSYD_SH6 | TRAVIS | GAS | SOUTH | 2010 | 47
255 | SANDHILL ENERGY CENTER CTG 7 | 09INR0045 | SANDHSYD_SH7 | TRAVIS | GAS | SOUTH | 2010 | 47
256 | SILAS RAY CTG 10 | 04INR0014 | SILASRAY_SILAS_10 | CAMERON | GAS | COASTAL | 2004 | 46
257 | T H WHARTON CTG 51 |  | THW_THWGT51 | HARRIS | GAS | HOUSTON | 1975 | 57
258 | T H WHARTON CTG 52 |  | THW_THWGT52 | HARRIS | GAS | HOUSTON | 1975 | 57
259 | T H WHARTON CTG 53 |  | THW_THWGT53 | HARRIS | GAS | HOUSTON | 1975 | 57
260 | T H WHARTON CTG 54 |  | THW_THWGT54 | HARRIS | GAS | HOUSTON | 1975 | 57
261 | T H WHARTON CTG 55 |  | THW_THWGT55 | HARRIS | GAS | HOUSTON | 1975 | 57
262 | T H WHARTON CTG 56 |  | THW_THWGT56 | HARRIS | GAS | HOUSTON | 1975 | 57
263 | T H WHARTON CTG G1 |  | THW_THWGT_1 | HARRIS | GAS | HOUSTON | 1967 | 13
264 | TEXAS GULF SULPHUR |  | TGF_TGFGT_1 | WHARTON | GAS | SOUTH | 1985 | 89
265 | V H BRAUNIG CTG 5 | 09INR0028 | BRAUNIG_VHB6CT5 | BEXAR | GAS | SOUTH | 2009 | 48
266 | V H BRAUNIG CTG 6 | 09INR0028 | BRAUNIG_VHB6CT6 | BEXAR | GAS | SOUTH | 2009 | 48
267 | V H BRAUNIG CTG 7 | 09INR0028 | BRAUNIG_VHB6CT7 | BEXAR | GAS | SOUTH | 2009 | 48
268 | V H BRAUNIG CTG 8 | 09INR0028 | BRAUNIG_VHB6CT8 | BEXAR | GAS | SOUTH | 2009 | 48
269 | W A PARISH CTG 1 |  | WAP_WAPGT_1 | FT. BEND | GAS | HOUSTON | 1967 | 13
270 | W A PARISH - PETRA NOVA CTG | 12INR0086 | PNPI_GT2 | FORT BEND | GAS | HOUSTON | 2013 | 83
271 | WINCHESTER POWER PARK CTG 1 | 09INR0027 | WIPOPA_WPP_G1 | FAYETTE | GAS | SOUTH | 2009 | 44
272 | WINCHESTER POWER PARK CTG 2 | 09INR0027 | WIPOPA_WPP_G2 | FAYETTE | GAS | SOUTH | 2009 | 44
273 | WINCHESTER POWER PARK CTG 3 | 09INR0027 | WIPOPA_WPP_G3 | FAYETTE | GAS | SOUTH | 2009 | 44
274 | WINCHESTER POWER PARK CTG 4 | 09INR0027 | WIPOPA_WPP_G4 | FAYETTE | GAS | SOUTH | 2009 | 44
275 | B M DAVIS STG U1 |  | B_DAVIS_B_DAVIG1 | NUECES | GAS | COASTAL | 1974 | 335
276 | CEDAR BAYOU STG U1 |  | CBY_CBY_G1 | CHAMBERS | GAS | HOUSTON | 1970 | 745
277 | CEDAR BAYOU STG U2 |  | CBY_CBY_G2 | CHAMBERS | GAS | HOUSTON | 1972 | 749
278 | DANSBY STG U1 |  | DANSBY_DANSBYG1 | BRAZOS | GAS | NORTH | 1978 | 110
279 | DECKER CREEK STG U1 |  | DECKER_DPG1 | TRAVIS | GAS | SOUTH | 1971 | 320
280 | DECKER CREEK STG U2 |  | DECKER_DPG2 | TRAVIS | GAS | SOUTH | 1978 | 420
281 | GRAHAM STG U1 |  | GRSES_UNIT1 | YOUNG | GAS | WEST | 1960 | 225
282 | GRAHAM STG U2 |  | GRSES_UNIT2 | YOUNG | GAS | WEST | 1969 | 390
283 | GREENS BAYOU STG U5 |  | GBY_GBY_5 | HARRIS | GAS | HOUSTON | 1973 | 371
284 | HANDLEY STG U3 |  | HLSES_UNIT3 | TARRANT | GAS | NORTH | 1963 | 395
285 | HANDLEY STG U4 |  | HLSES_UNIT4 | TARRANT | GAS | NORTH | 1976 | 435
286 | HANDLEY STG U5 |  | HLSES_UNIT5 | TARRANT | GAS | NORTH | 1977 | 435
287 | LAKE HUBBARD STG U1 |  | LHSES_UNIT1 | DALLAS | GAS | NORTH | 1970 | 392
288 | LAKE HUBBARD STG U2 |  | LHSES_UNIT2A | DALLAS | GAS | NORTH | 1973 | 515
289 | MOUNTAIN CREEK STG U6 |  | MCSES_UNIT6 | DALLAS | GAS | NORTH | 1956 | 121
290 | MOUNTAIN CREEK STG U7 |  | MCSES_UNIT7 | DALLAS | GAS | NORTH | 1958 | 117
291 | MOUNTAIN CREEK STG U8 |  | MCSES_UNIT8 | DALLAS | GAS | NORTH | 1967 | 567
292 | O W SOMMERS STG U1 |  | CALAVERS_OWS1 | BEXAR | GAS | SOUTH | 1972 | 420
293 | O W SOMMERS STG U2 |  | CALAVERS_OWS2 | BEXAR | GAS | SOUTH | 1974 | 420
294 | PEARSALL STG U1 |  | PEARSALL_PEARS_1 | FRIO | GAS | SOUTH | 1961 | 25
295 | PEARSALL STG U2 |  | PEARSALL_PEARS_2 | FRIO | GAS | SOUTH | 1961 | 25
296 | PEARSALL STG U3 |  | PEARSALL_PEARS_3 | FRIO | GAS | SOUTH | 1961 | 25
297 | POWERLANE PLANT STG U1 |  | STEAM1A_STEAM_1 | HUNT | GAS | NORTH | 1966 | 20
298 | POWERLANE PLANT STG U2 |  | STEAM_STEAM_2 | HUNT | GAS | NORTH | 1967 | 26
299 | POWERLANE PLANT STG U3 |  | STEAM_STEAM_3 | HUNT | GAS | NORTH | 1978 | 41
300 | R W MILLER STG U1 |  | MIL_MILLERG1 | PALO PINTO | GAS | NORTH | 2016 | 75
301 | R W MILLER STG U2 |  | MIL_MILLERG2 | PALO PINTO | GAS | NORTH | 2016 | 120
302 | R W MILLER STG U3 |  | MIL_MILLERG3 | PALO PINTO | GAS | NORTH | 2016 | 208
303 | RAY OLINGER STG U1 |  | OLINGR_OLING_1 | COLLIN | GAS | NORTH | 1967 | 78
304 | RAY OLINGER STG U2 |  | OLINGR_OLING_2 | COLLIN | GAS | NORTH | 1971 | 107
305 | RAY OLINGER STG U3 |  | OLINGR_OLING_3 | COLLIN | GAS | NORTH | 1975 | 146
306 | SIM GIDEON STG U1 |  | GIDEON_GIDEONG1 | BASTROP | GAS | SOUTH | 1965 | 130
307 | SIM GIDEON STG U2 |  | GIDEON_GIDEONG2 | BASTROP | GAS | SOUTH | 1968 | 135
308 | SIM GIDEON STG U3 |  | GIDEON_GIDEONG3 | BASTROP | GAS | SOUTH | 1972 | 336
309 | SPENCER STG U4 |  | SPNCER_SPNCE_4 | DENTON | GAS | NORTH | 1966 | 61
310 | SPENCER STG U5 |  | SPNCER_SPNCE_5 | DENTON | GAS | NORTH | 1973 | 61
311 | STRYKER CREEK STG U1 |  | SCSES_UNIT1A | CHEROKEE | GAS | NORTH | 1958 | 167
312 | STRYKER CREEK STG U2 |  | SCSES_UNIT2 | CHEROKEE | GAS | NORTH | 1965 | 502
313 | TRINIDAD STG U6 |  | TRSES_UNIT6 | HENDERSON | GAS | NORTH | 1965 | 226
314 | V H BRAUNIG STG U1 |  | BRAUNIG_VHB1 | BEXAR | GAS | SOUTH | 1966 | 220
315 | V H BRAUNIG STG U2 |  | BRAUNIG_VHB2 | BEXAR | GAS | SOUTH | 1968 | 230
316 | V H BRAUNIG STG U3 |  | BRAUNIG_VHB3 | BEXAR | GAS | SOUTH | 1970 | 412
317 | W A PARISH STG U1 |  | WAP_WAP_G1 | FT. BEND | GAS | HOUSTON | 1958 | 169
318 | W A PARISH STG U2 |  | WAP_WAP_G2 | FT. BEND | GAS | HOUSTON | 1958 | 169
319 | W A PARISH STG U3 |  | WAP_WAP_G3 | FT. BEND | GAS | HOUSTON | 1961 | 246
320 | W A PARISH STG U4 |  | WAP_WAP_G4 | FT. BEND | GAS | HOUSTON | 1968 | 536
321 | NOTREES BATTERY FACILITY | 12INR0076 | NWF_NBS | WINKLER | STORAGE | WEST | 2012 | 0
322 | ACACIA SOLAR | 13DGR0001 | ACACIA_UNIT_1 | PRESIDIO | SOLAR | WEST | 2012 | 10
323 | BARILLA SOLAR (FS, PECOS) | 12INR0059 | HOVEY_UNIT1 | PECOS | SOLAR | WEST | 2014 | 29.4
324 | OCI ALAMO 1 SOLAR | 13INR0058 | OCI_ALM1_UNIT1 | BEXAR | SOLAR | SOUTH | 2013 | 39.2
325 | OCI ALAMO 4 SOLAR (BRACKETVILLE) | 14INR0024 | ECLIPSE_UNIT1 | KINNEY | SOLAR | SOUTH | 2014 | 37.6
326 | WEBBERVILLE SOLAR | 10INR0082 | WEBBER_S_WSP1 | TRAVIS | SOLAR | SOUTH | 2011 | 26.7
327 | BLUE WING 1 SOLAR |  | DG_BROOK_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.6
328 | BLUE WING 2 SOLAR |  | DG_ELEM_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.3
329 | OCI ALAMO 2-ST. HEDWIG SOLAR |  | DG_STHWG_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 4.4
330 | OCI ALAMO 3-WALZEM SOLAR |  | DG_WALZM_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 5.5
331 | SUNEDISON CPS3 SOMERSET 1 SOLAR |  | DG_SOME1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5.6
332 | SUNEDISON SOMERSET 2 SOLAR |  | DG_SOME2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5
333 | SUNEDISON RABEL ROAD SOLAR |  | DG_VALL1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9
334 | SUNEDISON VALLEY ROAD SOLAR |  | DG_VALL2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9
335 | NACOGDOCHES POWER | 09INR0007 | NACPW_UNIT1 | NACOGDOCHES | BIOMASS | NORTH | 2012 | 105
336 | LUFKIN BIOMASS | 08INR0033 | LFBIO_UNIT1 | ANGELINA | BIOMASS | NORTH | 2012 | 45
337 | BIOENERGY AUSTIN WALZEM RD LFG |  | DG_WALZE_4UNITS | BEXAR | BIOMASS | SOUTH | 2002 | 9.8
338 | BIOENERGY TEXAS COVEL GARDENS LFG |  | DG_MEDIN_1UNIT | BEXAR | BIOMASS | SOUTH | 2005 | 9.6
339 | FORT WORTH METHANE |  | DG_RDLML_1UNIT | TARRANT | BIOMASS | NORTH | 2011 | 1.6
340 | MCKINNEY LFG |  | DG_MKNSW_2UNITS | COLLIN | BIOMASS | NORTH | 2011 | 3.2
341 | NELSON GARDENS LANDFILL |  | DG_78252_4UNITS | BEXAR | BIOMASS | SOUTH | 2013 | 4.2
342 | SKYLINE LANDFILL GAS |  | DG_FERIS_4 UNITS | DALLAS | BIOMASS | NORTH | 2007 | 6.4
343 | TRINITY OAKS LFG |  | DG_KLBRG_1UNIT | DALLAS | BIOMASS | NORTH | 2011 | 3.2
344 | VIRIDIS ENERGY-ALVIN |  | DG_AV_DG1 | GALVESTON | BIOMASS | HOUSTON | 2002 | 6.7
345 | VIRIDIS ENERGY-HUMBLE |  | DG_HB_DG1 | HARRIS | BIOMASS | HOUSTON | 2002 | 10
346 | VIRIDIS ENERGY-LIBERTY |  | DG_LB_DG1 | HARRIS | BIOMASS | HOUSTON | 2002 | 3.9
347 | VIRIDIS ENERGY-TRINITY BAY |  | DG_TRN_DG1 | CHAMBERS | BIOMASS | HOUSTON | 2002 | 3.9
348 | WM RENEWABLE-AUSTIN LFG |  | DG_SPRIN_4UNITS | TRAVIS | BIOMASS | SOUTH | 2007 | 6.4
349 | WM RENEWABLE-DFW GAS RECOVERY LFG |  | DG_BIO2_4UNITS | DENTON | BIOMASS | NORTH | 2009 | 6.4
350 | WM RENEWABLE-BIOENERGY PARTNERS LFG |  | DG_BIOE_2UNITS | DENTON | BIOMASS | NORTH | 1988 | 6.2
351 | WM RENEWABLE-MESQUITE CREEK LFG |  | DG_FREIH_2UNITS | COMAL | BIOMASS | SOUTH | 2011 | 3.2
352 | WM RENEWABLE-WESTSIDE LFG |  | DG_WSTHL_3UNITS | PARKER | BIOMASS | NORTH | 2010 | 4.8
353 | Operational Capacity Total (Coal, Gas, Nuclear, Biomass, Solar) | [6 empty] | 65592.5
354
355 | Operational Resources (Hydro)
356 | AMISTAD HYDRO 1 |  | AMISTAD_AMISTAG1 | VAL VERDE | HYDRO | WEST | 1983 | 37.9
357 | AMISTAD HYDRO 2 |  | AMISTAD_AMISTAG2 | VAL VERDE | HYDRO | WEST | 1983 | 37.9
358 | AUSTIN HYDRO 1 |  | AUSTPL_AUSTING1 | TRAVIS | HYDRO | SOUTH | 1940 | 8
359 | AUSTIN HYDRO 2 |  | AUSTPL_AUSTING2 | TRAVIS | HYDRO | SOUTH | 1940 | 9
360 | BUCHANAN HYDRO 1 |  | BUCHAN_BUCHANG1 | LLANO | HYDRO | SOUTH | 1938 | 16
361 | BUCHANAN HYDRO 2 |  | BUCHAN_BUCHANG2 | LLANO | HYDRO | SOUTH | 1938 | 16
362 | BUCHANAN HYDRO 3 |  | BUCHAN_BUCHANG3 | LLANO | HYDRO | SOUTH | 1950 | 17
363 | DENISON DAM 1 |  | DNDAM_DENISOG1 | GRAYSON | HYDRO | NORTH | 1944 | 40
364 | DENISON DAM 2 |  | DNDAM_DENISOG2 | GRAYSON | HYDRO | NORTH | 1948 | 40
365 | FALCON HYDRO 1 |  | FALCON_FALCONG1 | STARR | HYDRO | SOUTH | 1954 | 12
366 | FALCON HYDRO 2 |  | FALCON_FALCONG2 | STARR | HYDRO | SOUTH | 1954 | 12
367 | FALCON HYDRO 3 |  | FALCON_FALCONG3 | STARR | HYDRO | SOUTH | 1954 | 12
368 | GRANITE SHOALS HYDRO 1 |  | WIRTZ_WIRTZ_G1 | BURNET | HYDRO | SOUTH | 1951 | 29
369 | GRANITE SHOALS HYDRO 2 |  | WIRTZ_WIRTZ_G2 | BURNET | HYDRO | SOUTH | 1951 | 29
370 | INKS HYDRO 1 |  | INKSDA_INKS_G1 | LLANO | HYDRO | SOUTH | 1938 | 14
371 | MARBLE FALLS HYDRO 1 |  | MARBFA_MARBFAG1 | BURNET | HYDRO | SOUTH | 1951 | 21
372 | MARBLE FALLS HYDRO 2 |  | MARBFA_MARBFAG2 | BURNET | HYDRO | SOUTH | 1951 | 20
373 | MARSHALL FORD HYDRO 1 |  | MARSFO_MARSFOG1 | TRAVIS | HYDRO | SOUTH | 1941 | 36
374 | MARSHALL FORD HYDRO 2 |  | MARSFO_MARSFOG2 | TRAVIS | HYDRO | SOUTH | 1941 | 36
375 | MARSHALL FORD HYDRO 3 |  | MARSFO_MARSFOG3 | TRAVIS | HYDRO | SOUTH | 1941 | 29
376 | WHITNEY DAM HYDRO |  | WND_WHITNEY1 | BOSQUE | HYDRO | NORTH | 1953 | 20
377 | WHITNEY DAM HYDRO 2 |  | WND_WHITNEY2 | BOSQUE | HYDRO | NORTH | 1953 | 15
378 | ARLINGTON OUTLET HYDROELECTRIC FACILITY |  | DG_OAKHL_1UNIT | TARRANT | HYDRO | NORTH | 2014 | 1.4
379 | EAGLE PASS HYDRO |  | DG_EAGLE_HY_EAGLE_HY1 | MAVERICK | HYDRO | SOUTH | 2005 | 9.6
380 | GUADALUPE BLANCO RIVER AUTH-CANYON |  | DG_CANYHY_CANYHYG1 | COMAL | HYDRO | SOUTH | 1989 | 6
381 | GUADALUPE BLANCO RIVER AUTH-LAKEWOOD TAP |  | DG_LKWDT_2UNITS | GONZALES | HYDRO | SOUTH | 1931 | 4.8
382 | GUADALUPE BLANCO RIVER AUTH-MCQUEENEY |  | DG_MCQUE_5UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 7.7
383 | GUADALUPE BLANCO RIVER AUTH-SCHUMANSVILLE |  | DG_SCHUM_2UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 3.6
384 | CITY OF GARLAND LEWISVILLE HYDRO |  | DG_LWSVL_1UNIT | DENTON | HYDRO | NORTH | 1991 | 2.2
385 | Operational Capacity Total (Hydro) | [6 empty] | 542.1
386 | Hydro Capacity Contribution (Top 20 Hours) |  | HYDRO_CAP_CONT |  |  |  |  | 52
387
388 | Operational Capacity Unavailable due to Extended Outage |  | OPERATION_UNAVAIL |  | GAS |  |  | -20
389 | Operational Capacity Total (Including Hydro) | [6 empty] | 65624.5
390
391 | Switchable Resources
392 | KIAMICHI ENERGY FACILITY 1CT101 | 03INR0012 | KMCHI_1CT101 | FANNIN | GAS | NORTH | 2003 | 178
393 | KIAMICHI ENERGY FACILITY 1CT201 | 03INR0012 | KMCHI_1CT201 | FANNIN | GAS | NORTH | 2003 | 180
394 | KIAMICHI ENERGY FACILITY 1ST | 03INR0012 | KMCHI_1ST | FANNIN | GAS | NORTH | 2003 | 307
395 | KIAMICHI ENERGY FACILITY 2CT101 | 03INR0012 | KMCHI_2CT101 | FANNIN | GAS | NORTH | 2003 | 178
396 | KIAMICHI ENERGY FACILITY 2CT201 | 03INR0012 | KMCHI_2CT201 | FANNIN | GAS | NORTH | 2003 | 180
397 | KIAMICHI ENERGY FACILITY 2ST | 03INR0012 | KMCHI_2ST | FANNIN | GAS | NORTH | 2003 | 307
398 | TENASKA-FRONTIER CTG 1 | 00PSR4 | FTR_FTR_G1 | GRIMES | GAS | NORTH | 2000 | 180
399 | TENASKA-FRONTIER CTG 2 | 00PSR4 | FTR_FTR_G2 | GRIMES | GAS | NORTH | 2000 | 180
400 | TENASKA-FRONTIER CTG 3 | 00PSR4 | FTR_FTR_G3 | GRIMES | GAS | NORTH | 2000 | 180
401 | TENASKA-FRONTIER STG 4 | 00PSR4 | FTR_FTR_G4 | GRIMES | GAS | NORTH | 2000 | 400
402 | TENASKA-GATEWAY CTG 1 | 01INR0019 | TGCCS_CT1 | RUSK | GAS | NORTH | 2001 | 162
403 | TENASKA-GATEWAY CTG 2 | 01INR0019 | TGCCS_CT2 | RUSK | GAS | NORTH | 2001 | 179
404 | TENASKA-GATEWAY CTG 3 | 01INR0019 | TGCCS_CT3 | RUSK | GAS | NORTH | 2001 | 178
405 | TENASKA-GATEWAY STG 4 | 01INR0019 | TGCCS_UNIT4 | RUSK | GAS | NORTH | 2001 | 389
406 | FRONTERA GENERATION CTG 1 |  | FRONTERA_FRONTEG1 | HIDALGO | GAS | SOUTH | 1999 | 170
407 | FRONTERA GENERATION CTG 2 |  | FRONTERA_FRONTEG2 | HIDALGO | GAS | SOUTH | 1999 | 170
408 | FRONTERA GENERATION STG |  | FRONTERA_FRONTEG3 | HIDALGO | GAS | SOUTH | 2000 | 184
409 | Switchable Capacity Total | [6 empty] | 3702
410
411 | Switchable Capacity Unavailable to ERCOT |  | SWITCH_UNAVAIL |  | GAS |  |  | -470
412
413 | Available Mothball Capacity based on Owner's Return Probability |  | MOTH_AVAIL |  | COAL |  |  | 0
414
415 | Private-Use Network Capacity Contribution (Top 20 Hours) |  | PUN_CAP_CONT |  | GAS |  |  | 4433
416
417 | Wind Resources
418 | ANACACHO WIND | 12INR0072 | ANACACHO_ANA | KINNEY | WIND | SOUTH | 2012 | 99.8
419 | BARTON CHAPEL WIND | 06INR0021 | BRTSW_BCW1 | JACK | WIND | NORTH | 2007 | 120
420 | BLUE SUMMIT WIND 5 | 12INR0075 | BLSUMMIT_BLSMT1_5 | WILBARGER | WIND | WEST | 2013 | 9
421 | BLUE SUMMIT WIND 6 | 12INR0075 | BLSUMMIT_BLSMT1_6 | WILBARGER | WIND | WEST | 2013 | 126.4
422 | BOBCAT BLUFF WIND | 08INR0049 | BCATWIND_WIND_1 | ARCHER | WIND | WEST | 2012 | 150
423 | BUFFALO GAP WIND FARM 1 | 04INR0015 | BUFF_GAP_UNIT1 | TAYLOR | WIND | WEST | 2006 | 120.6
424 | BUFFALO GAP WIND FARM 2_1 | 06INR0037 | BUFF_GAP_UNIT2_1 | TAYLOR | WIND | WEST | 2007 | 115.5
425 | BUFFALO GAP WIND FARM 2_2 | 06INR0037 | BUFF_GAP_UNIT2_2 | TAYLOR | WIND | WEST | 2007 | 117
426 | BUFFALO GAP WIND FARM 3 | 07INR0030 | BUFF_GAP_UNIT3 | TAYLOR | WIND | WEST | 2008 | 170.2
427 | BULL CREEK WIND PLANT U1 | 07INR0037 | BULLCRK_WND1 | BORDEN | WIND | WEST | 2009 | 88
428 | BULL CREEK WIND PLANT U2 | 07INR0037 | BULLCRK_WND2 | BORDEN | WIND | WEST | 2009 | 90
429 | CALLAHAN WIND | 04INR0013 | CALLAHAN_WND1 | CALLAHAN | WIND | WEST | 2004 | 114
430 | CAMP SPRINGS WIND 1 | 06INR0038 | CSEC_CSECG1 | SCURRY | WIND | WEST | 2007 | 130.5
431 | CAMP SPRINGS WIND 2 | 07INR0040 | CSEC_CSECG2 | SCURRY | WIND | WEST | 2007 | 120
432 | CAPRICORN RIDGE WIND 1 | 07INR0018 | CAPRIDGE_CR1 | STERLING | WIND | WEST | 2007 | 214.5
433 | CAPRICORN RIDGE WIND 2 | 07INR0041 | CAPRIDGE_CR3 | STERLING | WIND | WEST | 2008 | 186
434 | CAPRICORN RIDGE WIND 3 | 07INR0041 | CAPRIDGE_CR2 | STERLING | WIND | WEST | 2007 | 149.5
435 | CAPRICORN RIDGE WIND 4 | 08INR0063 | CAPRIDG4_CR4 | COKE | WIND | WEST | 2008 | 112.5
436 | CEDRO HILL WIND 1 | 09INR0082 | CEDROHIL_CHW1 | WEBB | WIND | SOUTH | 2010 | 75
437 | CEDRO HILL WIND 2 | 09INR0082 | CEDROHIL_CHW2 | WEBB | WIND | SOUTH | 2010 | 75
438 | CHAMPION WIND FARM | 07INR0045d | CHAMPION_UNIT1 | NOLAN | WIND | WEST | 2008 | 126.5
439 | DESERT SKY WIND FARM 1 |  | INDNENR_INDNENR | PECOS | WIND | WEST | 2002 | 84
440 | DESERT SKY WIND FARM 2 |  | INDNENR_INDNENR_2 | PECOS | WIND | WEST | 2002 | 76.5
441 | ELBOW CREEK WIND | 08INR0053 | ELB_ELBCREEK | HOWARD | WIND | WEST | 2008 | 118.7
442 | FOREST CREEK WIND FARM | 05INR0019 | MCDLD_FCW1 | GLASSCOCK | WIND | WEST | 2007 | 124.2
443 | GOAT WIND | 07INR0028 | GOAT_GOATWIND | STERLING | WIND | WEST | 2008 | 80
444 | GOAT WIND 2 | 07INR0028b | GOAT_GOATWIN2 | STERLING | WIND | WEST | 2010 | 69.6
445 | GOLDTHWAITE WIND 1 | 11INR0013 | GWEC_GWEC_G1 | MILLS | WIND | NORTH | 2014 | 148.6
446 | GRANDVIEW 1 (CONWAY) GV1A | 13INR0005a | GRANDVW1_GV1A | CARSON | WIND | PANHANDLE | 2014 | 107.4
447 | GRANDVIEW 1 (CONWAY) GV1B | 13INR0005a | GRANDVW1_GV1B | CARSON | WIND | PANHANDLE | 2014 | 103.8
448 | GREEN MOUNTAIN WIND (BRAZOS) U1 | 03INR0020 | BRAZ_WND_WND1 | SCURRY | WIND | WEST | 2003 | 99
449 | GREEN MOUNTAIN WIND (BRAZOS) U2 | 03INR0020 | BRAZ_WND_WND2 | SCURRY | WIND | WEST | 2003 | 61
450 | HACKBERRY WIND FARM | 04INR0011e | HWF_HWFG1 | SHACKELFORD | WIND | WEST | 2008 | 163.5
451 | HORSE HOLLOW WIND 1 | 05INR0018b | H_HOLLOW_WND1 | TAYLOR | WIND | WEST | 2005 | 206.6
452 | HORSE HOLLOW WIND 2 | 05INR0018a | HHOLLOW2_WIND1 | TAYLOR | WIND | WEST | 2006 | 158
453 | HORSE HOLLOW WIND 3 | 06INR0040 | HHOLLOW3_WND_1 | TAYLOR | WIND | WEST | 2006 | 208
454 | HORSE HOLLOW WIND 4 | 06INR0040 | HHOLLOW4_WND1 | TAYLOR | WIND | WEST | 2006 | 108
455 | INADALE WIND | 07INR0045b | INDL_INADALE1 | NOLAN | WIND | WEST | 2008 | 196.6
456 | INDIAN MESA WIND FARM | 00INR0022 | INDNNWP_INDNNWP | PECOS | WIND | WEST | 2001 | 82.5
457 | JUMBO ROAD WIND 1 | 13INR0059b | HRFDWIND_JRDWIND1 | DEAF SMITH | WIND | PANHANDLE | 2015 | 146.2
458 | JUMBO ROAD WIND 2 | 13INR0059b | HRFDWIND_JRDWIND2 | DEAF SMITH | WIND | PANHANDLE | 2015 | 153.6
459 | KEECHI WIND 138 KV JOPLIN | 14INR0049_2 | KEECHI_U1 | JACK | WIND | NORTH | 2014 | 110
460 | KING MOUNTAIN NE | 00INR0025 | KING_NE_KINGNE | UPTON | WIND | WEST | 2001 | 79.3
461 | KING MOUNTAIN NW | 00INR0025 | KING_NW_KINGNW | UPTON | WIND | WEST | 2001 | 79.3
462 | KING MOUNTAIN SE | 00INR0025 | KING_SE_KINGSE | UPTON | WIND | WEST | 2001 | 40.3
463 | KING MOUNTAIN SW | 00INR0025 | KING_SW_KINGSW | UPTON | WIND | WEST | 2001 | 79.3
464 | LANGFORD WIND POWER | 10INR0026 | LGD_LANGFORD | TOM GREEN | WIND | WEST | 2009 | 155
465 | LONE STAR WIND 1 (MESQUITE) | 04INR0011d | LNCRK_G83 | SHACKELFORD | WIND | WEST | 2006 | 200
466 | LONE STAR WIND 2 (POST OAK) U1 | 04INR0011a | LNCRK2_G871 | SHACKELFORD | WIND | WEST | 2007 | 100
467 | LONE STAR WIND 2 (POST OAK) U2 | 04INR0011a | LNCRK2_G872 | SHACKELFORD | WIND | WEST | 2007 | 100
468 | LORAINE WINDPARK I | 09INR0047 | LONEWOLF_G1 | MITCHELL | WIND | WEST | 2009 | 49.5
469 | LORAINE WINDPARK II | 09INR0047 | LONEWOLF_G2 | MITCHELL | WIND | WEST | 2009 | 51
470 | LORAINE WINDPARK III | 09INR0047 | LONEWOLF_G3 | MITCHELL | WIND | WEST | 2011 | 25.5
471 | LORAINE WINDPARK IV | 09INR0047 | LONEWOLF_G4 | MITCHELL | WIND | WEST | 2011 | 24
472 | MESQUITE CREEK WIND 1 | 09INR0051 | MESQCRK_WND1 | DAWSON | WIND | WEST | 2015 | 105.6
473 | MESQUITE CREEK WIND 2 | 09INR0051 | MESQCRK_WND2 | DAWSON | WIND | WEST | 2015 | 105.6
474 | MIAMI WIND G1 | 14INR0012a | MIAM1_G1 | GRAY | WIND | PANHANDLE | 2014 | 144.3
475 | MIAMI WIND G2 | 14INR0012a | MIAM1_G2 | GRAY | WIND | PANHANDLE | 2014 | 144.3
476 | MCADOO WIND FARM | 08INR0028 | MWEC_G1 | DICKENS | WIND | PANHANDLE | 2008 | 150
477 | NOTREES WIND FARM 1 | 07INR0005 | NWF_NWF1 | WINKLER | WIND | WEST | 2009 | 92.6
478 | NOTREES WIND FARM 2 | 07INR0005 | NWF_NWF2 | WINKLER | WIND | WEST | 2009 | 60
479 | OCOTILLO WIND FARM | 04INR0017 | OWF_OWF | HOWARD | WIND | WEST | 2008 | 58.8
480 | PANHANDLE WIND 1 U1 | 14INR0030a_2 | PH1_UNIT1 | CARSON | WIND | PANHANDLE | 2014 | 109.2
481 | PANHANDLE WIND 1 U2 | 14INR0030a_2 | PH1_UNIT2 | CARSON | WIND | PANHANDLE | 2014 | 109.2
482 | PANHANDLE WIND 2 U1 | 14INR0030b | PH2_UNIT1 | CARSON | WIND | PANHANDLE | 2014 | 94.2
483 | PANHANDLE WIND 2 U2 | 14INR0030b | PH2_UNIT2 | CARSON | WIND | PANHANDLE | 2014 | 96.6
484 | PANTHER CREEK 1 | 07INR0022 | PC_NORTH_PANTHER1 | HOWARD | WIND | WEST | 2008 | 142.5
485 | PANTHER CREEK 2 | 08INR0037 | PC_SOUTH_PANTHER2 | HOWARD | WIND | WEST | 2008 | 115.5
486 | PANTHER CREEK 3 | 11INR0015 | PC_SOUTH_PANTHER3 | HOWARD | WIND | WEST | 2009 | 199.5
487 | PECOS WIND (WOODWARD 1) | 01INR0035 | WOODWRD1_WOODWRD1 | PECOS | WIND | WEST | 2001 | 82.5
488 | PECOS WIND (WOODWARD 2) | 01INR0035 | WOODWRD2_WOODWRD2 | PECOS | WIND | WEST | 2001 | 77.2
489 | PYRON WIND FARM | 07INR0045a | PYR_PYRON1 | SCURRY | WIND | WEST | 2008 | 249
490 | RED CANYON WIND | 05INR0017 | RDCANYON_RDCNY1 | BORDEN | WIND | WEST | 2006 | 84
491 | ROSCOE WIND FARM | 07INR0045e | TKWSW1_ROSCOE | NOLAN | WIND | WEST | 2008 | 209
492 | SAND BLUFF WIND FARM | 05INR0019 | MCDLD_SBW1 | GLASSCOCK | WIND | WEST | 2008 | 90
493 | SENATE WIND | 08INR0011 | SENATEWD_UNIT1 | JACK | WIND | NORTH | 2012 | 150
494 | SHERBINO I WIND | 06INR0012a | KEO_KEO_SM1 | PECOS | WIND | WEST | 2008 | 150
495 | SHERBINO 2 WIND | 06INR0012b | KEO_SHRBINO2 | PECOS | WIND | WEST | 2011 | 147.5
496 | SILVER STAR WIND | 03INR0034 | FLTCK_SSI | EASTLAND | WIND | NORTH | 2008 | 60
497 | SNYDER WIND FARM | 04INR0020 | ENAS_ENA1 | SCURRY | WIND | WEST | 2007 | 63
498 | SOUTH TRENT WIND FARM | 07INR0029 | STWF_T1 | NOLAN | WIND | WEST | 2008 | 98.2
499 | SPINNING SPUR WIND TWO | 13INR0048 | SSPURTWO_WIND_1 | OLDHAM | WIND | PANHANDLE | 2014 | 161
500 | STANTON WIND ENERGY | 07INR0010 | SWEC_G1 | MARTIN | WIND | WEST | 2008 | 120
501 | STEPHENS RANCH WIND 1 | 12INR0034a | SRWE1_UNIT1 | BORDEN | WIND | WEST | 2014 | 211.2
502 | SWEETWATER WIND 1 | 01INR0036 | SWEETWND_WND1 | NOLAN | WIND | WEST | 2003 | 36.6
503 | SWEETWATER WIND 2A | 01INR0036 | SWEETWN2_WND24 | NOLAN | WIND | WEST | 2006 | 15.9
504 | SWEETWATER WIND 2B | 01INR0036 | SWEETWN2_WND2 | NOLAN | WIND | WEST | 2004 | 97.5
505 | SWEETWATER WIND 3A | 01INR0036 | SWEETWN3_WND3A | NOLAN | WIND | WEST | 2011 | 28.5
506 | SWEETWATER WIND 3B | 01INR0036 | SWEETWN3_WND3B | NOLAN | WIND | WEST | 2011 | 100.5
507 | SWEETWATER WIND 4-5 | 07INR0023 | SWEETWN4_WND5 | NOLAN | WIND | WEST | 2007 | 79.2
508 | SWEETWATER WIND 4-4B | 07INR0023 | SWEETWN4_WND4B | NOLAN | WIND | WEST | 2007 | 103.7
509 | SWEETWATER WIND 4-4A | 07INR0023 | SWEETWN4_WND4A | NOLAN | WIND | WEST | 2007 | 117.8
510 | TEXAS BIG SPRING WIND a |  | SGMTN_SIGNALMT | HOWARD | WIND | WEST | 1999 | 27.7
511 | TEXAS BIG SPRING WIND b |  | SGMTN_SIGNALM2 | HOWARD | WIND | WEST | 1999 | 6.6
512 | TRENT WIND FARM | 01INR0038 | TRENT_TRENT | NOLAN | WIND | WEST | 2001 | 150
513 | TRINITY HILLS WIND 1 | 08INR0062 | TRINITY_TH1_BUS1 | YOUNG | WIND | WEST | 2012 | 117.5
514 | TRINITY HILLS WIND 2 | 08INR0062 | TRINITY_TH1_BUS2 | YOUNG | WIND | WEST | 2012 | 107.5
515 | TURKEY TRACK WIND ENERGY CENTER | 07INR0011 | TTWEC_G1 | NOLAN | WIND | WEST | 2008 | 169.5
516 | WEST TEXAS WIND ENERGY |  | SW_MESA_SW_MESA | UPTON | WIND | WEST | 1999 | 80.3
517 | WHIRLWIND ENERGY | 07INR0003 | WEC_WECG1 | FLOYD | WIND | PANHANDLE | 2007 | 57
518 | WHITETAIL WIND ENERGY | 11INR0091 | EXGNWTL_WIND_1 | WEBB | WIND | SOUTH | 2012 | 91
519 | WINDTHORST 2 | 13INR0057 | WNDTHST2_UNIT1 | ARCHER | WIND | WEST | 2014 | 67.6
520 | WKN MOZART WIND | 09INR0061 | MOZART_WIND_1 | KENT | WIND | WEST | 2012 | 30
521 | WOLF RIDGE WIND | 07INR0034 | WHTTAIL_WR1 | COOKE | WIND | NORTH | 2008 | 112.5
522 | TSTC WEST TEXAS WIND |  | DG_ROSC2_1UNIT | NOLAN | WIND | WEST | 2008 | 2
523 | WOLF FLATS WIND (WIND MGT) |  | DG_TURL_UNIT1 | HALL | WIND | PANHANDLE | 2007 | 1
524 | Wind Capacity Sub-total (Non-Coastal Counties) | [6 empty] | 11379.4
525
526 | GULF WIND I | 05INR0015a | TGW_T1 | KENEDY | WIND | COASTAL | 2010 | 141.6
527 | GULF WIND II | 05INR0015a | TGW_T2 | KENEDY | WIND | COASTAL | 2010 | 141.6
528 | LOS VIENTOS WIND I | 11INR0033 | LV1_LV1A | WILLACY | WIND | COASTAL | 2013 | 200.1
529 | LOS VIENTOS WIND II | 11INR0033 | LV1_LV1B | WILLACY | WIND | COASTAL | 2013 | 201.6
530 | MAGIC VALLEY WIND (REDFISH) 1A | 10INR0060 | REDFISH_MV1A | WILLACY | WIND | COASTAL | 2012 | 99.8
531 | MAGIC VALLEY WIND (REDFISH) 1B | 10INR0060 | REDFISH_MV1B | WILLACY | WIND | COASTAL | 2012 | 103.5
532 | PAPALOTE CREEK WIND FARM | 08INR0012a | PAP1_PAP1 | SAN PATRICIO | WIND | COASTAL | 2009 | 179.9
533 | PAPALOTE CREEK WIND FARM II | 08INR0012b | COTTON_PAP2 | SAN PATRICIO | WIND | COASTAL | 2010 | 200.1
534 | PENASCAL WIND 1 | 06INR0022a | PENA_UNIT1 | KENEDY | WIND | COASTAL | 2009 | 160.8
535 | PENASCAL WIND 2 | 06INR0022b | PENA_UNIT2 | KENEDY | WIND | COASTAL | 2009 | 141.6
536 | PENASCAL WIND 3 | 06INR0022b | PENA3_UNIT3 | KENEDY | WIND | COASTAL | 2011 | 100.8
537 | HARBOR WIND |  | DG_NUECE_6UNITS | NUECES | WIND | COASTAL | 2012 | 9
538 | Wind Capacity Sub-total (Coastal Counties) | [6 empty] | 1680.4
539 | Wind Capacity Total (All Counties) | [6 empty] | 13059.8
540
541 | Reliability Must-Run (RMR) Capacity |  | RMR_CAP_CONT |  | GAS |  |  | 0
542
543 | Non-Synchronous Tie Resources
544 | EAGLE PASS TIE |  | DC_S | MAVERICK |  | SOUTH |  | 30
545 | EAST TIE |  | DC_E | FANNIN |  | NORTH |  | 600
546 | LAREDO VFT TIE |  | DC_L | WEBB |  | SOUTH |  | 100
547 | NORTH TIE |  | DC_N | WILBARGER |  | WEST |  | 220
548 | SHARYLAND RAILROAD TIE |  | DC_R | HIDALGO |  | SOUTH |  | 150
549 | SHARYLAND RAILROAD TIE (FUTURE) |  | DC_R2 | HIDALGO |  | SOUTH |  | 20
550 | Non-Synchronous Ties Total | [6 empty] | 1120
551 | Non-Synchronous Ties Capacity Contribution (Top 20 Hours) |  | DCTIE_CAP_CONT |  | OTHER |  |  | 371.4
552
553 | Planned Resources with Executed SGIA, Air Permit, GHG Permit and Water Rights
554 | TEXAS CLEAN ENERGY PROJECT | 13INR0023 |  | ECTOR | COAL | WEST | 2018 | 0
555 | PANDA TEMPLE II CTG1 | 10INR0020b | PANDA_T2_TMPL2CT1 | BELL | GAS | NORTH | 2015 | 218.5
556 | PANDA TEMPLE II CTG2 | 10INR0020b | PANDA_T2_TMPL2CT2 | BELL | GAS | NORTH | 2015 | 218.5
557 | PANDA TEMPLE II STG | 10INR0020b | PANDA_T2_TMPL2ST1 | BELL | GAS | NORTH | 2015 | 353.1
558 | FGE TEXAS I | 16INR0010 |  | MITCHELL | GAS | WEST | 2017 | 0
559 | ANTELOPE STATION IC & CTG | 13INR0028 |  | HALE | GAS | PANHANDLE | 2016 | 0
560 | ECTOR COUNTY ENERGY [ECEC_G1-2] | 14INR0039 |  | ECTOR | GAS | WEST | 2015 | 341
561 | LA PALOMA ENERGY CENTER | 16INR0004 |  | CAMERON | GAS | COASTAL | 2017 | 0
562 | PHR PEAKERS [BAC_CTG1-6] | 14INR0038 |  | GALVESTON | GAS | HOUSTON | 2016 | 0
563 | SKY GLOBAL POWER ONE | 16INR0057 |  | COLORADO | GAS | SOUTH | 2016 | 0
564 | INDECK WHARTON ENERGY CENTER | 15INR0023 |  | WHARTON | GAS | SOUTH | 2017 | 0
565 | PONDERA KING PROJECT | 10INR0022 |  | HARRIS | GAS | HOUSTON | 2017 | 0
566 | PINECREST ENERGY CENTER | 16INR0006 |  | ANGELINA | GAS | NORTH | 2017 | 0
567 | STEC RED GATE IC PLANT | 14INR0040 |  | HIDALGO | GAS | SOUTH | 2016 | 0
568 | OCI ALAMO 5 SOLAR (DOWNIE RANCH) [HELIOS_UNIT1] | 15INR0036 |  | UVALDE | SOLAR | SOUTH | 2015 | 0
569 | EAST PECOS SOLAR | 16INR0073 |  | PECOS | SOLAR | WEST | 2016 | 0
570 | OCI ALAMO 6 SOLAR | 15INR0070_1 |  | PECOS | SOLAR | WEST | 2016 | 0
571 | RE ROSEROCK SOLAR | 16INR0048 |  | PECOS | SOLAR | WEST | 2016 | 0
572 | SUNEDISON BUCKTHORN WESTEX (OAK SOLAR) | 15INR0045 |  | PECOS | SOLAR | WEST | 2017 | 0
573 | Planned Capacity Total (Not Wind) | [6 empty] | 1131.1
574
575 | Planned Wind Resources with Executed SGIA
576 | STEPHENS RANCH PH 2 [SRWE1_SRWE2] | 12INR0034b |  | BORDEN | WIND | WEST | 2015 | 165
577 | MARIAH WIND PH a | 13INR0010a |  | PARMER | WIND | PANHANDLE | 2016 | 0
578 | MARIAH WIND PH b | 13INR0010b |  | PARMER | WIND | PANHANDLE | 2017 | 0
579 | MIDWAY FARMS WIND | 11INR0054 |  | SAN PATRICIO | WIND | COASTAL | 2016 | 0
580 | LONGHORN ENERGY NORTH [LHORN_N_UNIT1-2] | 14INR0023 |  | BRISCOE | WIND | PANHANDLE | 2015 | 200
581 | LONGHORN ENERGY SOUTH | 14INR0023b |  | BRISCOE | WIND | PANHANDLE | 2016 | 0
582 | GRANDVIEW PHASE 2 (CONWAY) | 13INR0005b |  | CARSON | WIND | PANHANDLE | 2016 | 0
583 | SHANNON WIND [SHANNONW_UNIT_1] | 11INR0079a |  | CLAY | WIND | WEST | 2015 | 200
584 | BAFFIN WIND (PENASCAL 3) [BAFFIN_UNIT1-2] | 06INR0022c |  | KENEDY | WIND | COASTAL | 2015 | 202
585 | GUNSIGHT MOUNTAIN WIND | 08INR0018 |  | HOWARD | WIND | WEST | 2015 | 0
586 | BRISCOE WIND FARM | 14INR0072 |  | BRISCOE | WIND | PANHANDLE | 2015 | 150
587 | CAMERON COUNTY WIND | 11INR0057 |  | CAMERON | WIND | COASTAL | 2015 | 165
588 | COMANCHE RUN WIND | 12INR0029 |  | SWISHER | WIND | PANHANDLE | 2016 | 0
589 | CPV RATTLESNAKE DEN PH 1 [RSNAKE_G1-2] | 13INR0020a |  | GLASSCOCK | WIND | WEST | 2015 | 211
590 | CPV RATTLESNAKE DEN PH 2 | 13INR0020b |  | GLASSCOCK | WIND | WEST | 2016 | 0
591 | GREEN PASTURES WIND [GPASTURE_WIND_I & II] | 12INR0070 |  | BAYLOR | WIND | WEST | 2015 | 300
592 | HEREFORD WIND [HRFDWIND_WIND_G & V] | 13INR0059a |  | CASTRO | WIND | PANHANDLE | 2015 | 200
593 | LOGANS GAP WIND I [LGW_UNIT1-2] | 13INR0050 |  | COMANCHE | WIND | NORTH | 2015 | 200
594 | LOS VIENTOS III WIND [LV3_UNIT_1] | 13INR0052 |  | STARR | WIND | SOUTH | 2015 | 200
595 | MIAMI WIND 1b | 14INR0012b |  | GRAY | WIND | PANHANDLE | 2016 | 0
596 | PAMPA WIND | 12INR0018 |  | GRAY | WIND | PANHANDLE | 2017 | 0
597 | PATRIOT WIND (PETRONILLA) | 11INR0062 |  | NUECES | WIND | COASTAL | 2016 | 0
598 | ROUTE 66 WIND [ROUTE_66_WIND1] | 14INR0032a |  | RANDALL | WIND | PANHANDLE | 2015 | 150
599 | SENDERO WIND ENERGY | 12INR0068 |  | JIM HOGG | WIND | SOUTH | 2015 | 0
600 | SOUTH PLAINS WIND I [SPLAIN1_WIND1-2] | 14INR0025a |  | FLOYD | WIND | PANHANDLE | 2015 | 200
601 | SOUTH PLAINS WIND II | 14INR0025b |  | FLOYD | WIND | PANHANDLE | 2016 | 0
602 | SPINNING SPUR 3 [SSPURTWO_SS3WIND1-2] | 14INR0053 |  | OLDHAM | WIND | PANHANDLE | 2015 | 194
603 | WAKE WIND ENERGY | 14INR0047 |  | DICKENS | WIND | PANHANDLE | 2015 | 299
604 | CAPROCK WIND | 10INR0009 |  | CASTRO | WIND | PANHANDLE | 2017 | 0
605 | JAVELINA WIND ENERGY | 13INR0055 |  | ZAPATA | WIND | SOUTH | 2015 | 0
606 | LOS VIENTOS IV WIND | 15INR0037 |  | STARR | WIND | SOUTH | 2016 | 0
607 | LOS VIENTOS V WIND | 15INR0021 |  | STARR | WIND | SOUTH | 2015 | 0
608 | PALO DURO WIND | 15INR0050 |  | DEAF SMITH | WIND | PANHANDLE | 2016 | 0
609 | PANHANDLE WIND PH 3 | 14INR0030c |  | CARSON | WIND | PANHANDLE | 2016 | 0
610 | PULLMAN ROAD WIND | 15INR0079 |  | RANDALL | WIND | PANHANDLE | 2016 | 0
611 | SALT FORK WIND | 14INR0062 |  | GRAY | WIND | PANHANDLE | 2016 | 0
612 | SCANDIA WIND PH d | 13INR0010d |  | PARMER | WIND | PANHANDLE | 2016 | 0
613 | SCANDIA WIND PH e | 13INR0010e |  | PARMER | WIND | PANHANDLE | 2016 | 0
614 | SCANDIA WIND PH f | 13INR0010f |  | PARMER | WIND | PANHANDLE | 2016 | 0
615 | SAN ROMAN WIND | 14INR0013 |  | CAMERON | WIND | COASTAL | 2016 | 0
616 | CHANGING WINDS | 13INR0045 |  | CASTRO | WIND | PANHANDLE | 2016 | 0
617 | ELECTRA WIND | 16INR0062 |  | WILBARGER | WIND | WEST | 2016 | 0
618 | SOUTH PLAINS WIND III | 14INR0025c |  | FLOYD | WIND | PANHANDLE | 2016 | 0
619 | TORRECILLAS WIND A | 14INR0045a |  | WEBB | WIND | SOUTH | 2016 | 0
620 | TORRECILLAS WIND B | 14INR0045b |  | WEBB | WIND | SOUTH | 2016 | 0
621 | Planned Wind Capacity Total | [6 empty] | 3036
622
623 | Planned Wind Capacity Sub-total (Non-Coastal Counties) | [6 empty] | 2669
624 | Planned Wind Capacity Sub-total (by Coastal County)
625 |  |  | CAMERON_NEW_WIND | CAMERON | WIND | COASTAL |  | 165
626 |  |  | WILLACY_NEW_WIND | WILLACY | WIND | COASTAL |  | 0
627 |  |  | KENEDY_NEW_WIND | KENEDY | WIND | COASTAL |  | 202
628 |  |  | KLEBERG_NEW_WIND | KLEBERG | WIND | COASTAL |  | 0
629 |  |  | NUECES_NEW_WIND | NUECES | WIND | COASTAL |  | 0
630 |  |  | SAN_PATRICIO_NEW_WIND | SAN PATRICIO | WIND | COASTAL |  | 0
631 |  |  | REFUGIO_NEW_WIND | REFUGIO | WIND | COASTAL |  | 0
632 |  |  | ARANSAS_NEW_WIND | ARANSAS | WIND | COASTAL |  | 0
633 |  |  | CALHOUN_NEW_WIND | CALHOUN | WIND | COASTAL |  | 0
634 |  |  | MATAGORDA_NEW_WIND | MATAGORDA | WIND | COASTAL |  | 0
635 |  |  | BRAZORIA_NEW_WIND | BRAZORIA | WIND | COASTAL |  | 0
636 | Planned Wind Capacity Sub-total (All Coastal Counties) | [6 empty] | 367
637
638 | Mothballed Resources
639 | SILAS RAY CTG 5 |  | SILASRAY_SILAS_5 | CAMERON | GAS | COASTAL | 1953 | 10
640 | J T DEELY U1 (MOTHBALLED) |  | CALAVERS_JTD1_M | BEXAR | COAL | SOUTH | 2018 | 0
641 | J T DEELY U2 (MOTHBALLED) |  | CALAVERS_JTD2_M | BEXAR | COAL | SOUTH | 2018 | 0
642 | S R BERTRON CTG 2 |  | SRB_SRBGT_2 | HARRIS | GAS | HOUSTON | 1967 | 13
643 | S R BERTRON U1 |  | SRB_SRB_G1 | HARRIS | GAS | HOUSTON | 1958 | 118
644 | S R BERTRON U2 |  | SRB_SRB_G2 | HARRIS | GAS | HOUSTON | 1956 | 174
645 | S R BERTRON U3 |  | SRB_SRB_G3 | HARRIS | GAS | HOUSTON | 1959 | 211
646 | S R BERTRON U4 |  | SRB_SRB_G4 | HARRIS | GAS | HOUSTON | 1960 | 211
647 | Total Mothballed Capacity | [6 empty] | 737
648
649 | Seasonal Mothballed Resources
650 | MARTIN LAKE U3 |  | MLSES_UNIT3 | RUSK | COAL | NORTH | 1979 | 820
651 | MONTICELLO U1 |  | MNSES_UNIT1 | TITUS | COAL | NORTH | 1974 | 572
652 | MONTICELLO U2 |  | MNSES_UNIT2 | TITUS | COAL | NORTH | 1975 | 572
653 | Total Seasonal Mothballed Capacity | [6 empty] | 1964
654
655 | Retiring Resources Unavailable to ERCOT
656 | NORTH TEXAS CTG 1 |  | NTX_NTX_1 | PARKER | GAS | NORTH | 1958 | 0
657 | NORTH TEXAS CTG 2 |  | NTX_NTX_2 | PARKER | GAS | NORTH | 1958 | 0
658 | NORTH TEXAS CTG 3 |  | NTX_NTX_3 | PARKER | GAS | NORTH | 1963 | 0
659 | PERMIAN BASIN SES U6 |  | PBSES_UNIT6 | WARD | GAS | WEST | 1973 | 0
660 | VALLEY SES U1 |  | VLSES_UNIT1 | FANNIN | GAS | NORTH | 1962 | 0
661 | VALLEY SES U2 |  | VLSES_UNIT2 | FANNIN | GAS | NORTH | 1967 | 0
662 | VALLEY SES U3 |  | VLSES_UNIT3 | FANNIN | GAS | NORTH | 1971 | 0
663 | Total Retiring Capacity | [6 empty] | 0

## Background
Release Date: May 4, 2015
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Background
The Seasonal Assessment of Resource Adequacy (SARA) report is a deterministic approach to considering the impact of potential variables that may affect the sufficiency of installed resources to meet the peak electrical demand on the ERCOT System during a particular season.
The standard approach to assessing resource adequacy for one or more years into the future is to account for projected load and resources on a normalized basis and to require sufficient reserves (resources in excess of peak demand, on this normalized basis) to cover the uncertainty in peak demand and resource availability to meet a one-in-ten-years loss-of-load event criteria on a probabilistic basis.
For seasonal assessments that look ahead less than a year, specific information may be available (such as seasonal climate forecasts or anticipated common-mode events such as drought) which can be used to consider the range of resource adequacy in a more deterministic manner.
In contrast to the Capacity, Demand and Reserves (CDR) report, which addresses the sufficiency of planning reserves on an annual basis as described above, the SARA report focuses on the availability of sufficient operating reserves to avoid emergency actions such as deployment of voluntary load reduction resources. Consequently, load reduction resources included in the CDR report, such as Emergency Response Service (ERS) and Load Resources that provide operating reserves (LRs), are excluded from the SARA.
The SARA report is intended to illustrate the range of resource adequacy outcomes that might occur, and thus help fulfill the reporting requirement per Public Utility Commission of Texas rule 25.362(i)(2)(H). Several sensitivity analyses are developed by varying the value of certain parameters that affect resource adequacy. The variation in these parameters is based on historic values of these parameters or adjustments by any known or expected changes.