## Slide 1
March 30, 2015 SCED Event Follow up:
Proposed Improvements
QMWG, May 08, 2015

## Slide 2: Proposed Improvements
For WGRs, set Emergency Base Points (EBP) based on current wind output instead of UDBP
Special treatment for QSGRs during EBP period
  Set EBP as often as needed or automatically after 7mins
  During operator training, review entering appropriate EBP offset during SCED failure
  Possibly create new posting of system available capacity based on HDL (ramp-able room) in System Ancillary Service Capacity Monitor

## Slide 3: Current Emergency Base Point Logic
Currently no special treatment is given for QSGRs and WGRs in EBP calculation
Online unit’s EBP = UDBP when EBP flag was set
+ Rampable room ratio * offset
    If OFFSET>0, Then
    EBP = UDBP + { MAX (0, HDL - UDBP) * OFFSET
    --------------------------------- SUM [ MAX(0, HDL – UDBP)]}
    Else
    EBP = UDBP + { MAX(0, UDBP-LDL) * OFFSET
    -------------------------------- SUM [ MAX(0, UDBP - LDL) ] }
Notes:     EBP logic
    Calculate available capacity for each online unit using HDL – UDBP or UDBP-LDL based on the direction of the Offset
    Calculate the system total available capacity
    Calculate the increment assigned to each online unit based on its available capacity ratio share of the offset,
    Add the increment on top of the unit UDBP when EBP flag was set

## Slide 4: Improvement 1 : EBP to follow WGR output
On March 30th, during SCED failure, WGR output dropped by more than 500MW but EBP was set based on the last SCED UDBP which caused regulation deployment
Proposed change: Base EBP on current output for WGR
    If OFFSET>0, Then
    EBP = GEN + { MAX (0, HDL - GEN) * OFFSET
    --------------------------------- SUM [ MAX( 0, HDL - GEN ) ] }
    Else
    EBP = GEN + { MAX(0, GEN - LDL) * OFFSET
    ---------------------------------- SUM [ MAX(0, GEN -LDL) ] }
Improvement with the change: Reduced regulation deployment during EBP operation.

## Slide 5: Improvement 2 : Commit QSGRs only if needed during EBP
Currently for each positive offset, all QSGRs with ON Resource status will get non-zero EBP proportional to their rampable room resulting in all of those resources to be started up
  During EBP operations, QSGRs will be dispatched only when non-QSGR online units available capacity cannot meet the offset
  QSGRs will be identified with QSGR flag
  QSGR will be kept at current UDBP when their capacity is not needed to meet the offset

## Slide 6: Improvement 3 & 4 : EBP Activation & Offset
Automated EBP activation if not manually activated by operator
  Current way : automatically activated 605sec after SCED failure
  Proposed way : automatically activate EBP 7mins after last valid SCED under normal condition and after 10min during planned events.
Two ways to balance load and maintain frequency using EBP
  Current way : Rely on regulation and put offset to recall regulation
  Proposed way : Put offset in advance based on anticipated need considering the direction of load ramp, wind generation and regulation deployed
Provide operator display showing suggested offset based on forecasted wind, regulation deployment and load change in the next 5 minutes to operator
Provide training to factor in anticipated wind changes and load changes in addition to recalling the current regulation deployments when entering offset

## Slide 7: Improvement 5 : Post SCED Rampable Room
Current AS capacity monitor display shows capacity available to SCED based on HSL
If needed, NPRR can be submitted to add to AS capacity monitor display, new value which shows 5 min rampable room available to SCED.

## Slide 8: Summary of Proposed Changes
For WGRs, set EBP based on current wind output instead of UDBP
During EBP, commit QSGRs only if needed
  Set EBP as often as needed or automatically after 6mins
  During operator training, review entering appropriate EBP offset during SCED failure
  Possibly create new posting of 5min rampable room available to SCED in AS Capacity Monitor display