ERCOT Nodal Protocols

Section 3: Management Activities for the ERCOT System

May 1, 2012

3	MANAGEMENT ACTIVITIES FOR THE ERCOT SYSTEM	3-1

3.1	Outage Coordination	3-1

3.1.1	Role of ERCOT	3-1

3.1.2	Planned Outage or Maintenance Outage Data Reporting	3-2

3.1.3	Rolling 12-Month Outage Planning and Update	3-3

3.1.3.1	Transmission Facilities	3-3

3.1.3.2	Resources	3-3

3.1.4	Communications Regarding Resource and Transmission Facilities Outages	3-3

3.1.4.1	Single Point of Contact	3-3

3.1.4.2	Method of Communication	3-4

3.1.4.3	Reporting for Planned Outages and Maintenance Outages of Resource and Transmission Facilities	3-4

3.1.4.4	Communicating Rejection of Proposed Resource Outages	3-5

3.1.4.5	Management of Resource or Transmission Forced Outages or Maintenance Outages	3-5

3.1.4.6	Notice of Forced Outage or Unavoidable Extension of Planned or Maintenance Outage Due to Unforeseen Events	3-6

3.1.4.7	Outage Coordination of Forecasted Emergency Conditions	3-6

3.1.4.8	Reporting of Forced Derates	3-7

3.1.5	Transmission System Outages	3-7

3.1.5.1	ERCOT Evaluation of Planned Outage and Maintenance Outage of Transmission Facilities	3-7

3.1.5.2	Receipt of TSP Requests by ERCOT	3-8

3.1.5.3	Timelines for Response by ERCOT for TSP Requests	3-9

3.1.5.4	Delay	3-9

3.1.5.5	Opportunity Outage of Transmission Facilities	3-9

3.1.5.6	Rejection Notice	3-10

3.1.5.7	Withdrawal of Approval and Rescheduling of Approved Planned Outages and Maintenance Outages of Transmission Facilities	3-10

3.1.5.8	Priority of Approved Planned Outages	3-11

3.1.5.9	Information for Inclusion in Transmission Facilities Outage Requests	3-11

3.1.5.10	Additional Information Requests	3-12

3.1.5.11	Evaluation of Transmission Facilities Planned Outage or Maintenance Outage Requests	3-12

3.1.5.12	Submittal Timeline for Transmission Facility Outage Requests	3-12

3.1.5.13	Transmission Report	3-13

3.1.6	Outages of Resources Other than Reliability Resources	3-13

3.1.6.1	Receipt of Resource Requests by ERCOT	3-14

3.1.6.2	Resources Outage Plan	3-15

3.1.6.3	Additional Information Requests	3-15

3.1.6.4	Approval of Changes to a Resource Outage Plan	3-15

3.1.6.5	Evaluation of Proposed Short-Noticed Resource Outage	3-16

3.1.6.6	Timelines for Response by ERCOT for Resource Outages	3-18

3.1.6.7	Delay	3-19

3.1.6.8	Resource Outage Rejection Notice	3-19

3.1.6.9	Withdrawal of Approval or Acceptance and Rescheduling of Approved or Accepted Planned Outages of Resource Facilities	3-19

3.1.6.10	Opportunity Outage	3-20

3.1.6.11	Outage Returning Early	3-20

3.1.6.12	Resource Coming On-Line	3-21

3.1.7	Reliability Resource Outages	3-21

3.1.7.1	Timelines for Response by ERCOT on Reliability Resource Outages	3-21

3.1.7.2	Changes to an Approved Reliability Resource Outage Plan	3-22

3.2 	Analysis of Resource Adequacy	3-22

3.2.1	Calculation of Aggregate Resource Capacity	3-22

3.2.2	Demand Forecasts	3-23

3.2.3	System Adequacy Reports	3-23

3.2.4	Statement of Opportunities	3-24

3.2.5	Publication of Resource and Load Information	3-25

3.3	Management of Changes to ERCOT Transmission Grid	3-30

3.3.1	ERCOT Approval of New or Relocated Facilities	3-31

3.3.2	Types of Work Requiring ERCOT Approval	3-31

3.3.2.1	Information to Be Provided to ERCOT	3-31

3.3.2.2	Record of Approved Work	3-33

3.4	Load Zones	3-33

3.4.1	Load Zone Types	3-34

3.4.2	Load Zone Modifications	3-34

3.4.3	NOIE Load Zones	3-34

3.4.4	DC Tie Load Zones	3-35

3.4.5	Additional Load Buses	3-35

3.5	Hubs	3-36

3.5.1	Process for Defining Hubs	3-36

3.5.2	Hub Definitions	3-37

3.5.2.1	North 345 kV Hub (North 345)	3-37

3.5.2.2	South 345 kV Hub (South 345)	3-40

3.5.2.3	Houston 345 kV Hub (Houston 345)	3-43

3.5.2.4	West 345 kV Hub (West 345)	3-45

3.5.2.5	ERCOT Hub Average 345 kV Hub (ERCOT 345)	3-48

3.5.2.6	ERCOT Bus Average 345 kV Hub (ERCOT 345 Bus)	3-49

3.5.3	ERCOT Responsibilities for Managing Hubs	3-52

3.5.3.1	Posting of Hub Buses and Electrical Buses included in Hubs	3-52

3.5.3.2	Calculation of Hub Prices	3-52

3.6	Load Participation	3-52

3.7	Resource Parameters	3-52

3.7.1	Resource Parameter Criteria	3-53

3.7.1.1	Generation Resource Parameters	3-53

3.7.1.2	Load Resource Parameters	3-54

3.7.1.3	Changes in Resource Parameters with Operational Impacts	3-55

3.7.2	Resource Parameter Validation	3-56

3.8	Special Considerations for Split Generation Meters, Combined Cycle Generation Resources, Quick Start Generation Resources, and Hydro Generation Resources	3-56

3.8.1	Split Generation Resources	3-56

3.8.2	Combined Cycle Generation Resources	3-57

3.8.3	Quick Start Generation Resources	3-59

3.8.4	Hydro Generation Resources	3-61

3.9	Current Operating Plan (COP)	3-61

3.9.1	Current Operating Plan (COP) Criteria	3-62

3.9.2	Current Operating Plan Validation	3-67

3.10	Network Operations Modeling and Telemetry	3-68

3.10.1	Time Line for Network Operations Model Changes	3-70

3.10.2	Annual Planning Model	3-72

3.10.3	CRR Network Model	3-72

3.10.4	ERCOT Responsibilities	3-73

3.10.5	TSP Responsibilities	3-75

3.10.6	Resource Entity Responsibilities	3-76

3.10.7	ERCOT System Modeling Requirements	3-76

3.10.7.1	Modeling of Transmission Elements and Parameters	3-76

3.10.7.1.1	Transmission Lines	3-76

3.10.7.1.2	Transmission Buses	3-77

3.10.7.1.3	Transmission Breakers and Switches	3-78

3.10.7.1.4	Transmission and Generation Resource Step-Up Transformers	3-79

3.10.7.1.5	Reactors, Capacitors, and other Reactive Controlled Sources	3-80

3.10.7.2	Modeling of Resources and Transmission Loads	3-80

3.10.7.3	Modeling of Private Use Networks	3-82

3.10.7.4	Definition of Special Protection Systems and Remedial Action Plans	3-83

3.10.7.5	Telemetry Criteria	3-84

3.10.7.5.1	Continuous Telemetry of the Status of Breakers and Switches	3-85

3.10.7.5.2	Continuous Telemetry of the Real-Time Measurements of Bus Load, Voltages, Tap Position, and Flows	3-86

3.10.7.6	Modeling of Generic Transmission Limits	3-88

3.10.8	Dynamic Ratings	3-88

3.10.8.1	Dynamic Ratings Delivered via ICCP	3-89

3.10.8.2	Dynamic Ratings Delivered via Static Table and Telemetered Temperature	3-89

3.10.8.3	Dynamic Rating Network Operations Model Change Requests	3-90

3.10.8.4	ERCOT Responsibilities Related to Dynamic Ratings	3-90

3.10.8.5	Transmission Service Provider Responsibilities Related to Dynamic Ratings	3-91

3.10.9	State Estimator Performance Standard	3-91

3.10.9.1	Considerations for Performance Standards	3-92

3.10.9.2	Telemetry and State Estimator Performance Monitoring	3-93

3.11	Transmission Planning	3-93

3.11.1	Overview	3-93

3.11.2	Planning Criteria	3-93

3.11.3	Regional Planning Group	3-95

3.11.4	Regional Planning Group Project Review Process	3-95

3.11.4.1	Project Submission	3-95

3.11.4.2	Project Comment Process	3-95

3.11.4.3	Categorization of Proposed Transmission Projects	3-95

3.11.4.4	Tier 4	3-96

3.11.4.5	Tier 3	3-96

3.11.4.6	Tier 2	3-97

3.11.4.7	Tier 1	3-97

3.11.4.8	Determine Designated Providers of Transmission Additions	3-98

3.11.4.9	Regional Planning Group Acceptance and ERCOT Endorsement	3-98

3.11.4.10	Modifications to ERCOT Endorsed Projects	3-99

3.11.5	Assessment of Chronic Congestion	3-99

3.11.6	Generation Interconnection Process	3-100

3.12	Load Forecasting	3-100

3.12.1	Seven-Day Load Forecast	3-100

3.13	Renewable Production Potential Forecasts	3-101

3.14	Contracts for Reliability Resources and EILS Loads	3-101

3.14.1	Reliability Must Run	3-102

3.14.1.1	Notification of Suspension of Operations	3-104

3.14.1.2	ERCOT Evaluation	3-105

3.14.1.3	ERCOT Report to Board on Signed RMR Agreements	3-106

3.14.1.4	Exit Strategy from an RMR Agreement	3-107

3.14.1.5	Potential Alternatives to RMR Agreements	3-107

3.14.1.6	Transmission System Upgrades Associated with an RMR and/or MRA Exit Strategy	3-108

3.14.1.7	RMR or MRA Contract Termination	3-109

3.14.1.8	RMR and/or MRA Contract Extension	3-110

3.14.1.9	Generation Resource Return to Service Updates	3-111

3.14.1.10	Eligible Costs	3-112

3.14.1.11	Budgeting Eligible Costs	3-113

3.14.1.12	Reporting Actual Eligible Cost	3-115

3.14.1.13	Incentive Factor	3-115

3.14.1.14	Major Equipment Modifications	3-116

3.14.1.15	Budgeting Fuel Costs	3-116

3.14.1.16	Reporting Actual Eligible Fuel Costs	3-116

3.14.2	Black Start	3-117

3.14.3	Emergency Interruptible Load Service (EILS)	3-118

3.14.3.1	Emergency Response Service Procurement	3-124

3.14.3.2	Emergency Response Service Self-Provision	3-128

3.14.3.3	Emergency Response Service Provision and Technical Requirements	3-129

3.14.3.4	Emergency Response Service Reporting and Market Communications	3-131

3.15	Voltage Support	3-132

3.15.1	ERCOT Responsibilities Related to Voltage Support	3-136

3.15.2	DSP Responsibilities Related to Voltage Support	3-136

3.15.3	QSE Responsibilities Related to Voltage Support	3-137

3.16	Standards for Determining Ancillary Service Quantities	3-138

3.17	Ancillary Service Capacity Products	3-139

3.17.1	Regulation Service	3-139

3.17.2	Responsive Reserve Service	3-140

3.17.3	Non-Spinning Reserve Service	3-140

3.18	Resource Limits in Providing Ancillary Service	3-141

3.19	Constraint Competitiveness Tests	3-142

3.19.1	Annual Competitiveness Test	3-143

3.19.2	Monthly Competitiveness Test	3-146

3.19.3	Daily Competitiveness Test	3-147

3.20	Process for Redacting State Estimator Data for Real-Time Publication	3-147

3.20.1	Methodology for Redaction of State Estimator Data	3-148

3.20.2 	Methodology of Identification of Redacted Load	3-148

# MANAGEMENT ACTIVITIES FOR THE ERCOT SYSTEM

This section focuses on the management activities, including Outage Coordination, Resource Adequacy, Load forecasting, transmission operations and planning, and contracts for Ancillary Services for the ERCOT System.

3.1	Outage Coordination

“Outage Coordination” is the management of Transmission Facilities Outages and Resource Outages in the ERCOT System. Facility owners are solely and directly responsible for the performance of all maintenance, repair, and construction work, whether on energized or de-energized facilities, including all activities related to providing a safe working environment.

3.1.1	Role of ERCOT

(1)	ERCOT shall coordinate and use reasonable efforts, consistent with Good Utility Practice, to accept, approve or reject all Outage schedules for maintenance, repair, and construction of both Transmission Facilities and Resources within the ERCOT System.  ERCOT may reject an Outage schedule under certain circumstances, as set forth in these Protocols.

(2)	ERCOT’s responsibilities with respect to Outage Coordination include:

(a)	Approving or rejecting requests for Planned Outages and Maintenance Outages of Transmission Facilities for Transmission Service Providers (TSPs) in coordination with and based on information regarding all Entities’ Planned Outages and Maintenance Outages;

(b)	Assessing the adequacy of available Resources, based on planned and known Resource Outages, relative to forecasts of Load, Ancillary Service requirements,  and reserve requirements;

(c)	Coordinating and approving or rejecting schedules for Planned Outages of Resources scheduled to occur within eight days after request;

[NPRR365: Replace paragraph (2)(c) above with the following upon system implementation and fulfillment of staffing requirements:] (c) Coordinating and approving or rejecting schedules for Planned Outages of Resources scheduled to occur within 45 days after request;

(d)	Coordinating and approving or rejecting schedules for Planned Outages of Reliability Must-Run (RMR) Units under the terms of the applicable RMR Agreements;

(e)	Coordinating and approving or rejecting Outages associated with Black Start Resources under the applicable Black Start Unit Agreements;

(f)	Reviewing and coordinating changes to existing 12-month Resource Outage plans to determine how changes will affect ERCOT System reliability, including Resource Outages not previously included in the Outage plan;

(g)	Monitoring how Planned Outage schedules compare with actual Outages;

(h)	Posting all proposed and approved schedules for Planned Outages and Maintenance Outages of Transmission Facilities on the Market Information System (MIS) Secure Area under Section 3.1.5.13, Transmission Report;

(i)	Creating aggregated schedules of Planned Outages for Resources and posting those schedules on the MIS Secure Area under Section 3.2.3, System Adequacy Reports;

(j)	Monitoring Transmission Facilities and Resource Forced Outages and Maintenance Outages of immediate nature and implementing responses to those Outages as provided in these Protocols;

(k)	Establishing and implementing communication procedures:

(i)	For a TSP to request approval of Transmission Facilities Planned Outage and Maintenance Outage schedules; and

(ii)	For a Resource Entity’s designated Single Point of Contact to submit Outage plans and to coordinate Resource Outages;

(l)	Establishing and implementing record-keeping procedures for retaining all requested Planned Outages, Maintenance Outages, and Forced Outages;

(m)	Planning and analyzing Transmission Facilities Outages; and

(n)	Working with the appropriate Technical Advisory Committee (TAC) Subcommittee to develop procedures for characterizing a Simple Transmission Outage.

3.1.2	Planned Outage or Maintenance Outage Data Reporting

Each Resource Entity and Transmission Service Provider (TSP) shall use reasonable efforts, consistent with Good Utility Practice, to continually update its Outage Schedule.  All information submitted about Planned Outages or Maintenance Outages must be submitted by the Resource Entity or the TSP under this Section.  If an Outage Schedule for a Resource is also applicable to the Current Operating Plan (COP), the Qualified Scheduling Entity (QSE) responsible for the Resource shall also update the COP to provide the same information describing the Outage.

3.1.3	Rolling 12-Month Outage Planning and Update

3.1.3.1	Transmission Facilities

(1)	Each TSP shall provide to ERCOT a Planned Outage or Maintenance Outage plan in an ERCOT-provided format for the next 12 months updated monthly.  Planned Outage or Maintenance Outage scheduling data for Transmission Facilities must be kept current.  Updates must identify all changes to any previously proposed Planned Outages or Maintenance Outages and any additional Planned Outages or Maintenance Outage anticipated over the next 12 months.  ERCOT shall coordinate in-depth reviews of the 12-month plan with each TSP at least twice per year.

[NPRR219: Insert paragraph (2) upon system implementation:] (2) ERCOT shall report statistics on how TSP Planned Outages compare with actual TSP Outages, post those statistics to the MIS Secure Area, and report those statistics to ERCOT subcommittees twice per year. However, to the extent Outages are required to repair or improve telemetry accuracy or failures, or to provide near-term solutions to Planning Criteria violations as described in Section 3.11.2, Planning Criteria, the Outage must not be counted against the TSP in its performance of planning Outages, because such Outages cannot reasonably be forecasted 12 months in advance.

3.1.3.2	Resources

(1)	Each Resource Entity shall provide to ERCOT a Planned Outage and Maintenance Outage plan for Generation Resources in an ERCOT-provided format for the next 12 months updated monthly.  Planned Outage and Maintenance Outage scheduling data must be kept current.  Updates, through an electronic interface as specified by ERCOT, must identify any changes to previously proposed Planned Outages or Maintenance Outages and any additional Planned Outages or Maintenance Outages anticipated over the next 12 months.

(2)	ERCOT shall report statistics monthly on how Resource Planned Outages compare with actual Resource Outages, and post those statistics to the MIS Secure Area.

3.1.4	Communications Regarding Resource and Transmission Facilities Outages

3.1.4.1	Single Point of Contact

(1)	All communications concerning a Planned Outage or Maintenance Outage must be between ERCOT and the designated “Single Point of Contact” for each TSP or Resource Entity.  All nonverbal communications concerning Planned Outages must be conveyed through an electronic interface as specified by ERCOT.  The TSP or Resource Entity shall identify, in its initial request or response, the Single Point of Contact, with primary and alternate means of communication.  The Resource Entity or TSP shall submit a Notice of Change of Information (NCI) form when changes occur to a Single Point of Contact.  This identification must be confirmed in all communications with ERCOT regarding Planned Outage or Maintenance Outage requests.

(2)	The Single Point of Contact must be either a person or a position available seven days per week and 24 hours per day for each Resource Entity and TSP.  The Resource Entity shall designate its QSE as its Single Point of Contact.  The designated Single Point of Contact for a Generation Resource that has been split into two or more Split Generation Resources shall be the Master QSE.  The Single Point of Contact for the TSP must be designated under the ERCOT Operating Guides.

3.1.4.2	Method of Communication

ERCOT, each TSP, and each Resource Entity shall communicate according to ERCOT procedures under these Protocols.  All submissions, changes, approvals, rejections, and withdrawals regarding Outages must be processed through the ERCOT Outage Scheduler on the ERCOT programmatic interface, except for Forced Outages and Maintenance Level I Outages, which must be communicated to ERCOT immediately via the Current Operating Plan if submitted for a Resource and using the Outage Scheduler if submitted by a TSP.  This does not prohibit any verbal communication when the situation warrants it.  ERCOT shall develop guidelines for the types of events that may require verbal communication.

3.1.4.3	Reporting for Planned Outages and Maintenance Outages of Resource and Transmission Facilities

(1)	Each Resource Entity and TSP shall submit information regarding proposed Planned Outages and Maintenance Outages of Transmission Facilities or Generation Resources under procedures adopted by ERCOT.  The obligation to submit that information applies to each Resource Entity that is responsible to operate or maintain a Generation Resource that is part of or that affects the ERCOT System.  The obligation to submit that information applies to each TSP or Resource Entity that is responsible to operate or maintain Transmission Facilities that are part of or affect the ERCOT System.  A Resource Entity or TSP is also obligated to submit information for Transmission Facilities or Generation Resources that are not part of the ERCOT System or that do not affect the ERCOT System if that information is required for regional security coordination as determined by ERCOT.

(2)	Before taking an RMR or Black Start Resource (“Reliability Resources”) out of service for a Planned Outage or Maintenance Outage, the Single Point of Contact for that Reliability Resource must obtain ERCOT’s approval of the schedule of the Planned Outage or Maintenance Outage.  ERCOT shall review and approve or reject each proposed Planned Outage or Maintenance Outage Schedule under this Section and the applicable Agreements.

3.1.4.4	Communicating Rejection of Proposed Resource Outages

(1)	This subsection applies to certain proposed Resource Outages submitted eight days or less prior to the Outage start date that are either:

(a)	Proposed changes to Planned Outages; or

(b)	Newly-proposed Resource Outages.

(2)	If a proposal under paragraph (1) above (“Proposed Short-Noticed Resource Outage”), in conjunction with Outages that have been previously approved or accepted, would cause a violation of applicable reliability standards, ERCOT shall communicate with the requesting Market Participant and each other Market Participant with a relevant Outage that was previously approved or accepted to try to identify how to adjust any of the proposed and approved or accepted Outages.

[NPRR365: Delete Section 3.1.4.4 above and renumber accordingly upon system implementation and fulfillment of staffing requirements.]

3.1.4.5	Management of Resource or Transmission Forced Outages or Maintenance Outages

(1)	In the event of a Forced Outage, after the affected equipment is removed from service, the Resource Entity or QSE, as appropriate, or TSP must notify ERCOT as soon as practicable of its action by:

(a)	For Resource Outages:

(i)	changing the telemetered Resource Status appropriately, including a text description when it becomes known, of the cause of the Forced Outage; and

(ii)	updating the Current Operating Plan; and

(iii)	updating the Outage Scheduler, if necessary.

(b)	For Transmission Facilities Forced Outages:

(i)	changing the telemetered status of the affected Transmission Elements; and

(ii)	updating the Outage Scheduler with the expected return-to-service time.

(2)	Forced Outages may require ERCOT to review and withdraw approval of previously approved or accepted, as applicable, Planned Outage or Maintenance Outage schedules to ensure reliability.

(3)	For Maintenance Outages, the Resource Entity or QSE, as appropriate, or TSP shall notify ERCOT of any Resource or Transmission Facilities Maintenance Outage according to the Maintenance Outage Levels by updating the Current Operating Plan and Outage Scheduler.  ERCOT shall coordinate the removal of facilities from service within the defined timeframes as specified by the TSP, QSE or Resource Entity in its notice to ERCOT.

(4)	ERCOT may require supporting information describing Forced Outages and Maintenance Outages.  ERCOT may reconsider and withdraw approvals of other previously approved Transmission Facilities Outage or an Outage of a Reliability Resource as a result of Forced Outages or Maintenance Outages, if necessary, in ERCOT’s determination to protect system reliability.  When ERCOT approves a Maintenance Outage, ERCOT shall coordinate timing of the appropriate course of action under these Protocols.

(5)	Removal of a Resource or Transmission Facilities from service under Maintenance Outages must be coordinated with ERCOT.  To minimize harmful impacts to the system in urgent situations, the equipment may be removed immediately from service, provided notice is given immediately, by the Resource Entity or TSP, to ERCOT of such action.

3.1.4.6	Notice of Forced Outage or Unavoidable Extension of Planned or Maintenance Outage Due to Unforeseen Events

(1)	If a Planned or Maintenance Outage is not completed within the ERCOT-approved timeframe and the Transmission Facilities or Resources are in such a condition that they cannot be restored at the Outage schedule completion date, the requesting party shall submit to ERCOT a Forced Outage (unavoidable extension) form describing the extension of the Outage and providing a revised return date.

(2)	Any Forced Outage that occurs in Real-Time must be entered into the Outage Scheduler if it is to remain an Outage for longer than two hours.

(3)	If the QSE is to receive the exemption described in paragraph (5)(d) of Section 8.1.1.4.1, Regulation Service and Generation Resource/Controllable Load Resource Energy Deployment Performance, the QSE will notify ERCOT Operators by voice communication of every Forced Outage, Forced Derate, or Startup Loading Failure within 15 minutes.

3.1.4.7	Outage Coordination of Forecasted Emergency Conditions

(1)	If ERCOT forecasts an inability to meet applicable reliability standards and it has exercised all other reasonable options, ERCOT shall inform the Single Point of Contact for any affected Market Participant and all QSEs verbally and in electronic form by declaring an Emergency Condition according to Section 6.5.9.3, Communication Under Emergency Conditions.

(2)	Under an Emergency Condition and if ERCOT cannot meet applicable reliability standards, ERCOT may discuss the reliability problem with Resource Entities, TSPs, and DSPs to reach mutually agreeable solutions where Outages are negatively affecting system reliability.  Actions may include changes to Outage schedules and the Current Operating Plan.

3.1.4.8	Reporting of Forced Derates

The Resource Entity or its designee must enter Forced Derates that are expected to last more than 48 hours into the Outage Scheduler.

3.1.5	Transmission System Outages

3.1.5.1	ERCOT Evaluation of Planned Outage and Maintenance Outage of Transmission Facilities

(1)	TSPs and Resource Entities shall request a Planned Outage or Maintenance Outage for their respective Transmission Facilities (i.e. Transmission Facilities owned by such Entities) that are part of the ERCOT Transmission Grid and defined in the Network Operations Model.  For Resource Entities within a Private Use Network, this only includes Transmission Facilities at the Point of Interconnection (POI).  Specifically, such requests shall be made when a relevant Transmission Facility will be removed from its normal service.  For TSP requests, the TSPs shall enter such requests in the Outage Scheduler.  For Resource Entity requests, ERCOT shall enter such requests in the Outage Scheduler on behalf of the Resource Entity.  ERCOT’s obligation to enter outage requests for Resource Entities is valid only for the purposes of Transmission Facilities Outage Scheduler entry requirements prescribed by the ERCOT Protocols and Operating Guides. ERCOT’s obligations hereunder do not create any legal obligation or responsibility related to any other legal obligations applicable to a Resource Entity.  ERCOT’s obligation shall terminate upon the implementation of system changes that enable Resource Entities to perform this function.  Planned Outages or Maintenance Outages for Electrical Buses will be treated as consequentially outaged Transmission Elements.  In those cases where a TSP enters the breaker and switch statuses associated with an Electrical Bus, a downstream topology processor will evaluate the breakers and switches associated with the applicable Electrical Bus to determine if the Electrical Bus is consequentially outaged, and to thereby designate the status of the Electrical Bus.  Proposed Transmission Planned Outage or Maintenance Outage information submitted by a TSP or Resource Entity in accordance with this Section constitutes a request for ERCOT’s approval of the Outage Schedule associated with the Planned Outage or Maintenance Outage.  ERCOT is not deemed to have approved the Outage Schedule associated with the Planned Outage or Maintenance Outage until ERCOT notifies the TSP or Resource Entity of its approval under procedures adopted by ERCOT.  Once ERCOT posts a Resource Entity Transmission Facility Outage request on the MIS Secure Area, the Resource Entity shall review the submitted Outage for accuracy and request that ERCOT submit modifications if necessary.  ERCOT shall evaluate requests under Section 3.1.5.11, Evaluation of Transmission Facilities Planned Outage or Maintenance Outage Requests.

[NPRR219: Replace paragraph (1) above with the following upon system implementation:] (1) A TSP or Resource Entity shall request a Planned Outage or Maintenance Outage when any Transmission Facility that is part of the ERCOT Transmission Grid and defined in the Network Operations Model will be removed from its normal service. For Resource Entities within a Private Use Network, this only includes Transmission Facilities at the Point of Interconnection (POI). For TSP requests, the TSPs shall enter such requests in the Outage Scheduler. For Resource Entity requests, the Resource Entity shall enter such requests in the Outage Scheduler. Planned Outages or Maintenance Outages for Electrical Buses will be treated as consequentially outaged Transmission Elements. In those cases where a TSP enters the breaker and switch statuses associated with an Electrical Bus, a downstream topology processor will evaluate the breakers and switches associated with the applicable Electrical Bus to determine if the Electrical Bus is consequentially outaged, and to thereby designate the status of the Electrical Bus. Proposed Transmission Planned Outage or Maintenance Outage information submitted by a TSP or Resource Entity in accordance with this Section constitutes a request for ERCOT’s approval of the Outage Schedule associated with the Planned Outage or Maintenance Outage. ERCOT is not deemed to have approved the Outage Schedule associated with the Planned Outage or Maintenance Outage until ERCOT notifies the TSP or Resource Entity of its approval under procedures adopted by ERCOT. ERCOT shall evaluate requests under Section 3.1.5.11, Evaluation of Transmission Facilities Planned Outage or Maintenance Outage Requests.

(2)	ERCOT shall review and approve Planned Outages and Maintenance Outages of Transmission Facilities schedules.  ERCOT shall transmit its approvals and rejections to TSPs via the ERCOT Outage Scheduler.  Once approved, ERCOT may not withdraw its approval except under the conditions described in Section 3.1.5.7, Withdrawal of Approval and Rescheduling of Approved Planned Outages and Maintenance Outages of Transmission Facilities.

(3)	Private Use Network Outage requests submitted pursuant to this Section shall not be publicly posted.

3.1.5.2	Receipt of TSP Requests by ERCOT

ERCOT shall acknowledge each request for approval of a Transmission Planned Outage schedule within two Business Hours of the receipt of the request.  ERCOT may request additional information or seek clarification from the TSP regarding the information submitted for a proposed Planned Outage or Maintenance Outage for Transmission Facilities.

3.1.5.3	Timelines for Response by ERCOT for TSP Requests

(1)	For Transmission Facilities Outages, ERCOT shall approve or reject each request in accordance with the following table:

| Amount of time between the request for approval of the proposed Outage and the scheduled start date of the proposed Outage: | ERCOT shall approve or reject no later than: |
| --- | --- |
| Three days | 1800 hours, two days before the start of the proposed Outage |
| Between four and eight days | 1800 hours, three days before the start of the proposed Outage |
| Between nine days and 45 days | Four days before the start of the proposed Outage |
| Between 46 and 90 days | 30 days before the start of the proposed Outage |
| Greater than 90 days | 75 days before the start of the proposed Outage |

(2)	For Outages scheduled at least three days before the scheduled start date of the proposed Outage, ERCOT shall make reasonable attempts to accommodate unusual circumstances that support TSP requests for approval earlier than required by the schedule above.

(3)	If circumstances prevent adherence to these timetables, ERCOT shall discuss the request status and reason for the delay of the approval with the requesting TSP and make reasonable attempts to mitigate the effect of the delay on the TSP.

(4)	When ERCOT rejects a request for an Outage, ERCOT shall provide the TSP, in written or electronic form, suggested amendments to the schedules of a Planned Outage or Maintenance Outage of Transmission Facilities.  Any such suggested amendments accepted by the TSP must be processed by ERCOT as a Planned Outage or Maintenance Outage of Transmission Facilities request under this Section.

3.1.5.4	Delay

ERCOT may delay its approval or rejection of a proposed Planned Outage or Maintenance Outage of a Transmission Facilities schedule if the requesting TSP has not submitted sufficient or complete information within the time frames set forth in these Protocols.

3.1.5.5	Opportunity Outage of Transmission Facilities

Opportunity Outages of Transmission Facilities may be approved under Section 3.1.6.10, Opportunity Outage.

3.1.5.6	Rejection Notice

(1)	If ERCOT rejects a request, ERCOT shall provide the TSP a written or electronic rejection notice that includes:

(a)	Specific concerns causing the rejection;

(b)	Possible remedies or transmission schedule revisions, if any that might mitigate the basis for rejection; and

(c)	An electronic copy of the ERCOT study case for review by the TSP.

(2)	ERCOT may reject a Planned Outage or Maintenance Outage of Transmission Facilities only:

(a)	To protect system reliability or security;

(b)	Due to insufficient information regarding the Outage; or

(c)	Due to failure to comply with submittal process requirements, as specified in these Protocols.

(3)	When multiple proposed Planned Outages or Maintenance Outages cause a reliability or security concern, ERCOT shall:

(a)	Communicate with each TSP to see if the TSP will adjust its proposed Planned Outage or Maintenance Outage schedule;

(b)	Determine if each TSP will agree to an alternative Outage schedule; or

(c)	Reject, in ERCOT’s sole discretion, one or more proposed Outages, considering order of receipt and impact on the ERCOT Transmission Grid.

3.1.5.7	Withdrawal of Approval and Rescheduling of Approved Planned Outages and Maintenance Outages of Transmission Facilities

(1)	If ERCOT believes it cannot meet the applicable reliability standards and has exercised reasonable options, ERCOT may contact the TSP for more information prior to its withdrawal of the approval for a Planned Outage or Maintenance Outage schedule.  ERCOT shall inform the affected TSP both orally and in written or electronic form as soon as ERCOT identifies a situation that may lead to the withdrawal of ERCOT’s approval.  If ERCOT withdraws its approval, the TSP may submit a new request for approval of the Planned Outage or Maintenance Outage schedule provided the new request meets the submittal requirements for Outage Scheduling.  If ERCOT withdraws approval of Planned Outages and Maintenance Outages of Transmission Facilities, ERCOT shall post notice through the MIS Secure Area as soon as practicable but not later than one hour of the change to inform Market Participants.

(2)	In determining whether to withdraw approval, ERCOT shall duly consider whether the Planned Outage or Maintenance Outage affects public infrastructure if ERCOT is made aware of such potential impacts by the TSP (e.g., impacts on highways, ports, municipalities, and counties).

3.1.5.8	Priority of Approved Planned Outages

In considering TSP requests, ERCOT shall give priority to approved Planned Outage and Maintenance Outage schedules previously posted to the MIS Secure Area.

3.1.5.9	Information for Inclusion in Transmission Facilities Outage Requests

Transmission Facilities Outage requests submitted by a TSP must include the following Transmission Facilities-specific information:

(a)	The identity of the Transmission Facilities, in the Network Operations Model, including TSP and location;

(b)	The nature of the work, by predefined classifications, to be performed during the proposed Transmission Facilities Outage;

(c)	The preferred start and finish dates for the proposed Transmission Planned or Maintenance Outage;

(d)	The time required to: (i) finish the Transmission Planned Outage or  Maintenance Outage and (ii) restore the Transmission Facilities to normal operation;

(e)	Primary and alternate telephone numbers for the TSP’s Single Point of Contact, as described in Section 3.1.4.1, Single Point of Contact, and the name of the individual submitting the information;

(f)	The scheduling flexibility (i.e., the earliest start date and the latest finish date for the Outage);

(g)	Any Transmission Facilities that must be out of service to facilitate the TSP’s request;

(h)	Any remedial actions or special protection systems necessary during the Outage and the contingency that would require the remedial action or relay action; and

(i)	Any other relevant information related to the proposed Outage or any unusual risks affecting the schedule.

3.1.5.10	Additional Information Requests

The requesting TSP shall comply with any ERCOT requests for more information about, or for clarification of, the information submitted by the TSP for a proposed Outage.

3.1.5.11	Evaluation of Transmission Facilities Planned Outage or Maintenance Outage Requests

(1)	ERCOT shall evaluate requests, approve, or reject Transmission Facilities Planned Outages and Maintenance Outages according to the requirements of this section.  ERCOT may approve Outage requests provided the Outage in combination with other proposed Outages does not cause a violation of applicable reliability standards.  ERCOT shall reject Outage requests that do not meet the submittal timeline specified in Section 3.1.5.12, Submittal Timeline for Transmission Facility Outage Requests.  ERCOT shall consider the following factors in its evaluation:

(a)	Forecasted conditions during the time of the Outage;

(b)	Outage plans submitted by Resource Entities and TSPs under Section 3.1, Outage Coordination;

(c)	Forced Outages of Transmission Facilities;

(d)	Potential for the proposed Outages to cause irresolvable transmission overloads or voltage supply concerns based on the indications from contingency analysis software;

(e)	Previously approved Planned Outages and Maintenance Outages;

(f)	Impacts on the transfer capability of DC Ties; and

(g)	Good Utility Practice for Transmission Facilities maintenance.

(2)	When ERCOT approves a Maintenance Outage, ERCOT shall coordinate the timing of the appropriate course of action with the requesting TSP.

3.1.5.12	Submittal Timeline for Transmission Facility Outage Requests

TSPs shall submit all requests for Planned Outages and Maintenance Outages or changes to existing approved Outages of Transmission Elements in the Network Operations Model to ERCOT no later than the minimum amount of time between the submittal of a request to ERCOT for approval of a proposed Outage and the scheduled start date of the proposed Outage, according to the following table:

| Type of Outage | Minimum amount of time between the Outage request and the scheduled start date of the proposed Outage: | Minimum amount of time between any change to an Outage request and the scheduled end date an existing Outage: |
| --- | --- | --- |
| Forced Outage | Immediate | Immediate |
| Maintenance Outage Level I | Immediate | Immediate |
| Maintenance Outage Level II | Two days [1] | Two days [1] |
| Maintenance Outage Level III | Three days | Three days |
| Planned Outage | Three days | Three days |
| Simple Transmission Outage | One day | One day |

Note:

1.	For reliability purposes, ERCOT may reduce to one day on a case-by-case basis.

3.1.5.13	Transmission Report

ERCOT shall post on the MIS Secure Area:

(a)	All proposed Transmission Facilities Outages that have not yet been approved or rejected within one hour of receipt by ERCOT; and

(b) 	Any approved, accepted or rejected Transmission Facilities Outage within one hour of approval, acceptance or rejection of the Outage.

3.1.6	Outages of Resources Other than Reliability Resources

(1)	ERCOT shall accept all Outage schedules and changes to Outage schedules for a Resource other than a reliability Resource submitted to ERCOT more than eight days before the proposed start date of the Outage.

(2)	If a Resource Entity plans to start a Planned or Maintenance Outage within eight days that has not been previously included in the Resource’s written Planned Outage and Maintenance Outage plan, then the Resource Entity must immediately notify ERCOT and include in its notice whether the Outage is a Forced Outage, Maintenance (Level I, II, or III) Outage, or Planned Outage.  ERCOT’s response to this notification must comply with these requirements:

(a)	ERCOT shall accept Forced and Levels I, II, and III Maintenance Outage proposals, and ERCOT shall coordinate the Outages within the time frames specified in these Protocols.

(b)	ERCOT shall accept Planned Outage proposals, except that ERCOT shall reject an Outage proposal if it will impair ERCOT’s ability to meet applicable reliability standards and other solutions cannot be exercised.

(c)	ERCOT shall accept Forced and Maintenance Outage plans from a Qualifying Facility (QF) that result from the outage of the QF’s thermal host facility.

[NPRR365: Replace Section 3.1.6 above with the following upon system implementation and fulfillment of staffing requirements:] 3.1.6 Outages of Resources Other than Reliability Resources (1) ERCOT shall accept all Outage schedules and changes to Outage schedules for a Resource other than a reliability Resource submitted to ERCOT more than 45 days before the proposed start date of the Outage. (2) If a Resource Entity plans to start a Planned or Maintenance Outage within 45 days that has not been previously included in the Resource’s written Planned Outage and Maintenance Outage plan, then the Resource Entity must immediately notify ERCOT and include in its notice whether the Outage is a Forced Outage, Maintenance (Level I, II, or III) Outage, or Planned Outage. ERCOT’s response to this notification must comply with these requirements: (a) ERCOT shall accept Forced and Levels I, II, and III Maintenance Outage proposals, and ERCOT shall coordinate the Outages within the time frames specified in these Protocols. (b) ERCOT shall approve Planned Outage proposals, except that ERCOT shall reject an Outage proposal if it will impair ERCOT’s ability to meet applicable reliability standards and other solutions cannot be exercised. (c) ERCOT shall accept Forced and Maintenance Outage plans from a Qualifying Facility (QF) that result from the outage of the QF’s thermal host facility.

3.1.6.1	Receipt of Resource Requests by ERCOT

ERCOT shall acknowledge each request for approval of a Resource Planned Outage schedule within two Business Hours of the receipt of the request.  ERCOT may request additional information or seek clarification from the Resource Entity regarding the information submitted for a proposed Planned Outage or Maintenance Outage for Resource Facilities.

3.1.6.2	Resources Outage Plan

(1)	Resource Entity Outage requests shall include the following information:

(a)	The primary and alternate phone number of the Resource Entity’s Single Point of Contact for Outage Coordination;

(b)	The Resource identified by the name in the Network Operations Model;

(c)	The net megawatts of capacity the Resource Entity anticipates will be available during the Outage (if any);

(d)	The estimated start and finish dates for each Planned and Maintenance Outage;

(e)	An estimate of the acceptable deviation in the Outage schedule (i.e., the earliest start date and the latest finish date for the Outage); and

(f)	The nature of work to be performed during the Outage.

(2)	When ERCOT accepts a Maintenance Outage, ERCOT shall coordinate the timing of the appropriate course of action within the Resource-specified timeframe.  The QSE shall notify ERCOT of the Outage and coordinate the time.

3.1.6.3	Additional Information Requests

ERCOT may request additional information from a Resource Entity regarding the information submitted as part of a Resource Outage plan.  ERCOT may not unnecessarily delay requests for information in terms of the required response time.

3.1.6.4	Approval of Changes to a Resource Outage Plan

(1)	ERCOT shall accept all changes to a Resource Outage plan submitted by a Resource Entity more than eight days before the planned start date for the Outage.  ERCOT may discuss with Resource Entities or QSEs any Outage requests that are expected to result in a violation of an ERCOT reliability criteria or that may result in cancellation of a  Transmission Facilities Planned Outage in an attempt to reach a mutually agreeable resolution, including rescheduling the Outage in a manner agreeable to the Resource Entity.

(2)	A Resource Entity must request approval from ERCOT only for new Resource Outages or changes to a previously accepted planned Resource Outage scheduled to occur within eight days of the request.

(3)	ERCOT shall approve Planned Outage and Maintenance Outage requests to occur within eight days, except that ERCOT shall reject proposals if the Outage proposal will impair ERCOT’s ability to meet applicable reliability standards.

(4)	When the scheduled work is complete, any Resource may return from a Planned Outage in accordance with Section 3.1.6.11, Outage Returning Early.  ERCOT shall accept this change and, in the event that a Transmission Facilities Outage was scheduled concurrently with the affected Resource(s) Outage, ERCOT shall coordinate between the TSP and the Resource Entity to schedule a time mutually agreeable to both parties for the Resource to be On-Line.  If mutual agreement cannot be reached, then ERCOT shall decide, considering expected impact on ERCOT System security, future Outage plans, and participants.

[NPRR365: Replace Section 3.1.6.4 above with the following upon system implementation and fulfillment of staffing requirements:] 3.1.6.4 Approval of Changes to a Resource Outage Plan (1) ERCOT shall accept all changes to a Resource Outage plan submitted by a Resource Entity more than 45 days before the planned start date for the Outage. Following acceptance, where ERCOT determines that Outage requests are expected to result in a violation of an ERCOT reliability criterion or that may result in a cancellation of a Transmission Facilities Planned Outage, ERCOT may discuss such concerns with Resource Entities or QSEs in an attempt to reach a mutually agreeable resolution, including rescheduling the Outage in a manner agreeable to the Resource Entity. (2) A Resource Entity must request approval from ERCOT only for new Resource Outages or changes to a previously accepted planned Resource Outage scheduled to occur within 45 days of the request. (3) ERCOT shall approve Planned Outage and Maintenance Outage requests to occur within 45 days, except that ERCOT shall reject proposals if the Outage proposal will impair ERCOT’s ability to meet applicable reliability standards. (4) When the scheduled work is complete, any Resource may return from a Planned Outage in accordance with Section 3.1.6.11, Outage Returning Early. ERCOT shall accept this change and, in the event that a Transmission Facilities Outage was scheduled concurrently with the affected Resource(s) Outage, ERCOT shall coordinate between the TSP and the Resource Entity to schedule a time mutually agreeable to both parties for the Resource to be On-Line. If mutual agreement cannot be reached, then ERCOT shall decide, considering expected impact on ERCOT System security, future Outage plans, and participants.

3.1.6.5	Evaluation of Proposed Short-Noticed Resource Outage

(1)	If a Proposed Short-Noticed Resource Outage, in conjunction with previously accepted Outages, would cause a violation of applicable reliability standards, ERCOT shall:

(a)	Communicate with the requesting Market Participant and each other Market Participants as required under Section 3.1.4.4, Communicating Rejection of Proposed Resource Outages; and

(b)	Consider modifying the previous acceptance or approval of one or more Transmission Facilities or reliability Resource Outages, considering order of receipt and impact to the ERCOT System; based upon security and reliability analysis results, ERCOT shall investigate possible Remedial Action Plans (RAPs) for all insecure states and strive to maximize transmission usage consistent with reliable operation.

(2)	If security can be maintained using an alternative considered in item (1)(b), then ERCOT, may, in its judgment, direct the selected alternatives and approve the Proposed Short-Noticed Resource Outage.

(3)	If ERCOT does not resolve the security issues using any alternatives considered in item (1)(b), then ERCOT shall reject the Proposed Short-Noticed Resource Outage.

[NPRR365: Replace Section 3.1.6.5 above with the following upon system implementation and fulfillment of staffing requirements:] 3.1.6.5 Evaluation of Proposed Resource Outage (1) If a proposed Resource Outage, in conjunction with previously accepted Outages, would cause a violation of applicable reliability standards, ERCOT shall: (a) Communicate with the requesting Market Participant and each other Market Participants as required under Section 3.1.6.8, Resource Outage Rejection Notice; and (b) Consider modifying the previous acceptance or approval of one or more Transmission Facilities or reliability Resource Outages, considering order of receipt and impact to the ERCOT System; based upon security and reliability analysis results, ERCOT shall investigate possible Remedial Action Plans (RAPs) for all insecure states and strive to maximize transmission usage consistent with reliable operation. (2) If security can be maintained using an alternative considered in item (1)(b), then ERCOT, may, in its judgment, direct the selected alternatives and approve the proposed Resource Outage. (3) If ERCOT does not resolve the security issues using any alternatives considered in item (1)(b), then ERCOT shall reject the proposed Resource Outage.

3.1.6.6	Timelines for Response by ERCOT for Resource Outages

ERCOT shall approve, accept or reject each request in accordance with the following table:

| Amount of time between a Request for acceptance of a Planned Outage and the scheduled start of the proposed Outage: | ERCOT shall approve, accept or reject no later than: |
| --- | --- |
| Between one and two days | ERCOT shall approve or reject within eight Business Hours of receipt by ERCOT |
| Between three and eight days | ERCOT shall approve or reject within 1800 hours, two days prior to the start of the proposed Outage |
| Greater than eight days | ERCOT must accept, but ERCOT may discuss reliability and scheduling impacts to minimize hazard/cost to ERCOT System in an attempt to accomplish minimum overall impact. |

[NPRR365: Replace Section 3.1.6.6 above with the following upon system implementation and fulfillment of staffing requirements:] 3.1.6.6 Timelines for Response by ERCOT for Resource Outages (1) ERCOT shall approve, accept or reject each request in accordance with the following table: Amount of time between a request for acceptance of a Planned Outage and the scheduled start of the proposed Outage:; ERCOT shall approve, accept or reject no later than:. Three days; ERCOT shall approve or reject within 1800 hours, two days before the start of the proposed Outage. Between four and eight days; ERCOT shall approve or reject within 1800 hours, three days prior to the start of the proposed Outage. Between nine and 45 days; Five Business Days after submission. Planned Outages are automatically accepted if not rejected at the end of the fifth Business Day following receipt of request.. Greater than 45 days; ERCOT must accept, but ERCOT may discuss reliability and scheduling impacts to minimize cost to the ERCOT System in an attempt to accomplish minimum overall impact. Within five Business Days, ERCOT will notify the submitter if there is a conflict with a previously scheduled Outage.. (2) If circumstances prevent adherence to these timetables, ERCOT shall discuss the request status and reason for the delay of decision with the QSE and make reasonable attempts to mitigate the effect of the delay.

3.1.6.7	Delay

ERCOT may delay its acceptance, approval or rejection of a proposed Planned Outage schedule if the requesting Resource Entity has not submitted sufficient or complete information within the time frames set forth in this Section 3.1.6, Outages of Resources Other Than Reliability Resources.  Review periods for Planned Outage consideration do not commence until sufficient and complete information is submitted to ERCOT as described in Section 3.1.6.2, Resources Outage Plan.

- 3.1.6.8	Resource Outage Rejection Notice

(1)	If ERCOT rejects a request for a Planned Outage, ERCOT shall provide the QSE a written or electronic rejection notice that includes:

(a)	Specific reasons causing the rejection; or

(b)	Possible remedies or Resource schedule revisions, if any, that might mitigate the basis for rejection.

(2)	ERCOT may reject a Planned Outage of Resource facilities only:

(a)	To protect the reliability or security of the ERCOT System;

(b)	Due to insufficient information regarding the Outage;

(c)	Due to failure to comply with submittal process requirements, as specified in these Protocols; or

(d)	As specified elsewhere in these Protocols.

(3)	When multiple proposed Planned Outages or Maintenance Outages cause a known capacity conflict, ERCOT shall:

(a)	Communicate with each QSE to see if the QSE will adjust its proposed Planned Outage schedule;

(b)	Determine if each QSE will agree to an alternative Outage schedule; or

(c)	Reject, in ERCOT’s sole discretion, one or more proposed Outages, considering order of receipt and impact to the ERCOT System.

- 3.1.6.9	Withdrawal of Approval or Acceptance and Rescheduling of Approved or Accepted Planned Outages of Resource Facilities

If ERCOT believes it cannot meet the applicable reliability standards and has exercised reasonable options, ERCOT may contact the QSE for more information prior to its withdrawal of the approval or acceptance of a Planned Outage schedule.  ERCOT will only withdraw approval or acceptance of a Planned Outage to maintain reliability standards.  ERCOT shall inform the affected QSE both orally and in written or electronic form as soon as ERCOT identifies a situation that may lead to the withdrawal of ERCOT’s approval or acceptance.  If ERCOT withdraws its approval or acceptance, the QSE may submit a new request for approval of the Planned Outage schedule provided the new request meets the submittal requirements for Outage Scheduling.

3.1.6.10	Opportunity Outage

(1)	Opportunity Outages for Resources are a special category of Planned Outages that may be approved by ERCOT when a specific Resource has been forced Off-Line due to a Forced Outage and the Resource has been previously accepted for a Planned Outage during the next eight days.

(2)	When a Forced Outage occurs on a Resource that has an accepted or approved Outage scheduled within the following eight days, the Resource may remain Off-Line and start the accepted or approved Outage earlier than scheduled.  The QSE must give as much notice as practicable to ERCOT.

(3)	Opportunity Outages of Transmission Facilities may be approved by ERCOT when a specific Resource is Off-Line due to a Forced, Planned or Maintenance Outage.  A TSP may request an Opportunity Outage at any time.

(4)	When an Outage occurs on a Resource that has an approved Transmission Facilities Opportunity Outage request on file, the TSP may start the approved Outage as soon as practical after receiving authorization to proceed by ERCOT.  ERCOT must give as much notice as practicable to the TSP.

3.1.6.11	Outage Returning Early

(1)	A Resource that completes a Planned Outage early and wants to resume operation shall notify ERCOT of the early return prior to resuming service by making appropriate entries in the Current Operating Plan or Outage Scheduler if applicable as much in advance as practicable, but not later than at least two hours prior to beginning startup.  Within two hours of receiving such request, ERCOT shall either:

(a) 	Approve the request unless, as a result of complying with the request, ERCOT cannot maintain system reliability or security with the Resource injection.  In such a case, ERCOT shall issue a Verbal Dispatch Instruction (VDI) to the Resource’s QSE to stay Off-Line; or

(b) 	Coordinate between the TSP and Resource Entity to schedule a time agreeable to both parties for the Resource to be Off-Line in the event if that a Transmission Facilities Outage requires the affected Resource to be Off-Line. If mutual agreement is not reached, then ERCOT shall decide on the appropriate time, after considering expected impacts on system security, future Outage plans, and participants and issue a VDI to the Resource’s QSE to stay Off-Line.

(2)	Before an early return from an Outage, a Resource Entity or QSE may inquire of ERCOT whether the Resource is expected to be decommitted by ERCOT upon its early return.  If a Resource Entity or QSE is notified by ERCOT that the Resource will be decommitted if it returns early and the Resource Entity or QSE starts the Resource within the previously accepted or approved Outage period, then the QSE representing the Resource will not be paid any decommitment compensation as otherwise would be provided for in Section 5.7, Settlement for RUC Process.

3.1.6.12	Resource Coming On-Line

Before start-up and synchronizing On-Line, a Resource Entity or QSE may inquire of ERCOT whether the Resource is expected to be decommitted by ERCOT upon its coming On-Line.  If a Resource Entity or QSE is notified by ERCOT that the Resource will be decommitted if the Resource comes On-Line and the Resource Entity or QSE starts the Resource, then the QSE representing the Resource will not be paid any decommitment compensation as otherwise would be provided for in Section 5.7.3, Payment When ERCOT Decommits a QSE-Committed Resource.

3.1.7	Reliability Resource Outages

ERCOT shall evaluate requests for approval of an Outage of a Reliability Resource to determine if any one or a combination of proposed Outages may cause ERCOT to violate applicable reliability standards.  ERCOT’s evaluations shall take into consideration factors including the following:

(a)	Load forecast;

(b)	All other known Outages; and

(c)	Potential for the proposed Outages to cause irresolvable transmission overloads or voltage supply concerns based on the indications from contingency analysis software.

3.1.7.1	Timelines for Response by ERCOT on Reliability Resource Outages

(1)	ERCOT shall approve requests for Planned Outages of Reliability Resources unless, in ERCOT’s determination, the requested Planned Outage would cause ERCOT to violate applicable reliability standards.  ERCOT shall approve or reject each request in accordance with the following table:

| Amount of time between a Request for approval of a proposed Planned Outage and the scheduled start date of the proposed Outage: | ERCOT shall approve or reject no later than: |
| --- | --- |
| No less than 30 days | 15 days before the start of the proposed Outage |
| Greater than 45 days | 30 days before the start of the proposed Outage |

(2)	ERCOT shall approve requests for Outages, other than Forced Outages or Level I Maintenance Outages, of Reliability Resources unless, in ERCOT’s determination, the requested Outage would cause ERCOT to violate applicable reliability standards.  ERCOT shall approve or reject Maintenance Outages on Reliability Resources as follows:

| Amount of time between a Request for approval of a proposed Outage and the scheduled start date of the proposed Outage: | ERCOT shall approve or reject no later than: |
| --- | --- |
| Between three and eight days | 0000 hours, two days before the start of the proposed Outage |
| Between nine and 30 days | Four days before the start of the proposed Outage |

(3)	ERCOT shall not be deemed to have approved the Outage request associated with the Planned Outage until ERCOT notifies the Single Point of Contact of its approval.  ERCOT shall transmit approvals electronically.

3.1.7.2	Changes to an Approved Reliability Resource Outage Plan

Once ERCOT has approved a Reliability Resource Planned Outage, the Resource Entity for the Reliability Resource may submit to ERCOT a change request by entering the change in the Outage Scheduler no later than 30 days before the scheduled start date of the approved Outage.  ERCOT shall approve or reject the proposed change within 15 days of receiving the change request form.  ERCOT may, at its discretion, relax the 30 day Notice requirement.

3.2 	Analysis of Resource Adequacy

3.2.1	Calculation of Aggregate Resource Capacity

(1)	ERCOT shall use Outages in the Outage Scheduler and, when applicable, the Resource Status from the Current Operating Plan (COP) to calculate the aggregate capacity from Generation Resources and Load Resources projected to be available in the ERCOT Region and in Forecast Zones in ERCOT.  “Forecast Zones” have the same boundaries as the 2003 ERCOT Congestion Management Zones.  Each Resource will be mapped to a Forecast Zone during the registration process.

(2)	Monthly, ERCOT shall calculate the aggregate weekly Generation Resource capacity for the ERCOT Region and the Forecast Zones projected to be available during the ERCOT Region peak Load hour of each week for the following 36 months, starting with the second week and the aggregate weekly Load Resource capacity for the ERCOT Region projected to be available during the ERCOT Region peak Load hour of each week for the following 36 months, starting with the second week.

(3)	On a rolling hourly basis, ERCOT shall calculate the aggregate hourly Generation Resource capacity and Load Resource capacity in the ERCOT Region and Forecast Zones projected to be available during each hour for the following seven days.

(4)	Projections of Generation Resource capacity from Intermittent Renewable Resources (IRRs) shall be consistent with capacity availability estimates, such as the effective Load carrying capability of wind, developed jointly between ERCOT and the appropriate Technical Advisory Committee (TAC) subcommittee and approved by the ERCOT Board or typical production expectations consistent with expected wind profiles as appropriate for the scenario being studied.

(5)	ERCOT shall publish procedures describing the forecasting process on the Market Information System (MIS) Public Area.

3.2.2	Demand Forecasts

(1)	Monthly, ERCOT shall develop the weekly peak hour Demand forecast for the ERCOT Region and for the Forecast Zones based on the 36-Month Load Forecast as described in Section 3.12, Load Forecasting, for the following 36 months, starting with the second week.  During the development of this forecast, ERCOT may consult with Qualified Scheduling Entities (QSEs), Transmission Service Providers (TSPs), and other Market Participants that may have knowledge of potential Load growth.

(2)	ERCOT may, at its discretion, publish on the MIS Secure Area, additional peak Demand analyses for periods beyond 36 months.

(3)	ERCOT shall develop and publish hourly on the MIS Public Area, peak Demand forecasts by Forecast Zone for each hour of the next seven days using the Seven-Day Load Forecast as described in Section 3.12.

(4)	For purposes of Demand forecasting, ERCOT may choose to use the same forecast as that used for the Load forecast.

(5)	ERCOT shall publish procedures describing the forecasting process on the MIS Public Area.

3.2.3	System Adequacy Reports

(1)	ERCOT shall publish system adequacy reports to assess the adequacy of Resources and Transmission Facilities to meet the projected Demand.  ERCOT shall provide reports on a system-wide basis and by Forecast Zone, where applicable.

(2)	ERCOT shall generate and post a “Medium-Term System Adequacy Report” on the MIS Secure Area.  ERCOT shall update the report monthly using the latest aggregate Generation Resource capacity and Load Resource capacity.  The data will be provided for each week, starting with the second week, of a rolling 36-month period.  The Medium-Term System Adequacy Report will provide:

(a)	Generation Resource capacity at the time of forecasted weekly peak Demand;

(b)	Load Resource capacity at the time of the forecasted weekly peak Demand;

(c)	Weekly peak forecast Demand described in Section 3.2.2, Demand Forecasts;

(d)	Calculated system reserve, highlighting any deficiency hours, that excludes Load Resource capacity;

(e)	Calculated system reserve, highlighting any deficiency hours, that includes Load Resource capacity shown as a reduction in forecast Demand;

(f)	Ancillary Service requirements; and

(g)	Transmission constraints that have a high probability of being binding in the Security-Constrained Economic Dispatch (SCED) or Day-Ahead Market (DAM) given the forecasted system conditions for each week excluding the effects of any transmission or Resource Outages.

(3)	ERCOT shall generate and post a “Short-Term System Adequacy Report” on the MIS Public Area.  ERCOT shall update this report hourly following updates to the Seven-Day Load Forecast and on detection of a change to Resource Status that changes the availability of a Resource.  The Short-Term System Adequacy Report will provide:

(a)	For Generation Resources, the available On-Line Resource capacity for each hour, using the COP for the first seven days;

(b)	For Load Resources, the available capacity for each hour using the COP;

(c)	Forecast Demand for each hour described in Section 3.2.2;

(d)	Ancillary Service requirements for the Operating Day and subsequent days; and

(e)	Transmission constraints that have a high probability of being binding in SCED or DAM given the forecasted system conditions for each week including the effects of any transmission or Resource Outages.  The binding constraints may not be updated every hour.

3.2.4	Statement of Opportunities

(1)	ERCOT shall annually publish on the MIS Public Area a “Statement of Opportunities” that provides a projection of the capability of existing and planned Generation Resources, Load Resources, and Transmission Facilities to reliably meet ERCOT’s projected needs.  A Statement of Opportunities published in even-numbered years shall use a ten-year study horizon and be published by December 31 of those years.  A Statement of Opportunity published in odd-numbered years shall use a five-year study horizon and be published on or around October 1 of those years.

(2)	If additional information is required to complete the Statement of Opportunities, ERCOT shall prescribe these reporting requirements for Generation Entities and TSPs to report their plans for adding new facilities, upgrading existing facilities, and mothballing or retiring existing facilities.  ERCOT also shall prescribe any additional reporting requirements needed for Load Entities to report to ERCOT their plans for adding new Load Resources or retiring existing Load Resources.

(3)	Prior to prescribing new reporting requirements for the development of the Statement of Opportunities, ERCOT shall use information already being provided by Market Participants if doing so is cost-effective.

3.2.5	Publication of Resource and Load Information

(1)	Two days after the applicable Operating Day, ERCOT shall post on the MIS Public Area for the ERCOT System and, if applicable, for each Disclosure Area, the information derived from the first complete execution of SCED in each 15-minute Settlement Interval.  A “Disclosure Area” is a geographical area of the ERCOT Region defined by the TAC and approved by the ERCOT Board.  The initial Disclosure Areas as of the Texas Nodal Market Implementation Date are the 2003 ERCOT Congestion Management Zones.  Posting requirements will be applicable to Generation Resources physically located in the defined Disclosure Area.  The information posted by ERCOT shall include:

(a)	An aggregate energy supply curve based on non-wind Resources with Energy Offer Curves that are available to be dispatched by SCED.  The energy supply curves will be calculated in ten MW increments, beginning at the sum of the Low Sustained Limits (LSLs) and ending at the sum of the High Sustained Limits (HSLs) for non-wind Resources with Energy Offer Curves, with the dispatch for each Resource constrained between the Resource’s LSL and HSL.  The result will represent the ERCOT System energy supply curve economic dispatch of the non-wind Resources with Energy Offer Curves at various pricing points, not taking into consideration any physical limitations of the ERCOT System;

(b)	An aggregate energy supply curve based on Wind-powered Generation Resources (WGRs) with Energy Offer Curves that are available to be dispatched by SCED.  The energy supply curves will be calculated in ten MW increments, beginning at the sum of the LSLs and ending at the sum of the HSLs for WGRs with Energy Offer Curves, with the dispatch for each WGR constrained between the WGR’s LSL and HSL.  The result will represent the ERCOT System energy supply curve economic dispatch of the WGRs with Energy Offer Curves at various pricing points, not taking into consideration any physical limitations of the ERCOT System.  The posting of this data by Disclosure Area shall be available no later than 180-days after the Texas Nodal Market Implementation Date;

(c)	The sum of LSLs, sum of Output Schedules, and sum of HSLs for Generation Resources without Energy Offer Curves.  The posting of this data by Disclosure Area shall be available no later than 180 days after the Texas Nodal Market Implementation Date;

(d)	The sum of the Base Points, High Ancillary Service Limit (HASL) and Low Ancillary Service Limit (LASL) of non-wind Resources with Energy Offer Curves, sum of the Base Points, HASL and LASL of WGRs with Energy Offer Curves, and the sum of the Base Points, HASL and LASL of all remaining Resources dispatched in SCED.  The posting of this data by Disclosure Area shall be available no later than 180 days after the Texas Nodal Market Implementation Date; and

(e)	The sum of the telemetered Generation Resource net output used in SCED.  The posting of this data by Disclosure Area shall be available no later than 180 days after the Texas Nodal Market Implementation Date.

(2)	Two days after the applicable Operating Day, ERCOT shall post on the MIS Public Area for the ERCOT System the following information derived from the first complete execution of SCED in each 15-minute Settlement Interval:

(a)	Each telemetered Dynamically Scheduled Resource (DSR) Load, and the telemetered Resource net output(s) associated with each DSR Load; and

(b)	The actual ERCOT Load as determined by subtracting the Direct Current Tie (DC Tie) Resource actual telemetry from the sum of the telemetered Generation Resource net output as used in SCED.

(3)	Two days after the applicable Operating Day, ERCOT shall post on the MIS Public Area the following information for the ERCOT System and, if applicable, for each Disclosure Area from the DAM for each hourly Settlement Interval:

(a)	An aggregate energy supply curve based on all energy offers that are available to the DAM, not taking into consideration Resource Startup Offer or Minimum-Energy Offer or any physical limitations of the ERCOT System.  The energy supply curves will be calculated in ten MW increments.  The result will represent the energy supply curve at various pricing points for energy offers available in the DAM;

(b)	Aggregate minimum energy supply curves based on all Minimum-Energy Offers that are available to the DAM.  The minimum energy supply curves will be calculated in ten MW increments.  The posting of this data by Disclosure Area shall be available no later than 180 days after the Texas Nodal Market Implementation Date;

(c)	An aggregate energy Demand curve based on the DAM Energy Bid curves available to the DAM, not taking into consideration any physical limitations of the ERCOT System.  The energy demand curve will be calculated in ten MW increments;

(d)	The aggregate amount of cleared energy bids and offers including cleared Minimum-Energy Offer quantities.  The posting of this data by Disclosure Area shall be available no later than 180 days after the Texas Nodal Market Implementation Date;

(e)	The aggregate Ancillary Service Offers (prices and quantities) in the DAM, for each type of Ancillary Service regardless of a Resource’s On-Line or Off-Line status.  For Responsive Reserve (RRS) service, ERCOT shall separately post aggregated offers from Generation Resources, Controllable Load Resources, and non-Controllable Load Resources.  Linked Ancillary Service Offers will be included as non-linked Ancillary Service Offers;

(f)	The aggregate Self-Arranged Ancillary Service Quantity, for each type of service, by hour;

(g)	The aggregate amount of cleared Ancillary Service Offers; and

(h)	The aggregate Point-to-Point (PTP) Obligation bids (not-to-exceed price and quantities) for the ERCOT System and the aggregate PTP Obligation bids that sink in the Disclosure Area for each Disclosure Area.  The posting of this data by Disclosure Area shall be available no later than 180 days after the Texas Nodal Market Implementation Date.

(4)	Beginning 61 days after the Texas Nodal Market Implementation Date, ERCOT shall post on the MIS Public Area the following information for each Resource for each 15-minute Settlement Interval 60 days prior to the current Operating Day:

(a)	The Resource name and the Resource’s Energy Offer Curve (prices and quantities) used in SCED, including the incremental/decremental Energy Offer Curves for DSRs;

(b)	The Resource name and the Resource’s Output Schedule;

(c)	The DSR Load and associated Resource name and Resource net output;

(d)	The Resource name and actual metered Resource net output;

(e)	The self-arranged Ancillary Service by service for each QSE;

(f)	The following Generation Resource data using a single snapshot during the first SCED execution in each Settlement Interval:

(i)	The Generation Resource name;

(ii)	The Generation Resource status;

(iii)	The Generation Resource HSL, LSL, HASL, LASL, High Dispatch Limit (HDL), and Low Dispatch Limit (LDL);

(iv)	The Generation Resource Base Point from SCED;

(v)	The telemetered Generation Resource net output used in SCED;

(vi)	The Ancillary Service Resource Responsibility for each Ancillary Service; and

(vii)	The Generation Resource Startup Cost and minimum energy cost used in the Reliability Unit Commitment (RUC); and

(g)	The following Load Resource data using a single snapshot during the first SCED execution in each Settlement Interval:

(i)	The Load Resource name;

(ii)	The Load Resource status;

(iii)	The Maximum Power Consumption (MPC for a Load Resource);

(iv)	The Low Power Consumption (LPC for a Load Resource);

(v)	The telemetered real power consumption; and

(vi)	The Ancillary Service Resource Responsibility for each Ancillary Service.

(5)	Beginning 61 days after the Texas Nodal Market Implementation Date, if any Real-Time Locational Marginal Price (LMP) exceeds 50 times the Fuel Index Price (FIP) during any 15-minute Settlement Interval for the applicable Operating Day, ERCOT shall post on the MIS Public Area the portion of any Resource’s Energy Offer Curve that is at or above 50 times the FIP for each 15-minute Settlement Interval seven days after the applicable Operating Day.

(6)	Beginning 61 days after the Texas Nodal Market Implementation Date, ERCOT shall post on the MIS Public Area the offer price and the name of the Entity submitting the offer for the highest-priced offer selected or Dispatched by SCED two days after the applicable Operating Day.  If multiple Entities submitted the highest-priced offers selected, all Entities shall be identified on the MIS Public Area.

(7)	ERCOT shall post on the MIS Public Area for each Operating Day the following information for each Resource:

(a)	The Resource name;

(b)	The names of the Entities providing information to ERCOT;

(c)	The names of the Entities controlling each Resource.  ERCOT shall determine whether the Entity is in control of each Resource in accordance with subsection (e) of P.U.C. Subst. R. 25.502, Pricing Safeguards in Markets Operated by the Electric Reliability Council of Texas; and

(d)	Flag for Reliability Must-Run (RMR) Resources.

(8)	Beginning 61 days after the Texas Nodal Market Implementation Date, ERCOT shall post on the MIS Public Area the following information from the DAM for each hourly Settlement Interval for the applicable Operating Day 60 days prior to the current Operating Day:

(a)	The Generation Resource name and the Generation Resource’s Three-Part Supply Offer (prices and quantities), including Startup Offer and Minimum-Energy Offer, available for the DAM;

(b)	For each Settlement Point, individual DAM Energy-Only Offer Curves available for the DAM and the name of the QSE submitting the offer;

(c)	The Resource name and the Resource’s Ancillary Service Offers available for the DAM;

(d)	For each Settlement Point, individual DAM Energy Bids available for the DAM and the name of the QSE submitting the bid;

(e)	For each Settlement Point, individual Congestion Revenue Right (CRR) offers available to the DAM that sink at the Settlement Point and the QSE submitting the offer;

(f)	For each Settlement Point, individual PTP Obligation bids available to the DAM that sink at the Settlement Point and the QSE submitting the bid;

(g)	The awards for each Ancillary Service from DAM for each Generation Resource;

(h)	The awards for each Ancillary Service from DAM for each Load Resource;

(i)	The award of each Three-Part Supply Offer from the DAM and the name of the QSE receiving the award;

(j)	For each Settlement Point, the award of each DAM Energy-Only Offer from the DAM and the name of the QSE receiving the award;

(k)	For each Settlement Point, the award of each DAM Energy Bid from the DAM and the name of the QSE receiving the award;

(l)	For each Settlement Point, the award of each CRR offer from the DAM that sinks at the Settlement Point and the QSE submitting the offer; and

(m)	For each Settlement Point, the award of each PTP Obligation bid from the DAM that sinks at the Settlement Point and the QSE submitting the bid.

[NPRR322: Replace paragraph (8) above with the following upon system implementation:] (8) Beginning 61 days after the Texas Nodal Market Implementation Date, ERCOT shall post on the MIS Public Area the following information from the DAM for each hourly Settlement Interval for the applicable Operating Day 60 days prior to the current Operating Day: (a) The Generation Resource name and the Generation Resource’s Three-Part Supply Offer (prices and quantities), including Startup Offer and Minimum-Energy Offer, available for the DAM; (b) For each Settlement Point, individual DAM Energy-Only Offer Curves available for the DAM and the name of the QSE submitting the offer; (c) The Resource name and the Resource’s Ancillary Service Offers available for the DAM; (d) For each Settlement Point, individual DAM Energy Bids available for the DAM and the name of the QSE submitting the bid; (e) For each Settlement Point, individual PTP Obligation bids available to the DAM that sink at the Settlement Point and the QSE submitting the bid; (f) The awards for each Ancillary Service from DAM for each Generation Resource; (g) The awards for each Ancillary Service from DAM for each Load Resource; (h) The award of each Three-Part Supply Offer from the DAM and the name of the QSE receiving the award; (i) For each Settlement Point, the award of each DAM Energy-Only Offer from the DAM and the name of the QSE receiving the award; (j) For each Settlement Point, the award of each DAM Energy Bid from the DAM and the name of the QSE receiving the award; and (k) For each Settlement Point, the award of each PTP Obligation bid from the DAM that sinks at the Settlement Point, including whether or not the PTP Obligation bid was Linked to an Option, and the QSE submitting the bid.

3.3	Management of Changes to ERCOT Transmission Grid

Additions and changes to the ERCOT System must be coordinated with ERCOT to accurately represent the ERCOT Transmission Grid.

3.3.1	ERCOT Approval of New or Relocated Facilities

Before energizing and placing into service any new or relocated facility connected to the ERCOT Transmission Grid, a TSP, QSE, or Resource Entity shall enter appropriate information in the Outage Scheduler and coordinate with, and receive written notice of approval from, ERCOT.

3.3.2	Types of Work Requiring ERCOT Approval

Each TSP, QSE and Resource Entity shall coordinate with ERCOT the requirements of Section 3.10, Network Operations Modeling and Telemetry, the following types of work for any addition to, replacement of, or change to or removal from the ERCOT Transmission Grid:

(a)	Transmission lines;

(b)	Equipment including circuit breakers, transformers, disconnects, reactive devices, and wave traps;

(c)	Resource interconnections; and

(d)	Protection and control schemes, including changes to Remedial Action Plans (RAP), Supervisory Control and Data Acquisition (SCADA) systems, Energy Management Systems (EMS), AGC, or Special Protection Systems (SPS).

3.3.2.1	Information to Be Provided to ERCOT

(1)	The energization or removal of a Transmission Facility or Generation Resource in the Network Operations Model requires an entry into the Outage Scheduler by a TSP or Resource Entity.  The Resource Entity shall make entries in the Outage Scheduler for Outages of new or relocated Generation Resources.  ERCOT shall submit entries into the Outage Scheduler on behalf of the Resource Entity, for any energization or removal of Transmission Facilities owned by the Resource Entity.  Once ERCOT posts a Resource Entity Transmission Facility Outage request on the MIS Secure Area, the Resource Entity shall review the submitted Outage for accuracy of information and request that ERCOT submit modifications if necessary.  If any changes in system topology or telemetry are expected, then the TSP or Resource Entity shall notify ERCOT in accordance with the schedule in Section 3.3.1, ERCOT Approval of New or Relocated Facilities.  Information submitted pursuant to Section 3.3.2.1 for Transmission Facilities within a Private Use Network shall not be publicly posted.

(2)	If a Resource Entity within a Private Use Network is adding or removing a Transmission Facility at the Point of Interconnection (POI), it shall inform and determine with ERCOT whether any corresponding Network Operations Model updates are necessary.  If ERCOT and the Resource Entity determine that updates are needed, the process set forth in paragraph (1) above shall be used to incorporate the update into the Network Operations Model and Outage Scheduler.  Information submitted pursuant to paragraph (1) above shall not be publicly posted.

[NPRR219: Replace paragraphs (1) and (2) above with the following upon system implementation:] (1) The energization or removal of a Transmission Facility or Generation Resource in the Network Operations Model requires an entry into the Outage Scheduler by a TSP or Resource Entity. For TSP requests, the TSPs shall enter such requests in the Outage Scheduler. For Resource Entity requests, the Resource Entity shall enter such requests in the Outage Scheduler. If any changes in system topology or telemetry are expected, then the TSP or Resource Entity shall notify ERCOT in accordance with the schedule in Section 3.3.1, ERCOT Approval of New or Relocated Facilities. Information submitted pursuant to this subsection for Transmission Facilities within a Private Use Network shall not be publicly posted. (2) If a Resource Entity within a Private Use Network is adding or removing a Transmission Facility at the Point of Interconnection (POI), it shall inform and determine with ERCOT whether any corresponding Network Operations Model updates are necessary. If ERCOT and the Resource Entity determine that updates are needed, the process set forth in paragraph (1) above shall be used to incorporate the update into the Network Operations Model. Information submitted pursuant to this paragraph (1) above shall not be publicly posted.

(3)	TSPs and Resource Entities shall submit any changes in system topology or telemetry in accordance with the Network Operations Model Change Request (NOMCR) process or other ERCOT-prescribed process applicable to Resource Entities and according to the requirements of Section 3.10.1, Time Line for Network Operations Model Changes.  The submittal shall include the following:

(a)	Proposed energize date;

(b)	TSPs or Resource Entities performing work;

(c)	TSPs or Resource Entities responsible for rating affected Transmission Element(s);

(d)	For Resource Entities, data and information required by Section 16.5, Registration of a Resource Entity;

(e)	Station identification code;

(f)	Identification of existing Transmission Facilities involved and new Transmission Facilities (if any) being added or existing Transmission Facilities being permanently removed from service;

(g)	Ratings of existing Transmission Facilities involved and new Transmission Facilities (if any) being added;

(h)	Outages required (clearly identify each Outage if multiple Outages are required), including sequence of Outage and estimate of Outage duration;

(i)	General statement of work to be completed with intermediate progress dates and events identified;

(j)	SCADA modification work, including descriptions of the telemetry points or changes to existing telemetry, providing information on equipment being installed, changed, or monitored;

(k)	Additional data determined by ERCOT and TSPs, or Resource Entities as needed to complete the ERCOT model representation of existing Transmission Facilities involved and new Transmission Facilities (if any) being added;

(l)	Statement of completion, including:

(i)	Statement to be made at the completion of each intermediate stage of project; and

(ii)	Statement to be made at completion of total project.

(m)	Drawings, including:

(i)	Existing status;

(ii)	Each intermediate stage; and

(iii)	Proposed final configuration.

3.3.2.2	Record of Approved Work

ERCOT shall maintain a record of all work approved in accordance with Section 3.3, Management of Changes to ERCOT Transmission Grid, and shall publish, and update monthly, information on the MIS Secure Area regarding each new Transmission Element to be installed on the ERCOT Transmission Grid.

3.4	Load Zones

ERCOT shall assign every Electrical Bus to a Load Zone for settlement purposes.  ERCOT shall calculate a Settlement Point Price for each Load Zone as the Load-weighted average of the LMPs at all Electrical Buses assigned to that Load Zone.  The Load-weighting must be determined using the Load, if any, from the State Estimator at each Electrical Bus.

3.4.1	Load Zone Types

(1)	The Load Zone types are:

(a)	the Competitive Load Zones;

(b)	the NOIE Load Zones created pursuant to Section 3.4.3, NOIE Load Zones; and

(c)	the DC Tie Load Zones as defined in Section 3.4.4, DC Tie Load Zones.

(2)	The Competitive Load Zones are the four zones in effect during the 2003 ERCOT market unless they are changed pursuant to Section 3.4.2, Load Zone Modifications, less any Electrical Buses that are assigned to a NOIE Load Zone or a DC Tie Load Zone.

3.4.2	Load Zone Modifications

(1)	Load Zones may be added, deleted, or changed, only when approved by the ERCOT Board, with the exception of paragraphs (2)(a) and (2)(d) of Section 3.4.3, NOIE Load Zones.  Approved additions, deletions, or changes go into effect 36 months after the end of the month in which the addition, deletion, or change was approved.

(2)	A member who is a part of the group of NOIEs that have the same pre-1999 power supply arrangements and therefore establish an automatic NOIE Load Zone under paragraph (2)(d) of Section 3.4.3 may elect to be assigned to an appropriate Competitive Load Zone after giving notice of termination of its power supply arrangement to ERCOT.  Such notice must be given to ERCOT no later than 90 days prior to the next annual Congestion Revenue Right (CRR) Auction.  This type of Load Zone change will go into effect on January 1st of the next calendar year if the change was approved by the ERCOT Board.

3.4.3	NOIE Load Zones

(1)	A NOIE or a group of NOIEs may establish a Load Zone in accordance with this Section.

(2)	The descriptions and conditions set forth below apply to Load Zones established by NOIEs:

(a)	All NOIEs must be assigned to an appropriate Competitive Load Zone, unless they had made a one-time choice to establish a NOIE Load Zone and notified ERCOT in writing of that choice six months before the Texas Nodal Market Implementation Date, except as specified otherwise in item (d) below;

(b)	The number of NOIE Load Zones may not exceed 20;

(c)	Any costs allocated based upon a zonal Load Ratio Share must be allocated using “Cost-Allocation Load Zones,” which are the four zones in effect during the 2003 ERCOT market unless they are changed pursuant to Section 3.4.2, Load Zone Modifications.  For these allocation purposes, any NOIE Load Zone is considered to be located entirely within the 2003 ERCOT Congestion Management Zone (CMZ) that represented the largest Load for that NOIE or group of NOIEs in 2003;

(d)	Each group of NOIEs who are parties to the same pre-1999 power supply arrangements and that has an overall 2003 peak Load in excess of 2,300 MW is automatically a separate NOIE Load Zone.  A member of this separate NOIE Load Zone who has given notice of termination of its power supply arrangement to ERCOT may elect to be assigned to an appropriate Competitive Load Zone.  An election made prior to Texas Nodal Market Implementation Date does not require approval of the ERCOT Board and will be effective for the next appropriate CRR Auction.  An election made after Texas Nodal Market Implementation Date shall be subject to the approval process in Section 3.4.2.  Any other NOIE that has a 2003 peak Load in excess of 2,300 MW is automatically a separate NOIE Load Zone;

(e)	ERCOT shall uniquely identify NOIE Load Zones.  NOIEs may participate in only one NOIE Load Zone, and all Loads served by that NOIE must be contained within that Load Zone;

(f)	Except as specified otherwise in this subsection, Load Zones established by NOIEs will be treated the same as other Load Zones, including a 36-month notice requirement for ERCOT Board approval of any changes to Load Zones; and

(g)	Three years after a NOIE offers its Customers retail choice, the NOIE’s Load must be merged into the appropriate Competitive Load Zone(s).  For a Load Zone that is an aggregation of NOIE systems of which less than all of the NOIEs opt into Customer Choice, each remaining NOIE in that NOIE Load Zone may choose to have its Load merged into the appropriate Competitive Load Zone(s) under the same three-year time frame.

3.4.4	DC Tie Load Zones

A DC Tie Load Zone contains only the Electrical Bus in the ERCOT Transmission Grid that connects the DC Tie and is used in the settlement of the DC Tie Load in that zone.

3.4.5	Additional Load Buses

ERCOT shall assign new Electrical Buses to a Load Zone and Cost Allocation Zone in accordance with the following rules; changes are effective immediately:

(a)	For each new Electrical Bus serving Load of a NOIE that is a part of a NOIE Load Zone, the new Electrical Bus will be assigned to that NOIE Load Zone;

(b)	For each new Electrical Bus not covered in paragraph (a) above, connected via Transmission Facilities to Electrical Buses all located within the same Competitive Load Zone, the new Electrical Bus will be assigned to that Competitive Load Zone;

(c)	For each new Electrical Bus not covered in paragraphs (a) or (b) above, ERCOT shall simulate LMPs for the annual peak hour of the system with the new Electrical Bus incorporated into the model.  ERCOT shall assign that new Electrical Bus to the Competitive Load Zone with the closest matching zonal Settlement Point Price to the new Electrical Bus's LMP;

(d)	For each new Electrical Bus covered in paragraph (a) above and connected via Transmission Facilities to Electrical Buses all located within the same Cost Allocation Zone, then the new Electrical Bus will be assigned to that Cost Allocation Zone;

(e)	For each new Electrical Bus covered in paragraph (a) above and not covered in paragraph (d) above, ERCOT shall simulate LMPs for the annual peak hour of the system with the new Electrical Bus incorporated into the model.  ERCOT shall assign each new Electrical Bus associated with a NOIE that is a part of a NOIE Load Zone to the Cost Allocation Zone with the closest matching zonal Settlement Point Price to the new Electrical Bus's LMP.

(f)	For each new Electrical Bus not covered in paragraph (a), the new Electrical Bus is assigned to the same Cost Allocation Zone as its designated Load Zone;

3.5	Hubs

3.5.1	Process for Defining Hubs

(1)	Hubs settled through ERCOT may only be created by an amendment to Section 3.5.2, Hub Definitions.  Hubs are made up of one or more Electrical Buses.  ERCOT shall post the list of Electrical Buses (including their names) that are part of a Hub on the Market Information System (MIS) Public Area.  A Hub, once defined, may not be modified except as explicitly described in the definition of that Hub.

(2)	When any Electrical Bus within a Hub Bus is added to the Network Operations Model or the Congestion Revenue Right (CRR) Network Model through changes to the Network Operations Model or CRR Network Model, ERCOT shall provide notice to all Market Participants as soon as practicable and include that Electrical Bus in the Hub Bus price calculation.

(3)	When any Electrical Bus within a Hub Bus is disconnected from the Network Operations Model or the CRR Network Model through operations changes in transmission topology temporarily, ERCOT shall provide notice to all Market Participants as soon as practicable and exclude that Electrical Bus from the Hub Bus price calculation.

(4)	In the event of a permanent change that removes the Hub Bus from the ERCOT Transmission Grid, ERCOT shall file a Nodal Protocol Revision Request (NPRR) to revise the appropriate Hub definition.

(5)	If a Transmission Service Provider (TSP) or ERCOT plans a nomenclature change in the Network Operations Model or the CRR Network Model, ERCOT shall file a NPRR to include the nomenclature change in the Hub Bus definitions before implementing the name change to either the Network Operations Model or the CRR Network Model.

3.5.2	Hub Definitions

3.5.2.1	North 345 kV Hub (North 345)

(1)	The North 345 kV Hub is composed of the following Hub Buses:

|  | ERCOT Operations |  |  |
| --- | --- | --- | --- |
| No. | Hub Bus | kV | Hub |
| 1 | ANASW | 345 | NORTH |
| 2 | CN345 | 345 | NORTH |
| 3 | WLSH | 345 | NORTH |
| 4 | FMRVL | 345 | NORTH |
| 5 | LPCCS | 345 | NORTH |
| 6 | MNSES | 345 | NORTH |
| 7 | PRSSW | 345 | NORTH |
| 8 | SSPSW | 345 | NORTH |
| 9 | VLSES | 345 | NORTH |
| 10 | ALNSW | 345 | NORTH |
| 11 | ALLNC | 345 | NORTH |
| 12 | BNDVS | 345 | NORTH |
| 13 | BNBSW | 345 | NORTH |
| 14 | BBSES | 345 | NORTH |
| 15 | BOSQUESW | 345 | NORTH |
| 16 | CDHSW | 345 | NORTH |
| 17 | CNTRY | 345 | NORTH |
| 18 | CRLNW | 345 | NORTH |
| 19 | CMNSW | 345 | NORTH |
| 20 | CNRSW | 345 | NORTH |
| 21 | CRTLD | 345 | NORTH |
| 22 | DCSES | 345 | NORTH |
| 23 | EMSES | 345 | NORTH |
| 24 | ELKTN | 345 | NORTH |
| 25 | ELMOT | 345 | NORTH |
| 26 | EVRSW | 345 | NORTH |
| 27 | KWASS | 345 | NORTH |
| 28 | FGRSW | 345 | NORTH |
| 29 | FORSW | 345 | NORTH |
| 30 | FRNYPP | 345 | NORTH |
| 31 | GIBCRK | 345 | NORTH |
| 32 | HKBRY | 345 | NORTH |
| 33 | VLYRN | 345 | NORTH |
| 34 | JEWET | 345 | NORTH |
| 35 | KNEDL | 345 | NORTH |
| 36 | KLNSW | 345 | NORTH |
| 37 | LCSES | 345 | NORTH |
| 38 | LIGSW | 345 | NORTH |
| 39 | LEG | 345 | NORTH |
| 40 | LFKSW | 345 | NORTH |
| 41 | LWSSW | 345 | NORTH |
| 42 | MLSES | 345 | NORTH |
| 43 | MCCREE | 345 | NORTH |
| 44 | MDANP | 345 | NORTH |
| 45 | ENTPR | 345 | NORTH |
| 46 | NCDSE | 345 | NORTH |
| 47 | NORSW | 345 | NORTH |
| 48 | NUCOR | 345 | NORTH |
| 49 | PKRSW | 345 | NORTH |
| 50 | KMCHI | 345 | NORTH |
| 51 | PTENN | 345 | NORTH |
| 52 | RENSW | 345 | NORTH |
| 53 | RCHBR | 345 | NORTH |
| 54 | RNKSW | 345 | NORTH |
| 55 | RKCRK | 345 | NORTH |
| 56 | RYSSW | 345 | NORTH |
| 57 | SGVSW | 345 | NORTH |
| 58 | SHBSW | 345 | NORTH |
| 59 | SHRSW | 345 | NORTH |
| 60 | SCSES | 345 | NORTH |
| 61 | SYCRK | 345 | NORTH |
| 62 | THSES | 345 | NORTH |
| 63 | TMPSW | 345 | NORTH |
| 64 | TNP_ONE | 345 | NORTH |
| 65 | TRCNR | 345 | NORTH |
| 66 | TRSES | 345 | NORTH |
| 67 | TOKSW | 345 | NORTH |
| 68 | VENSW | 345 | NORTH |
| 69 | WLVEE | 345 | NORTH |
| 70 | W_DENT | 345 | NORTH |
| 71 | WTRML | 345 | NORTH |
| 72 | WCSWS | 345 | NORTH |
| 73 | WEBB | 345 | NORTH |
| 74 | WHTNY | 345 | NORTH |
| 75 | WCPP | 345 | NORTH |

(2)	The North 345 kV Hub Price is the simple average of the Hub Bus prices for each hour of the Settlement Interval of the Day-Ahead Market (DAM) in the Day-Ahead and is the simple average of the time-weighted Hub Bus prices for each 15-minute Settlement Interval in Real-Time, for each Hub Bus included in this Hub.

(3)	The Day-Ahead Settlement Point Price of the Hub for a given Operating Hour is calculated as follows:

DASPP North345	=	Σhb(HUBDF hb, North345 * DAHBP hb, North345), if HB North345≠0

DASPP North345	=	DASPPERCOT345Bus, if HB North345=0

Where:

DAHBP hb, North345	=	Σb(HBDF b, hb, North345 * DALMP b, hb, North345)

HUBDF hb, North345	=	IF(HB North345=0, 0, 1 / HB North345)

HBDF b, hb, North345	=	IF(B hb, North345=0, 0, 1 / B hb, North345)

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| DASPP North345 | $/MWh | Day-Ahead Settlement Point PriceThe DAM Settlement Point Price at the Hub, for the hour. |
| DAHBP hb, North345 | $/MWh | Day-Ahead Hub Bus Price at Hub BusThe DAM energy price at Hub Bus hb for the hour. |
| DALMP b, hb, North345 | $/MWh | Day-Ahead Locational Marginal Price (LMP) at Electrical Bus of Hub BusThe DAM LMP at Electrical Bus b that is a component of Hub Bus hb for the hour. |
| HUBDF hb, North345 | none | Hub Distribution Factor per Hub BusThe distribution factor of Hub Bus hb. |
| HBDF b, hb, North345 | none | Hub Bus Distribution Factor per Electrical Bus of Hub BusThe distribution factor of Electrical Bus b that is a component of Hub Bus hb. |
| b | none | An energized Electrical Bus that is a component of a Hub Bus. |
| B hb, North345 | none | The total number of energized Electrical Buses in Hub Bus hb. |
| hb | none | A Hub Bus that is a component of the Hub. |
| HB North345 | none | The total number of Hub Buses in the Hub with at least one energized component in each Hub Bus. |

(4)	The Real-Time Settlement Point Price of the Hub for a given 15-minute Settlement Interval is calculated as follows:

RTSPP North345	=	Σhb(HUBDF hb, North345 * (Σy(RTHBP hb, North345, y * TLMP y) / (ΣyTLMP y))), if HB North345≠0

RTSPP North345	=	RTSPPERCOT345Bus, if HB North345=0

Where:

RTHBP hb, North345, y	=	Σb(HBDF b, hb, North345 * RTLMP b, hb, North345, y)

HUBDF hb, North345	=	IF(HB North345=0, 0, 1 / HB North345)

HBDF b, hb, North345	=	IF(B hb, North345=0, 0, 1 / B hb, North345)

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTSPP North345 | $/MWh | Real-Time Settlement Point PriceThe Real-Time Settlement Point Price at the Hub, for the 15-minute Settlement Interval. |
| RTHBP hb, North345, y | $/MWh | Real-Time Hub Bus Price at Hub Bus per Security-Constrained Economic Dispatch (SCED) intervalThe Real-Time energy price at Hub Bus hb for the SCED interval y. |
| RTLMP b, hb, North345, y | $/MWh | Real-Time Locational Marginal Price at Electrical Bus of Hub Bus per intervalThe Real-Time LMP at Electrical Bus b that is a component of Hub Bus hb, for the SCED interval y. |
| TLMP y | second | Duration of SCED interval per intervalThe duration of the portion of the SCED interval y within the 15-minute Settlement Interval |
| HUBDF hb, North345 | none | Hub Distribution Factor per Hub BusThe distribution factor of Hub Bus hb. |
| HBDF b, hb, North345 | none | Hub Bus Distribution Factor per Electrical Bus of Hub BusThe distribution factor of Electrical Bus b that is a component of Hub Bus hb. |
| y | none | A SCED interval in the 15-minute Settlement Interval. The summation is over the total number of SCED runs that cover the 15-minute Settlement Interval. |
| b | none | An energized Electrical Bus that is a component of a Hub Bus. |
| B hb, North345 | none | The total number of energized Electrical Buses in Hub Bus hb. |
| hb | none | A Hub Bus that is a component of the Hub. |
| HB North345 | none | The total number of Hub Buses in the Hub with at least one energized component in each Hub Bus. |

3.5.2.2	South 345 kV Hub (South 345)

(1)	The South 345 kV Hub is composed of the following Hub Buses:

|  | ERCOT Operations |  |  |
| --- | --- | --- | --- |
| No. | Hub Bus | kV | Hub |
| 1 | AUSTRO | 345 | SOUTH |
| 2 | BLESSING | 345 | SOUTH |
| 3 | CAGNON | 345 | SOUTH |
| 4 | COLETO | 345 | SOUTH |
| 5 | CLEASP | 345 | SOUTH |
| 6 | NEDIN | 345 | SOUTH |
| 7 | FAYETT | 345 | SOUTH |
| 8 | FPPYD1 | 345 | SOUTH |
| 9 | FPPYD2 | 345 | SOUTH |
| 10 | GARFIE | 345 | SOUTH |
| 11 | GUADG | 345 | SOUTH |
| 12 | HAYSEN | 345 | SOUTH |
| 13 | HILLCTRY | 345 | SOUTH |
| 14 | HOLMAN | 345 | SOUTH |
| 15 | KENDAL | 345 | SOUTH |
| 16 | LA_PALMA | 345 | SOUTH |
| 17 | LON_HILL | 345 | SOUTH |
| 18 | LOSTPI | 345 | SOUTH |
| 19 | LYTTON_S | 345 | SOUTH |
| 20 | MARION | 345 | SOUTH |
| 21 | PAWNEE | 345 | SOUTH |
| 22 | RIOHONDO | 345 | SOUTH |
| 23 | RIONOG | 345 | SOUTH |
| 24 | SALEM | 345 | SOUTH |
| 25 | SANMIGL | 345 | SOUTH |
| 26 | SKYLINE | 345 | SOUTH |
| 27 | STP | 345 | SOUTH |
| 28 | CALAVERS | 345 | SOUTH |
| 29 | BRAUNIG | 345 | SOUTH |
| 30 | WHITE_PT | 345 | SOUTH |
| 31 | ZORN | 345 | SOUTH |

(2)	The South 345 kV Hub Price is the simple average of the Hub Bus prices for each hour of the Settlement Interval of the DAM in the Day-Ahead and is the simple average of the time-weighted Hub Bus prices for each 15-minute Settlement Interval in Real-Time, for each Hub Bus included in this Hub.

(3)	The Day-Ahead Settlement Point Price of the Hub for a given Operating Hour is calculated as follows:

DASPP South345	=	Σhb(HUBDF hb, South345 * DAHBP hb, South345) , if HB South345≠0

DASPP South345	=	DASPPERCOT345Bus, if HB South345=0

Where:

DAHBP hb, South345	=	Σb(HBDF b, hb, South345 * DALMP b, hb, South345)

HUBDF hb, South345	=	IF(HB South345=0, 0, 1 / HB South345)

HBDF b, hb, South345	=	IF(B hb, South345=0, 0, 1 / B hb, South345)

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| DASPP South345 | $/MWh | Day-Ahead Settlement Point PriceThe DAM Settlement Point Price at the Hub, for the hour. |
| DAHBP hb, South345 | $/MWh | Day-Ahead Hub Bus Price at Hub BusThe DAM energy price at Hub Bus hb for the hour. |
| DALMP b, hb, South345 | $/MWh | Day-Ahead Locational Marginal Price at Electrical Bus of Hub BusThe DAM LMP at Electrical Bus b that is a component of Hub Bus hb for the hour. |
| HUBDF hb, South345 | none | Hub Distribution Factor per Hub BusThe distribution factor of Hub Bus hb. |
| HBDF b, hb, South345 | none | Hub Bus Distribution Factor per Electrical Bus of Hub BusThe distribution factor of Electrical Bus b that is a component of Hub Bus hb. |
| b | none | An energized Electrical Bus that is a component of a Hub Bus. |
| B hb, South345 | none | The total number of energized Electrical Buses in Hub Bus hb. |
| hb | none | A Hub Bus that is a component of the Hub. |
| HB South345 | none | The total number of Hub Buses in the Hub with at least one energized component in each Hub Bus. |

(4)	The Real-Time Settlement Point Price of the Hub for a given 15-minute Settlement Interval is calculated as follows:

RTSPP South345	=	Σhb(HUBDF hb, South345 * (Σy(RTHBP hb, South345, y * TLMP y) / (ΣyTLMP y))), if HB South345≠0

RTSPP South345	=	RTSPPERCOT345Bus, if HB South345=0

Where:

RTHBP hb, South345, y	=	Σb(HBDF b, hb, South345 * RTLMP b, hb, South345, y)

HUBDF hb, South345	=	IF(HB South345=0, 0, 1 / HB South345)

HBDF b, hb, South345	=	IF(B hb, South345=0, 0, 1 / B hb, South345)

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTSPP South345 | $/MWh | Real-Time Settlement Point PriceThe Real-Time Settlement Point Price at the Hub, for the 15-minute Settlement Interval. |
| RTHBP hb, South345, y | $/MWh | Real-Time Hub Bus Price at Hub Bus per SCED intervalThe Real-Time energy price at Hub Bus hb for the SCED interval y. |
| RTLMP b, hb, South345, y | $/MWh | Real-Time Locational Marginal Price at Electrical Bus of Hub Bus per intervalThe Real-Time LMP at Electrical Bus b that is a component of Hub Bus hb, for the SCED interval y. |
| TLMP y | second | Duration of SCED interval per intervalThe duration of the portion of the SCED interval y within the 15-minute Settlement Interval |
| HUBDF hb, South345 | none | Hub Distribution Factor per Hub BusThe distribution factor of Hub Bus hb. |
| HBDF b, hb, South345 | none | Hub Bus Distribution Factor per Electrical Bus of Hub BusThe distribution factor of Electrical Bus b that is a component of Hub Bus hb. |
| y | none | A SCED interval in the 15-minute Settlement Interval. The summation is over the total number of SCED runs that cover the 15-minute Settlement Interval. |
| b | none | An energized Electrical Bus that is a component of a Hub Bus. |
| B hb, South345 | none | The total number of energized Electrical Buses in Hub Bus hb. |
| hb | none | A Hub Bus that is a component of the Hub. |
| HB South345 | none | The total number of Hub Buses in the Hub with at least one energized component in each Hub Bus. |

3.5.2.3	Houston 345 kV Hub (Houston 345)

(1)	The Houston 345 kV Hub is composed of the following listed Hub Buses:

|  | ERCOT Operations |  |  |
| --- | --- | --- | --- |
| No. | Hub Bus | kV | Hub |
| 1 | ADK | 345 | HOUSTON |
| 2 | _BI | 345 | HOUSTON |
| 3 | CBY | 345 | HOUSTON |
| 4 | CTR | 345 | HOUSTON |
| 5 | CHB | 345 | HOUSTON |
| 6 | DPW | 345 | HOUSTON |
| 7 | DOW | 345 | HOUSTON |
| 8 | RNS | 345 | HOUSTON |
| 9 | GBY | 345 | HOUSTON |
| 10 | _JN | 345 | HOUSTON |
| 11 | _KG | 345 | HOUSTON |
| 12 | KDL | 345 | HOUSTON |
| 13 | _NB | 345 | HOUSTON |
| 14 | _OB | 345 | HOUSTON |
| 15 | PHR | 345 | HOUSTON |
| 16 | SDN | 345 | HOUSTON |
| 17 | SMITHERS | 345 | HOUSTON |
| 18 | THW | 345 | HOUSTON |
| 19 | WAP | 345 | HOUSTON |
| 20 | _WO | 345 | HOUSTON |

(2)	The Houston 345 kV Hub Price is the simple average of the Hub Bus prices for each hour of the Settlement Interval of the DAM in the Day-Ahead and is the simple average of the time-weighted Hub Bus prices for each 15-minute Settlement Interval in Real-Time, for each Hub Bus included in this Hub.

(3)	The Day-Ahead Settlement Point Price of the Hub for a given Operating Hour is calculated as follows:

DASPP Houston345	=	Σhb(HUBDF hb, Houston345 * DAHBP hb, Houston345), if HB Houston345≠0

DASPP Houston345	=	DASPPERCOT345Bus, if HB Houston345=0

Where:

DAHBP hb, Houston345	=	Σb(HBDF b, hb, Houston345 * DALMP b, hb, Houston345)

HUBDF hb, Houston345	=	IF(HB Houston345=0, 0, 1 / HB Houston345)

HBDF b, hb, Houston345	=	IF(B hb, Houston345=0, 0, 1 / B hb, Houston345)

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| DASPP Houston345 | $/MWh | Day-Ahead Settlement Point PriceThe DAM Settlement Point Price at the Hub, for the hour. |
| DAHBP hb, Houston345 | $/MWh | Day-Ahead Hub Bus Price at Hub BusThe DAM energy price at Hub Bus hb for the hour. |
| DALMP b, hb, Houston345 | $/MWh | Day-Ahead Locational Marginal Price at Electrical Bus of Hub BusThe DAM LMP at Electrical Bus b that is a component of Hub Bus hb for the hour. |
| HUBDF hb, Houston345 | none | Hub Distribution Factor per Hub BusThe distribution factor of Hub Bus hb. |
| HBDF b, hb, Houston345 | none | Hub Bus Distribution Factor per Electrical Bus of Hub BusThe distribution factor of Electrical Bus b that is a component of Hub Bus hb. |
| b | none | An energized Electrical Bus that is a component of a Hub Bus. |
| B hb, Houston345 | none | The total number of energized Electrical Buses in Hub Bus hb. |
| hb | none | A Hub Bus that is a component of the Hub. |
| HB Houston345 | none | The total number of Hub Buses in the Hub with at least one energized component in each Hub Bus. |

(4)	The Real-Time Settlement Point Price of the Hub for a given 15-minute Settlement Interval is calculated as follows:

RTSPP Houston345	=	Σhb(HUBDF hb, Houston345 * (Σy(RTHBP hb, Houston345, y * TLMP y) / (ΣyTLMP y))), if HB Houston345≠0

RTSPP Houston345	=	RTSPPERCOT345Bus, if HB Houston345=0

Where:

RTHBP hb, Houston345, y	=	Σb(HBDF b, hb, Houston345 * RTLMP b, hb, Houston345, y)

HUBDF hb, Houston345	=	IF(HB Houston345=0, 0, 1 / HB Houston345)

HBDF b, hb, Houston345	=	IF(B hb, Houston345=0, 0, 1 / B hb, Houston345)

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTSPP Houston345 | $/MWh | Real-Time Settlement Point PriceThe Real-Time Settlement Point Price at the Hub, for the 15-minute Settlement Interval. |
| RTHBP hb, Houston345, y | $/MWh | Real-Time Hub Bus Price at Hub Bus per SCED intervalThe Real-Time energy price at Hub Bus hb for the SCED interval y. |
| RTLMP b, hb, Houston345, y | $/MWh | Real-Time Locational Marginal Price at Electrical Bus of Hub Bus per intervalThe Real-Time LMP at Electrical Bus b that is a component of Hub Bus hb, for the SCED interval y. |
| TLMP y | second | Duration of SCED interval per intervalThe duration of the portion of the SCED interval y within the 15-minute Settlement Interval |
| HUBDF hb, Houston345 | none | Hub Distribution Factor per Hub BusThe distribution factor of Hub Bus hb. |
| HBDF b, hb, Houston345 | none | Hub Bus Distribution Factor per Electrical Bus of Hub BusThe distribution factor of Electrical Bus b that is a component of Hub Bus hb. |
| y | none | A SCED interval in the 15-minute Settlement Interval. The summation is over the total number of SCED runs that cover the 15-minute Settlement Interval. |
| b | none | An energized Electrical Bus that is a component of a Hub Bus. |
| B hb, Houston345 | none | The total number of energized Electrical Buses in Hub Bus hb. |
| hb | none | A Hub Bus that is a component of the Hub. |
| HB Houston345 | none | The total number of Hub Buses in the Hub with at least one energized component in each Hub Bus. |

3.5.2.4	West 345 kV Hub (West 345)

(1)	The West 345 kV Hub is composed of the following listed Hub Buses:

|  | ERCOT Operations |  |  |
| --- | --- | --- | --- |
| No. | Hub Bus | kV | Hub |
| 1 | ABMB | 345 | WEST |
| 2 | BOMSW | 345 | WEST |
| 3 | OECCS | 345 | WEST |
| 4 | BTRCK | 345 | WEST |
| 5 | FSHSW | 345 | WEST |
| 6 | FLCNS | 345 | WEST |
| 7 | GRSES | 345 | WEST |
| 8 | JCKSW | 345 | WEST |
| 9 | MDLNE | 345 | WEST |
| 10 | MOSSW | 345 | WEST |
| 11 | MGSES | 345 | WEST |
| 12 | DCTM | 345 | WEST |
| 13 | ODEHV | 345 | WEST |
| 14 | OKLA | 345 | WEST |
| 15 | SARC | 345 | WEST |
| 16 | SWCOG | 345 | WEST |
| 17 | TWINBUTE | 345 | WEST |

(2)	The West 345 kV Hub Price is the simple average of the Hub Bus prices for each hour of the Settlement Interval of the DAM in the Day-Ahead and is the simple average of the time weighted Hub Bus prices for each 15-minute Settlement Interval in Real-Time, for each Hub Bus included in this Hub.

(3)	The Day-Ahead Settlement Point Price of the Hub for a given Operating Hour is calculated as follows:

DASPP West345	=	Σhb(HUBDF hb, West345 * DAHBP hb, West345), if HB West345≠0

DASPP West345	=	DASPPERCOT345Bus, if HB West345=0

Where:

DAHBP hb, West345	=	Σb(HBDF b, hb, West345 * DALMP b, hb, West345)

HUBDF hb, West345	=	IF(HB West345=0, 0, 1 / HB West345)

HBDF b, hb, West345	=	IF(B hb, West345=0, 0, 1 / B hb, West345)

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| DASPP West345 | $/MWh | Day-Ahead Settlement Point PriceThe DAM Settlement Point Price at the Hub, for the hour. |
| DAHBP hb, West345 | $/MWh | Day-Ahead Hub Bus Price at Hub BusThe DAM energy price at Hub Bus hb for the hour. |
| DALMP b, hb, West345 | $/MWh | Day-Ahead Locational Marginal Price at Electrical Bus of Hub BusThe DAM LMP at Electrical Bus b that is a component of Hub Bus hb for the hour. |
| HUBDF hb, West345 | none | Hub Distribution Factor per Hub BusThe distribution factor of Hub Bus hb. |
| HBDF b, hb, West345 | none | Hub Bus Distribution Factor per Electrical Bus of Hub BusThe distribution factor of Electrical Bus b that is a component of Hub Bus hb. |
| b | none | An energized Electrical Bus that is a component of a Hub Bus. |
| B hb, West345 | none | The total number of energized Electrical Buses in Hub Bus hb. |
| hb | none | A Hub Bus that is a component of the Hub. |
| HB West345 | none | The total number of Hub Buses in the Hub. |

(4)	The Real-Time Settlement Point Price of the Hub for a given 15-minute Settlement Interval is calculated as follows:

RTSPP West345	=	Σhb(HUBDF hb, West345 * (Σy(RTHBP hb, West345, y * TLMP y) / (ΣyTLMP y))), if HB West345≠0

RTSPP West345	=	RTSPPERCOT345Bus, if HB West345=0

Where:

RTHBP hb, West345, y	=	Σb(HBDF b, hb, West345 * RTLMP b, hb, West345, y)

HUBDF hb, West345	=	IF(HB West345=0, 0, 1 / HB West345)

HBDF b, hb, West345	=	IF(B hb, West345=0, 0, 1 / B hb, West345)

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTSPP West345 | $/MWh | Real-Time Settlement Point PriceThe Real-Time Settlement Point Price at the Hub, for the 15-minute Settlement Interval. |
| RTHBP hb, West345, y | $/MWh | Real-Time Hub Bus Price at Hub Bus per SCED intervalThe Real-Time energy price at Hub Bus hb for the SCED interval y. |
| RTLMP b, hb, West345, y | $/MWh | Real-Time Locational Marginal Price at Electrical Bus of Hub Bus per intervalThe Real-Time LMP at Electrical Bus b that is a component of Hub Bus hb, for the SCED interval y. |
| TLMP y | second | Duration of SCED interval per intervalThe duration of the portion of the SCED interval y within the 15-minute Settlement Interval |
| HUBDF hb, West345 | none | Hub Distribution Factor per Hub BusThe distribution factor of Hub Bus hb. |
| HBDF b, hb, West345 | none | Hub Bus Distribution Factor per Electrical Bus of Hub BusThe distribution factor of Electrical Bus b that is a component of Hub Bus hb. |
| y | none | A SCED interval in the 15-minute Settlement Interval. The summation is over the total number of SCED runs that cover the 15-minute Settlement Interval. |
| b | none | An energized Electrical Bus that is a component of a Hub Bus. |
| B hb, West345 | none | The total number of energized Electrical Buses in Hub Bus hb. |
| hb | none | A Hub Bus that is a component of the Hub. |
| HB West345 | none | The total number of Hub Buses in the Hub with at least one energized component in each Hub Bus. |

3.5.2.5	ERCOT Hub Average 345 kV Hub (ERCOT 345)

(1)	The ERCOT Hub Average 345 kV Hub price, for both Day-Ahead and Real-Time, is the simple average of four prices from the applicable time period: the North 345 kV Hub price, the South 345 kV Hub price, the Houston 345 kV Hub price, and the West 345 kV Hub price.

(2)	The Day-Ahead Settlement Point Price for the Hub “ERCOT 345” for a given Operating Hour is calculated as follows:

DASPP ERCOT345	=	(DASPP North345 + DASPP South345 + DASPP Houston345 + DASPP West345) / 4

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| DASPP ERCOT345 | $/MWh | Day-Ahead Settlement Point Price at ERCOT 345The DAM Settlement Point Price at ERCOT 345 Hub for the hour. |
| DASPP North345 | $/MWh | Day-Ahead Settlement Point Price at North 345The DAM Settlement Point Price at the North 345 Hub for the hour. |
| DASPP South345 | $/MWh | Day-Ahead Settlement Point Price at South 345The DAM Settlement Point Price at the South 345 Hub for the hour. |
| DASPP Houston345 | $/MWh | Day-Ahead Settlement Point Price at Houston 345The DAM Settlement Point Price at the Houston 345 Hub for the hour. |
| DASPP West345 | $/MWh | Day-Ahead Settlement Point Price at West 345The DAM Settlement Point Price at the West 345 Hub for the hour. |

(3)	The Real-Time Settlement Point Price for the Hub “ERCOT 345” for a given 15-minute Settlement Interval is calculated as follows:

RTSPP ERCOT345	=	(RTSPP North345 + RTSPP South345 + RTSPP Houston345 + RTSPP West345) / 4

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| RTSPP ERCOT345 | $/MWh | Real-Time Settlement Point Price at ERCOT 345The Real-Time Settlement Point Price at ERCOT 345 Hub for the 15-minute Settlement Interval. |
| RTSPP North345 | $/MWh | Real-Time Settlement Point Price at North 345The Real-Time Settlement Point Price at the North 345 Hub for the 15-minute Settlement Interval. |
| RTSPP South345 | $/MWh | Real-Time Settlement Point Price at South 345The Real-Time Settlement Point Price at the South 345 Hub for the 15-minute Settlement Interval. |
| RTSPP Houston345 | $/MWh | Real-Time Settlement Point Price at Houston 345The Real-Time Settlement Point Price at the Houston 345 Hub for the 15-minute Settlement Interval. |
| RTSPP West345 | $/MWh | Real-Time Settlement Point Price at West 345The Real-Time Settlement Point Price at the West 345 Hub for the 15-minute Settlement Interval. |

3.5.2.6	ERCOT Bus Average 345 kV Hub (ERCOT 345 Bus)

(1)	The ERCOT Bus Average 345 kV Hub is composed of the Hub Buses listed in Section 3.5.2.1, North 345 kV Hub (North 345); Section 3.5.2.2, South 345 kV Hub (South 345); Section 3.5.2.3, Houston 345 kV Hub (Houston 345); and Section 3.5.2.4,West 345 kV Hub (West 345).

(2)	The ERCOT Bus Average 345 kV Hub is the simple average of the Hub Bus prices for each hour of the Settlement Interval of the DAM in the Day-Ahead and is the simple average of the time weighted Hub Bus prices for each 15-minute Settlement Interval in Real-Time, for each Hub Bus included in this Hub.

(3)	The Day-Ahead Settlement Point Price of the Hub for a given Operating Hour is calculated as follows:

DASPP ERCOT345Bus	=	Σhb(HUBDF hb, ERCOT345Bus * DAHBP hb, ERCOT345Bus), if HB ERCOT345Bus ≠0

DASPP ERCOT345Bus	=	0, if HB ERCOT345Bus =0

Where:

DAHBP hb, ERCOT345Bus	=	Σb(HBDF b, hb, ERCOT345Bus * DALMP b, hb, ERCOT345Bus)

HUBDF hb, ERCOT345Bus	=	1 / (HB North345 + HB South345 + HB Houston345 + HB West345)

If Electrical Bus b is a component of “North 345”

HBDF b, hb, ERCOT345Bus	=	IF(B hb, North345=0, 0, 1 / B hb, North345)

Otherwise

If Electrical Bus b is a component of “South 345”

HBDF b, hb, ERCOT345Bus	=	IF(B hb, South345=0, 0, 1 / B hb, South345)

Otherwise

If Electrical Bus b is a component of “Houston 345”

HBDF b, hb, ERCOT345Bus	=	IF(B hb, Houston345=0, 0, 1 / B hb, Houston345)

Otherwise

HBDF b, hb, ERCOT345Bus	=	IF(B hb, West345=0, 0, 1 / B hb, West345)

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| DASPP ERCOT345Bus | $/MWh | Day-Ahead Settlement Point PriceThe DAM Settlement Point Price at the Hub, for the hour. |
| DAHBP hb, ERCOT345Bus | $/MWh | Day-Ahead Hub Bus Price at Hub BusThe DAM energy price at Hub Bus hb for the hour. |
| DALMP b, hb, ERCOT345Bus | $/MWh | Day-Ahead Locational Marginal Price at Electrical Bus of Hub BusThe DAM LMP at Electrical Bus b that is a component of Hub Bus hb for the hour. |
| HUBDF hb, ERCOT345Bus | none | Hub Distribution Factor per Hub BusThe distribution factor of Hub Bus hb. |
| HBDF b, hb, ERCOT345Bus | none | Hub Bus Distribution Factor per Electrical Bus of Hub BusThe distribution factor of Electrical Bus b that is a component of Hub Bus hb. |
| b | none | An energized Electrical Bus that is a component of a Hub Bus. |
| B hb, North345 | none | The total number of energized Electrical Buses in Hub Bus hb that is a component of “North 345”. |
| B hb, South345 | none | The total number of energized Electrical Buses in Hub Bus hb that is a component of “South 345”. |
| B hb, Houston345 | none | The total number of energized Electrical Buses in Hub Bus hb that is a component of “Houston 345”. |
| B hb, West345 | none | The total number of energized Electrical Buses in Hub Bus hb that is a component of “West 345”. |
| hb | none | A Hub Bus that is a component of the Hub. |
| HB North345 | none | The total number of Hub Buses in “North 345”. |
| HB South345 | none | The total number of Hub Buses in “South 345”. |
| HB Houston345 | none | The total number of Hub Buses in “Houston 345”. |
| HB West345 | none | The total number of Hub Buses in “West 345”. |

(4)	The Real-Time Settlement Point Price of the Hub for a given 15-minute Settlement Interval is calculated as follows:

RTSPP ERCOT345Bus	=	Σhb(HUBDF hb, ERCOT345Bus * (Σy(RTHBP hb, ERCOT345Bus, y * TLMP y) / (ΣyTLMP y))), if HB ERCOT345Bus ≠0

RTSPP ERCOT345Bus	=	0, if HB ERCOT345Bus =0

Where:

RTHBP hb, ERCOT345Bus, y	=	Σb(HBDF b, hb, ERCOT345Bus * RTLMP b, hb, ERCOT345Bus, y)

HUBDF hb, ERCOT345Bus	=	1 / (HB North345 + HB South345 + HB Houston345 + HB West345)

If Electrical Bus b is a component of “North 345”

HBDF b, hb, ERCOT345Bus	=	IF(B hb, North345=0, 0, 1 / B hb, North345)

Otherwise

If Electrical Bus b is a component of “South 345”

HBDF b, hb, ERCOT345Bus	=	IF(B hb, South345=0, 0, 1 / B hb, South345)

Otherwise

If Electrical Bus b is a component of “Houston 345”

HBDF b, hb, ERCOT345Bus	=	IF(B hb, Houston345=0, 0, 1 / B hb, Houston345)

Otherwise

HBDF b, hb, ERCOT345Bus	=	IF(B hb, West345=0, 0, 1 / B hb, West345)

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTSPP ERCOT345Bus | $/MWh | Real-Time Settlement Point PriceThe Real-Time Settlement Point Price at the Hub, for the 15-minute Settlement Interval. |
| RTHBP hb, ERCOT345Bus, y | $/MWh | Real-Time Hub Bus Price at Hub Bus per SCED intervalThe Real-Time energy price at Hub Bus hb for the SCED interval y. |
| RTLMP b, hb, ERCOT345Bus, y | $/MWh | Real-Time Locational Marginal Price at Electrical Bus of Hub Bus per intervalThe Real-Time LMP at Electrical Bus b that is a component of Hub Bus hb, for the SCED interval y. |
| TLMP y | second | Duration of SCED interval per intervalThe duration of the portion of the SCED interval y within the 15-minute Settlement Interval |
| HUBDF hb, ERCOT345Bus | none | Hub Distribution Factor per Hub BusThe distribution factor of Hub Bus hb. |
| HBDF b, hb, ERCOT345Bus | none | Hub Bus Distribution Factor per Electrical Bus of Hub BusThe distribution factor of Electrical Bus b that is a component of Hub Bus hb. |
| y | none | A SCED interval in the 15-minute Settlement Interval. The summation is over the total number of SCED runs that cover the 15-minute Settlement Interval. |
| b | none | An energized Electrical Bus that is a component of a Hub Bus. |
| B hb, North345 | none | The total number of energized Electrical Buses in Hub Bus hb that is a component of “North 345”. |
| B hb, South345 | none | The total number of energized Electrical Buses in Hub Bus hb that is a component of “South 345”. |
| B hb, Houston345 | none | The total number of energized Electrical Buses in Hub Bus hb that is a component of “Houston 345”. |
| B hb, West345 | none | The total number of energized Electrical Buses in Hub Bus hb that is a component of “West 345”. |
| hb | none | A Hub Bus that is a component of the Hub. |
| HB North345 | none | The total number of Hub Buses in “North 345”. |
| HB South345 | none | The total number of Hub Buses in “South 345”. |
| HB Houston345 | none | The total number of Hub Buses in “Houston 345”. |
| HB West345 | none | The total number of Hub Buses in “West 345”. |

3.5.3	ERCOT Responsibilities for Managing Hubs

3.5.3.1	Posting of Hub Buses and Electrical Buses included in Hubs

ERCOT shall post a list of all the Hub Buses included in each Hub on the MIS Public area.  The list must include the name and kV rating for each Electrical Bus included in each Hub Bus.

3.5.3.2	Calculation of Hub Prices

ERCOT shall calculate Hub prices for each Settlement Interval as identified in the description of each Hub.

3.6	Load Participation

(1)	Load Resources may participate by providing the following types of service:

(a)	Ancillary Service:

(i)	Regulation Up Reserve Service (Reg-Up);

(ii)	Regulation Down Reserve Service (Reg-Down);

(iii)	Responsive Reserve Service (RRS);

(iv)	Non-Spinning Reserve Service (Non-Spin); and

(b)	Voluntary load response in Real-Time.

(2)	Except for voluntary load response, loads participating in any ERCOT market must be individually registered as a Load Resource by ESID and are subject to qualification testing administered by ERCOT.  All ERCOT settlements resulting from Load Resource participation are made only with the QSE representing the Load Resource.

3.7	Resource Parameters

(1)	A Resource Entity shall register Resource Parameters for its Resources with ERCOT.

(2)	ERCOT shall provide each Qualified Scheduling Entity (QSE) that represents a Resource the ability to submit changes to Resource Parameters for that Resource.

(3)	The QSE may revise Resource Parameters only with sufficient documentation to justify a change in Resource Parameters.

(4)	ERCOT shall use the Resource Parameters as inputs into the Day-Ahead Market (DAM), Reliability Unit Commitment (RUC), Security-Constrained Economic Dispatch (SCED), Resource Limit Calculator, Load Frequency Control (LFC), and other ERCOT business processes.

(5)	The Independent Market Monitor (IMM) may require the QSE to provide justification for the Resource Parameters submitted.

(6)	Seasons for seasonal parameters are defined in the Operating Guides.

(7)	The QSE or Resource Entity must update any Resource Parameter for a specific Resource:

(a)	Within ten Business Days of completion of a Net Dependable Capability test to reflect the results of the test;

(b)	Within ten Business Days of completion of a reactive capability test to reflect the results of the test;

(c)	Within ten Business Days of a request by ERCOT to check or update a specific Resource Parameter; and

(d)	Within ten Business Days of a known change to any Resource Parameter.

3.7.1	Resource Parameter Criteria

3.7.1.1	Generation Resource Parameters

(1)	General Resource Parameters submitted by a Resource Entity must include the following for each of its Generation Resources:

(a)	The Resource’s name;

(b)	High Reasonability Limit (HRL) used in Incremental and Decremental Energy Offer Curves and to verify operator entries of High Sustained Limit (HSL);

(c)	Low Reasonability Limit (LRL) used in Incremental and Decremental Energy Offer Curves and to verify operator entries of Low Sustained Limit (LSL);

(d)	Type of Resource – steam turbine, hydro, gas turbine, combined cycle, other;

(e)	Qualifying Facility (QF) status, if applicable;

(f)	Normal Ramp Rate curve;

(g)	Emergency Ramp Rate curve;

(h)	Minimum On-Line time – The minimum number of consecutive hours the Resource must be On-Line before being shut down;

(i)	Minimum Off-Line time – The minimum number of consecutive hours the Resource must be Off-Line before being restarted;

(j)	Hot start time – The time, in hours, from the ERCOT notice to LSL, for a Resource in its hot-temperature state;

(k)	Intermediate start time – The time interval, in hours, from the ERCOT notice to LSL, for a Resource in its intermediate temperature state; and

(l)	Cold start time – The time interval, in hours, from the ERCOT notice to LSL, for a Resource in its cold-temperature state.

(2)	Seasonal Resource Parameters must be submitted by a Resource Entity and must include the following for each of its Generation Resources:

(a)	Seasonal gross and net MW rating;

(b)	Conversion constants to be used to convert from gross MW to net MW or net MW to gross MW in accordance with ERCOT Operating Guides, if applicable;

(c)	Maximum weekly starts – The maximum number of times a Resource can be started in seven consecutive days under normal operating conditions;

(d)	Maximum On-Line time – The maximum number of consecutive hours a Resource can run before it needs to be shut down;

(e)	Maximum daily starts – The maximum number of times a Resource can be started in a 24 hour period under normal operating conditions;

(f)	Maximum weekly energy – The maximum amount of energy, in MWh, a Resource can produce in seven consecutive days;

(g)	Hot-to-intermediate time – The time, in hours, after shutdown that a hot-temperature-state Resource takes to cool down to intermediate-temperature state; and

(h)	Intermediate-to-cold time – The time, in hours, after shutdown that an intermediate-temperature-state Resource takes to cool down to cold-temperature state.

3.7.1.2	Load Resource Parameters

(1)	Resource Parameters submitted by a Resource Entity must include the following for each of its Load Resources that is not a Controllable Load Resource:

(a)	The Resource’s name;

(b)	High reasonability limit used to verify operator entries for HSL;

(c)	Low reasonability limit used to verify operator entries for LSL;

(d)	Minimum interruption time – The minimum number of consecutive hours the Resource can be deployed (between breaker open to breaker close);

(e)	Minimum restoration time – The minimum number of consecutive hours the Resource must remain energized (not deployed), from the time the Resource is restored from interruption and available for the next potential interruption;

(f)	Maximum weekly deployments – The maximum number of times the Resource can be deployed in seven consecutive days under normal operating conditions;

(g)	Maximum interruption time – The maximum number of consecutive hours the Resource can remain deployed before it needs to be energized;

(h)	Maximum daily deployments – The maximum number of times the Resource can be deployed in a day under normal operating conditions;

(i)	Maximum weekly energy – The maximum amount of energy, in MWh, a for which the Resource can be deployed in seven consecutive days; and

(j)	Minimum notice time – The notice time that the Resource requires before deployment (e.g., instantaneous, 30 minutes, etc.).

(2)	Resource Parameters submitted by a Resource Entity must include the following for each of its Controllable Load Resources:

(a)	The Resource’s name;

(b)	High reasonability limit used to verify operator entries for the HSL;

(c)	Low reasonability limit used to verify operator entries for the LSL;

(d)	Normal Ramp Rate curve;

(e)	Emergency Ramp Rate curve;

(f)	Maximum deployment time – The maximum amount of time a Controllable Load Resource can be deployed before it must return to normal operating conditions; and

(g)	Maximum weekly energy – The maximum amount of energy a Controllable Load Resource can be deployed in seven consecutive days.

3.7.1.3	Changes in Resource Parameters with Operational Impacts

The QSE representing each Resource shall have the responsibility to submit changes to Resource Parameters for those Resource Parameters related to the Current Operating Plan (COP), as described in Section 3.9, Current Operating Plan (COP), and to Real-Time operations as described in Section 6, Adjustment Period and Real-Time Operations.  If the QSE cancels a Resource Parameter submission, ERCOT will use as a default the Resource Parameter that was provided through the registration or Network Operations Model Change Request (NOMCR) process.

3.7.2	Resource Parameter Validation

ERCOT shall verify that changes to Resource Parameters submitted by a Resource Entity or the QSE representing the Resource comply with the applicable criteria in Section 3.7.1, Resource Parameter Criteria.  If a Resource Parameter is determined to be invalid, then ERCOT shall reject it and provide written notice to the Resource Entity or the QSE representing the Resource, as appropriate, of the reason for the rejection.

3.8	Special Considerations for Split Generation Meters, Combined Cycle Generation Resources, Quick Start Generation Resources, and Hydro Generation Resources

### 3.8.1	Split Generation Resources

(1)	When a generation meter is split, as provided for in Section 10.3.2.1, Generation Resource Meter Splitting, two or more independent Generation Resources must be created in the ERCOT Network Operations Model according to Section 3.10.7.2, Modeling of Resources and Transmission Loads, to function in all respects as Split Generation Resources in ERCOT System operation.  A Combined Cycle Train may not be registered in ERCOT as a Split Generation Resource.

(2)	Each Qualified Scheduling Entity (QSE) representing a Split Generation Resource shall collect and shall submit to ERCOT the Resource Parameters defined under Section 3.7, Resource Parameters, for the Split Generation Resource it represents.  The parameters provided must be consistent with the parameters submitted by each other QSE that represents a Split Generation Resource from the same Generation Resource.  The parameters submitted for each Split Generation Resource for limits and ramp rates must be according to the capability of the Split Generation Resource represented by the QSE.  Startup and shutdown times, time to change status and number of starts must be identical for all the Split Generation Resources from the same Generation Resource submitted by each QSE.  ERCOT shall review data submitted by each QSE representing Split Generation Resources for consistency and notify each QSE of any errors.

(3)	Each Split Generation Resource may be represented by a different QSE.  The Resource Entities that own or control the Split Generation Resources from a single Generation Resource must designate a Master QSE.  Each QSE representing a Split Generation Resource must comply in all respects to the requirements of a Generation Resource specified under these Protocols.

(4)	The Master QSE shall:

(a)	Serve as the Single Point of Contact for the Generation Resource, as required by Section 3.1.4.1, Single Point of Contact;

(b)	Provide real-time telemetry for the total Generation Resource, as specified in Section 6.5.5.2, Operational Data Requirements; and

(c)	Receive Verbal Dispatch Instructions (VDIs) from ERCOT, as specified in Section 6.5.7.8, Dispatch Procedures.

(5)	Each QSE is responsible for representing its Split Generation Resource in its Current Operating Plan (COP).  During the Reliability Unit Commitment (RUC) Study Periods, any conflict in the Resource Status of a Split Generation Resource in the COP is resolved according to the following:

(a)	If a Split Generation Resource has a Resource Status of OUT for any hour in the COP, then any other QSEs’ COP entries for their Split Generation Resources from the same Generation Resource are also considered unavailable for the hour;

(b)	If the QSEs for all Split Generation Resources from the same Generation Resource have submitted a COP and at least one of the QSEs has an On-Line Resource Status in a given hour, then the status for all Split Generation Resources for the Generation Resource is considered to be On-Line for that hour, except if any of the QSEs has indicated in the COP a Resource Status of OUT.

(6)	Each QSE representing a Split Generation Resource shall update its individual Resource Status appropriately.

(7)	Each QSE representing a Split Generation Resource may independently submit Energy Offer Curves and Three-Part Supply Offers.  ERCOT shall treat each Split Generation Resource offer as a separate offer, except that all Split Generation Resources in a single Generation Resource must be committed or decommitted together.

(8)	Each QSE submitting verifiable cost data to ERCOT shall coordinate among all owners of a single Generation Resource to provide individual Split Generation Resource data consistent with the total verifiable cost of the entire Generation Resource.  ERCOT may compare the total verifiable costs with other similarly situated Generation Resources to determine the reasonability of the cost.

3.8.2	Combined Cycle Generation Resources

(1)	ERCOT shall assign a logical Resource Node for use in the Day-Ahead Market (DAM), RUC, Supplemental Ancillary Services Market (SASM), Security-Constrained Economic Dispatch (SCED) and Load Frequency Control (LFC) to each registered Combined Cycle Train.  Each Combined Cycle Generation Resource registered in the Combined Cycle Train will be mapped to the Combined Cycle Train logical Resource Node for the purposes of evaluating and settling each Combined Cycle Generation Resource’s Three-Part Supply Offer and Ancillary Service Offer in the DAM, RUC and SCED.  Each generation unit identified in the Combined Cycle Train registration for a Combined Cycle Generation Resource configuration will be mapped to its designated Resource Node as determined in accordance with these Protocols and the Technical Advisory Committee (TAC) approved ERCOT Procedure for Identifying Resource Nodes.

(2)	If any of the generation units, designated in the Combined Cycle Train registration as a primary generation unit in a Combined Cycle Generation Resource, is isolated from the ERCOT Transmission Grid because of a transmission Outage reported in the Outage Scheduler, the DAM and RUC applications shall select an alternate generation unit for use in the application.

(3)	Three-Part Supply Offers and Resource-specific Ancillary Service Offers submitted for a Combined Cycle Generation Resource may only be made at the Resource’s logical Resource Node.  ERCOT shall use the logical Resource Node to settle these offers.

(4)	In the DAM and RUC, ERCOT shall model the energy injection from each generation unit registered to the Combine Cycle Generation Resource designated in a Three Part Supply Offer as follows:

(a)	The energy injection for each generation unit registered in the Combined Cycle Generation Resource designated in a Three-Part Supply Offer shall be the offered energy injection for the selected price point on the Three-Part Supply Offer’s Energy Offer Curve times a weight factor as determined in paragraph (4)(b) below.

(b)	The weight factor for each generation unit registered in a Combined Cycle Generation Resource shall be the generation unit’s High Reasonability Limit (HRL), as specified in its ERCOT approved Resource Asset Registration Form, divided by the total of all HRL values for the generation units registered in the designated Combine Cycle Generation Resource.

(5)	In the Network Operations Network Models used in the DAM, RUC and SCED applications, each generation unit identified in the Combined Cycle Train registration must be modeled at its designated Point of Interconnection (POI).

(6)	For Ancillary Services offered and provided from Combined Cycle Generation Resources, ERCOT shall apply, without exception, the same rules and requirements specified in these Protocols for the DAM, RUC and Adjustment Period and Real-Time markets that apply to Ancillary Services provided from any other Generation Resources.

(a)	ERCOT systems shall determine the High and Low Ancillary Service Limits (HASL and LASL) for a Combined Cycle Generation Resource as follows:

(i)	In Real Time, relative to the telemetered High Sustained Limit (HSL) for the Combined Cycle Generation Resource, or

(ii)	During the DAM and RUC study periods, relative to the HSL in the COP.

(b)	The QSE shall assure that the Combined Cycle Generation Resource designated as On-Line through telemetry or in the COP can meet its Ancillary Service Resource Responsibility.

3.8.3	Quick Start Generation Resources

(1)	The QSE for a Quick Start Generation Resource (QSGR) that is available for deployment by SCED shall set the COP Resource Status ON, the COP Low Sustained Limit (LSL) and COP HSL values to the expected sustainable LSL and HSL for the QSGR for the hour.  If the QSGR is providing Non-Spinning Reserve (Non-Spin) service, then the Ancillary Service Resource Responsibility for Non-Spin shall be set to the Resource’s QSE-assigned Non-Spin responsibility in the COP.  If the QSGR’s Non-Spin responsibility is greater than the difference between HSL and LSL, then the QSGR that is available for deployment by SCED shall set the COP LSL to zero.

[NPRR272: Replace paragraph (1) above with the following upon system implementation:] (1) The QSE for a Quick Start Generation Resource (QSGR) that is available for deployment by SCED shall set the COP Resource Status to OFFQS, and the COP Low Sustained Limit (LSL) and COP HSL values to the expected sustainable LSL and HSL for the QSGR for the hour. If the QSGR is providing Non-Spinning Reserve (Non-Spin) service, then the Ancillary Service Resource Responsibility for Non-Spin shall be set to the Resource’s QSE-assigned Non-Spin responsibility in the COP.

(2)	The QSGR that is available for deployment by SCED shall telemeter a Resource Status of ON and an LSL of zero prior to receiving a deployment instruction from SCED.  This status is necessary in order for SCED to recognize that the Resource can be Dispatched.  The status of the breaker shall be open and the output of the Resource shall be zero in order for the State Estimator to correctly assess the state of the system.  After being deployed for energy from SCED, the Resource shall telemeter an LSL equal to or less than the Resource’s actual output until the Resource has ramped to its physical LSL.  After reaching its physical LSL, the QSGR shall telemeter an LSL that reflects its physical LSL.  The QSGR that is providing Off-Line Non-Spin shall always telemeter an Ancillary Service Resource Responsibility for Non-Spin to reflect the Resource’s Non-Spin obligation and shall always telemeter an Ancillary Service Schedule for Non-Spin of zero to make the capacity available for SCED.

[NPRR272: Replace paragraph (2) above with the following upon system implementation:] (2) The QSGR that is available for deployment by SCED shall telemeter a Resource Status of OFFQS and a LSL of zero prior to receiving a deployment instruction from SCED. This status is necessary in order for SCED to recognize that the Resource can be Dispatched. The status of the breaker shall be open and the output of the Resource shall be zero in order for the State Estimator to correctly assess the state of the system. After being deployed for energy from SCED, the Resource shall telemeter an LSL equal to or less than the Resource’s actual output until the Resource has ramped to its physical LSL. After reaching its physical LSL, the QSGR shall telemeter an LSL that reflects its physical LSL. The QSGR that is providing Off-Line Non-Spin shall always telemeter an Ancillary Service Resource Responsibility for Non-Spin to reflect the Resource’s Non-Spin obligation and shall always telemeter an Ancillary Service Schedule for Non-Spin of zero to make the capacity available for SCED.

(3)	A QSGR with a telemeter breaker status of open and a telemeter Resource Status of ON shall not provide Regulation Service or Responsive Reserve (RRS) Service.

[NPRR272: Replace paragraph (3) above with the following upon system implementation:] (3) A QSGR with a telemeter breaker status of open and a telemeter Resource Status OFFQS shall not provide Regulation Service or Responsive Reserve (RRS) Service.

(4)	ERCOT shall adjust the QSGR’s Mitigated Offer Cap curve as described in Section 4.4.9.4.1, Mitigated Offer Cap.

(5)	For a QSGR, the Resource Entity shall submit a Normal Ramp Rate curve and Emergency Ramp Rate curve indicating QSGR’s ability to reach its ten-minute tested output from zero output in five minutes.  This is necessary to prevent SCED from deploying multiple QSGRs due to ramp limitation in the first five minutes after being Dispatched by SCED.  QSGRs shall be exempt from Base Point Deviation Charges as described in Section 6.6.5.3, Generators Exempt from Deviation Charges.

(6)	Any hour in which the QSE for the QSGR has shown the Resource as available for SCED Dispatch as described in this Section 3.8.3 is considered a QSE-Committed Interval.

(7)	QSEs must submit and maintain an Energy Offer Curve for their QSGRs for all hours in which the COP Resource Status is submitted as ON or OFFNS.  If a valid Energy Offer Curve or an Output Schedule does not exist for any QSGR for which a Resource Status of ON is telemetered at the end of the Adjustment Period, then ERCOT shall notify the QSE and set the Output Schedule equal to the then-current telemetered output of the Resource until an Output Schedule or Energy Offer Curve is submitted in a subsequent Adjustment Period.  For use as SCED inputs, ERCOT shall create proxy Energy Offer Curves for the Resource as described in paragraph (3) of Section 6.5.7.3, Security Constrained Economic Dispatch.

[NPRR272: Replace paragraph (7) above with the following upon system implementation:] (7) QSEs must submit and maintain an Energy Offer Curve for their QSGRs for all hours in which the COP Resource Status is submitted as OFFQS. If a valid Energy Offer Curve or an Output Schedule does not exist for any QSGR for which a Resource Status of OFFQS is telemetered at the end of the Adjustment Period, then ERCOT shall notify the QSE and set the Output Schedule equal to the then-current telemetered output of the Resource until an Output Schedule or Energy Offer Curve is submitted in a subsequent Adjustment Period. For use as SCED inputs, ERCOT shall create proxy Energy Offer Curves for the Resource as described in paragraph (3) of Section 6.5.7.3, Security Constrained Economic Dispatch.

(8)	If a QSGR comes On-Line as a result of a Base Point less than its COP LSL, the energy produced during the first q consecutive Settlement Intervals beginning with the Settlement Interval in which the QSGR comes On-Line shall be considered for additional compensation pursuant to Section 6.6.9, Emergency Operations Settlement, and using SCED Base Points in place of the Emergency Base Points.  The value of q shall be reviewed at least annually by TAC.  The value of q shall be provided to the market via Market Notice within three Business Days after a TAC approval of a change in value, and the new value shall be effective on the first day of the next month.  Following a SCED QSGR deployment, the QSGR is expected to follow the SCED Base Points.

3.8.4	Hydro Generation Resources

A QSE is considered to have performed for the amount of its RRS obligation for the MW amount provided by a hydro Generation Resource operating in synchronous condenser fast-response mode and triggered by an under-frequency relay device at the frequency set point specified in paragraph (3)(b) of Section 3.18, Resource Limits in Providing Ancillary Service, without corresponding RRS deployment by ERCOT.  This provision applies only for the duration when hydro RRS MW is deployed by automatic under-frequency relay action.

3.9	Current Operating Plan (COP)

(1)	Each Qualified Scheduling Entity (QSE) that represents a Resource must submit a Current Operating Plan (COP) under this Section.

(2)	ERCOT shall use the information provided in the COP to calculate the High Ancillary Service Limit (HASL) and Low Ancillary Service Limit (LASL) for each Resource for the Reliability Unit Commitment (RUC) processes.

(3)	ERCOT shall monitor the accuracy of each QSE’s COP as outlined in Section 8, Performance Monitoring.

(4)	A QSE must notify ERCOT that it plans to have a Resource On-Line by means of the COP using the Resource Status codes listed in Section 3.9.1, Current Operating Plan (COP) Criteria, paragraph (4)(b)(i).  The QSE must show the Resource as On-Line with a Status of “ONRUC,” indicating a RUC process committed the Resource for all RUC-Committed Intervals.  A QSE may only use a RUC-committed Resource during that Resource’s RUC-Committed Interval to meet the QSE’s Ancillary Service Supply Responsibility if the Resource has been committed by the RUC process to provide Ancillary Service.

(5)	To reflect changes to a Resource’s capability, each QSE shall report by exception, changes to the COP for all hours after the Operating Period through the rest of the Operating Day.

(6)	When a QSE updates its COP to show changes in Resource status, the QSE shall update for each On-Line Resource, either an Energy Offer Curve under Section 4.4.9, Energy Offers and Bids, or Output Schedule under Section 6.4.2, Output Schedules.

(7)	Each QSE, including QSEs representing Reliability Must-Run (RMR) Units, or Black Start Resources, shall submit a revised COP reflecting changes in Resource availability as soon as reasonably practicable, but in no event later than 60 minutes after the event that caused the change.

(8)	Each QSE representing a Qualifying Facility (QF) must submit a Low Sustained Limit (LSL) that represents the minimum energy available, in MW, from the unit for economic dispatch based on the minimum stable steam delivery to the thermal host plus a justifiable reliability margin that accounts for changes in ambient conditions.

3.9.1	Current Operating Plan (COP) Criteria

(1)	Each QSE that represents a Resource must submit a COP to ERCOT that reflects expected operating conditions for each Resource for each hour in the next seven Operating Days.

(2)	Each QSE that represents a Resource shall update its COP reflecting changes in availability of any Resource as soon as reasonably practicable, but in no event later than 60 minutes after the event that caused the change.

(3)	The Resource capacity in a QSE’s COP must be sufficient to supply the Ancillary Service Supply Responsibility of that QSE.

(4)	A COP must include the following for each Resource represented by the QSE:

(a)	The name of the Resource;

(b)	The expected Resource Status:

(i)	Select one of the following for Generation Resources synchronized to the ERCOT System that best describes the Resource’s status:

[NPRR348: Replace paragraph (4)(b)(i) above with the following upon system implementation:] (i) Select one of the following for Generation Resources synchronized to the ERCOT System that best describes the Resource’s status. These Resource Statuses are to be used for COP and/or Real-Time telemetry purposes.

(A)	ONRUC – On-Line and the hour is a RUC-Committed Hour;

(B)	ONREG – On-Line Resource with Energy Offer Curve providing Regulation Service;

(C)	ON – On-Line Resource with Energy Offer Curve or Off-Line Quick Start Generation Resource (QSGR) available for Security-Constrained Economic Dispatch (SCED) Dispatch;

[NPRR272: Replace paragraph (4)(b)(i)(C) above with the following upon system implementation:] (C) ON – On-Line Resource with Energy Offer Curve;

(D)	ONDSR – On-Line Dynamically Scheduled Resource (DSR);

(E)	ONOS – On-Line Resource with Output Schedule;

(F)	ONOSREG – On-Line Resource with Output Schedule providing Regulation Service;

(G)	ONDSRREG – On-Line DSR providing Regulation Service;

(H)	ONTEST – On-Line blocked from SCED or performing an operations test or a Resource is in start-up or shut down sequence;

[NPRR348: Replace paragraph (4)(b)(i)(H) above with the following upon system implementation:] (H) ONTEST – On-Line blocked from SCED for operations testing;

(I)	ONEMR – On-Line EMR (available for commitment or dispatch only for ERCOT-declared Emergency Conditions; the QSE may appropriately set LSL and High Sustained Limit (HSL) to reflect operating limits); and

(J)	ONRR – On-Line as a synchronous condenser (hydro) providing Responsive Reserve (RRS) but unavailable for Dispatch by SCED and available for commitment by RUC;

[NPRR348: Insert paragraphs (4)(b)(i)(K) and (4)(b)(i)(L) below upon system implementation:] (K) SHUTDOWN – The Resource is On-Line and in a shut down sequence, and has no Ancillary Service Obligations. This Resource Status is only to be used for Real-Time telemetry purposes; (L) STARTUP – The Resource is On-Line and in a start-up sequence and has no Ancillary Service Obligations. This Resource Status is only to be used for Real-Time telemetry purposes;

[NPRR272: Insert paragraph (4)(b)(i)(M) upon system implementation:] (M) OFFQS – Off-Line but available for SCED deployment. Only qualified QSGRs may utilize this status.

(ii)	Select one of the following for Off-Line Generation Resources not synchronized to the ERCOT System that best describes the Resource’s status:

[NPRR348: Replace paragraph (4)(b)(ii) above with the following upon system implementation:] (ii) Select one of the following for Off-Line Generation Resources not synchronized to the ERCOT System that best describes the Resource’s status. These Resource Statuses are to be used for COP and/or Real-Time telemetry purposes.

(A)	OUT – Off-Line and unavailable;

(B)	OFFNS – Off-Line but reserved for Non-Spinning Reserve (Non-Spin);

(C)	OFF – Off-Line but available for commitment in the Day-Ahead Market (DAM) and RUC; and

(D)	EMR – Available for commitment only for ERCOT-declared Emergency Condition events; the QSE may appropriately set LSL and HSL to reflect operating limits; and

(iii)	Select one of the following for Load Resources:

[NPRR348: Replace paragraph (4)(b)(iii) above with the following upon system implementation:] (iii) Select one of the following for Load Resources. These Resource Statuses are to be used for COP and/or Real-Time telemetry purposes.

(A)	ONRGL – Available for Dispatch of Regulation Service;

(B)	ONRRCLR – Available for Dispatch of RRS Service as a Controllable Load Resource;

(C)	ONRL – Available for Dispatch of RRS Service or Non-Spin, excluding Controllable Load Resources; and

(D)	OUTL – Not available;

(c)	The HSL;

(d)	The LSL;

(e)	The High Emergency Limit (HEL);

(f)	The Low Emergency Limit (LEL); and

(g)	Ancillary Service Resource Responsibility capacity in MW for:

(i)	Regulation Up (Reg-Up);

(ii)	Regulation Down (Reg-Down);

(iii)	RRS Service; and

(iv)	Non-Spin.

(5)	For Combined Cycle Generation Resources, the above items are required for each operating configuration.  In each hour only one Combined Cycle Generation Resource in a Combined Cycle Train may be assigned one of the On-Line Resource Status codes described above.

(a)	During a RUC study period, if a QSE’s COP reports multiple Combined Cycle Generation Resources in a Combined Cycle Train to be On-Line for any hour, then until the QSE corrects its COP, the On-Line Combined Cycle Generation Resource with the largest HSL is considered to be On-Line and all other Combined Cycle Generation Resources in the Combined Cycle Train are considered to be Off-Line.  Furthermore, until the QSE corrects its COP, the Off-Line Combined Cycle Generation Resources as designated through the application of this process are ineligible for RUC commitment or de-commitment Dispatch Instructions.

(b)	For any hour in which QSE-submitted COP entries are used to determine the initial state of a Combined Cycle Generation Resource for a DAM or Day-Ahead Reliability Unit Commitment (DRUC) study and the COP shows multiple Combined-Cycle Generation Resources in a Combined Cycle Train to be in an On-line Resource Status, then until the QSE corrects its COP, the On-Line Combined Cycle Generation Resource that has been On-Line for the longest time from the last recorded start by ERCOT systems, regardless of the reason for the start, combined with the COP Resource Status for the remaining hours of the current Operating Day, is considered to be On-Line at the start of the DRUC study period and all other COP-designated Combined Cycle Generation Resources in the Combined Cycle Train are considered to be Off-Line.

(c)	ERCOT systems shall allow only one Combined Cycle Generation Resource in a Combined Cycle Train to offer Off-Line Non-Spin in the DAM or Supplemental Ancillary Services Market (SASM).

(i)	If there are multiple Non-Spin offers from different Combined Cycle Generation Resources in a Combined Cycle Train, then prior to execution of the DAM, ERCOT shall select the Non-Spin offer from the Combined Cycle Generation Resource with the highest HSL for consideration in the DAM and ignore the other offers.

(ii)	Combined Cycle Generation Resources offering Off-Line Non-Spin must be able to transition from the shutdown state to the offered Combined Cycle Generation Resource On-Line state and be capable of ramping to the full amount of the Non-Spin offered.

(d)	The DAM and RUC shall honor the registered hot, intermediate or cold Startup Costs for each Combined Cycle Generation Resource registered in a Combined Cycle Train when determining the transition costs for a Combined Cycle Generation Resource.  In the DAM and RUC, the Startup Cost for a Combined Cycle Generation Resource shall be determined by the positive transition cost from the On-Line Combined Cycle Generation Resource within the Combine Cycle Train or from a shutdown condition, whichever ERCOT determines to be appropriate.

(6)	ERCOT may accept COPs only from QSEs.

(7)	For the first 48 hours of the COP, a QSE representing a Wind-powered Generation Resource (WGR) must enter an HSL value that is less than or equal to the amount for that Resource from the most recent Short-Term Wind Power Forecast (STWPF) provided by ERCOT.

(8)	For hours 49 to 168 of the COP, a QSE representing a WGR shall enter an HSL value equal to their best estimate, which may be based on the wind power profile as published on the ERCOT website.

(9)	A QSE representing a Generation Resource that is not actively providing Ancillary Services may only use a Resource Status of ONTEST to indicate to ERCOT in the COP and through telemetry that the Resource is operating in a start-up or shut-down sequence and is being manually dispatched by the QSE or to indicate the Generation Resource is performing a test of its operations either manually dispatched by the QSE or by ERCOT as part of the test.

[NPRR348: Replace paragraph (9) above with the following upon system implementation:] (9) A QSE representing a Generation Resource that is not actively providing Ancillary Services may only use a Resource Status of SHUTDOWN to indicate to ERCOT through telemetry that the Resource is operating in a shut-down sequence or a Resource Status of ONTEST to indicate in the COP and through telemetry that the Generation Resource is performing a test of its operations either manually dispatched by the QSE or by ERCOT as part of the test. A QSE representing a Generation Resource that is not actively providing Ancillary Services may only use a Resource Status of STARTUP to indicate to ERCOT through telemetry that the Resource is operating in a start-up sequence requiring manual control and is not available for Dispatch.

(10)	If a QSE has not  submitted a valid COP for any Generation Resource for any hour in the DAM or RUC Study Period, then the Generation Resource is considered to have a Resource Status as OUT thus not available for DAM awards or RUC commitments for those hours.

(11)	If a COP is not available for any Resource for any hour from the current hour to the start  of the DAM period or RUC study, then the Resource Status for those hours are considered equal to the last known Resource Status from a previous hour’s COP or from telemetry as appropriate for that Resource.

3.9.2	Current Operating Plan Validation

(1)	ERCOT shall verify that each COP, on its submission, complies with the criteria described in Section 3.9.1, Current Operating Plan (COP) Criteria.  ERCOT shall notify the QSE by means of the Messaging System if the QSE’s COP fails to comply with the criteria described in Section 3.9.1 and this Section 3.9.2 for any reason.  The QSE must then resubmit the COP within the appropriate market timeline.

(2)	ERCOT may reject a COP that does not meet the criteria described in Section 3.9.1.

(3)	If a Resource is designated in the COP to provide Ancillary Service, then ERCOT shall verify that the COP complies with Section 3.16, Standards for Determining Ancillary Service Quantities.  The Ancillary Service Supply Responsibilities as indicated in the Ancillary Service Resource Responsibility submitted immediately before the end of the Adjustment Period are physically binding commitments for each QSE for the corresponding Operating Period.

(4)	ERCOT shall notify the QSE if the sum of the Ancillary Service capacity designated in the COP for each hour, by service type, is less than the QSE’s Ancillary Service Supply Responsibility for each service type for that hour.  If the QSE does not correct the deficiency within one hour after receiving the notice from ERCOT, then ERCOT shall follow the procedures outlined in Section 6.4.8.1, Evaluation and Maintenance of Ancillary Service Capacity Sufficiency.

(5)	A QSE may change Ancillary Service Resource designations by changing its COP, subject to Section 6.4.8.1.

(6)	If ERCOT determines that it needs more Ancillary Service during the Adjustment Period, then the QSE’s allocated portion of the additional Ancillary Service may be self-arranged.

(7)	ERCOT systems must be able to detect a change in status of a Resource shown in the COP and must provide notice to ERCOT operators of changes that a QSE makes to its COP.

(8)	A QSE representing a Resource that has an Energy Offer Curve valid for an hour of the COP may not designate a Resource Status of ONOS or ONDSR for that hour for that Resource.

3.10	Network Operations Modeling and Telemetry

(1)	ERCOT shall use the physical characteristics, ratings, and operational limits of all Transmission Elements of the ERCOT Transmission Grid and other information from the Transmission Service Providers (TSPs) and Resource Entities to specify limits within which the transmission network is defined in the network models made available to Market Participants as noted below and used to operate the ERCOT Transmission Grid as updated.  If a Private Use Network is not registered as a Resource Entity, then ERCOT shall use equivalent model data provided by TSPs, if available, that represents the Private Use Network in the TSPs’ modeling systems for use in the Network Operations Model.

(2)	Because the ERCOT market requires accurate modeling of Transmission Elements in order to send accurate Base Points and pricing signals to Market Participants, ERCOT shall manage the Network Operations Model.  By providing Base Points and pricing signals by Electrical Bus to Market Participants, the Market Participants’ responses result in power flows on all Transmission Elements that ERCOT must monitor and, if necessary for reliability reasons, manage within ratings provided by the TSP and Resource Entity and limits assigned by ERCOT including Generic Transmission Limits (GTLs) as may be defined in Section 3.10.7.6, Modeling of Generic Transmission Limits.

(3)	TSPs and Resource Entities shall provide ERCOT with equipment ratings and update the ratings as required by ERCOT.  ERCOT may request TSPs and Resource Entities to provide detailed information on the methodology, including data for determination of each requested rating.  ERCOT may review and comment on the methodology.  ERCOT shall post all methodologies on the Market Information System (MIS) Secure Area within seven days following a change in methodology.

(4)	ERCOT must use system ratings consistent with the ratings expected to be used during Real-Time for the system condition being modeled, including Dynamic Ratings using expected temperatures for those system conditions.  For each model, ERCOT shall post ratings and the ambient temperatures used to calculate the ratings on the MIS Secure Area when the model is published.

(5)	ERCOT shall use consistent information within and between the various models used by ERCOT Operations, ERCOT Planning, and other workgroups in a manner that yields consistent results.  For operational and planning models that are intended to represent the same system state the results should be consistent and the naming should be identical.  An independent audit must be performed at least annually to confirm that consistent information is used in all ERCOT Operations models.

(6)	ERCOT shall use a Network Operations Model Change Request (NOMCR) process to control all information entering the Network Operations Model.  In order to allow for construction schedules, each NOMCR must be packaged as a single package describing any incremental changes and referencing any prerequisite NOMCRs, using an industry standard data exchange format.  A package must contain a series of instructions that define the changes that need to be made to implement a network model change.  ERCOT shall verify each package for completeness and accuracy prior to the period it is to be implemented.

(7)	ERCOT shall use an automated process to manage the Common Information Model (CIM) compliant packages loaded into the Network Operations Model as each construction phase is completed.  ERCOT shall reject any NOMCRs that are not CIM compliant.  Each CIM compliant NOMCR must also be associated with commands to update the graphical displays associated with the network model modification.  During the testing phase, each NOMCR must be tested for proper sequencing and its effects on downstream applications.

(8)	ERCOT shall track each data submittal received from TSPs and Resource Entities via the NOMCR process, or in the case of Resources, the prescribed Resource asset registration process which is converted by ERCOT to the appropriate NOMCR format, through implementation and final testing of the change.  ERCOT shall notify each TSP and Resource Entity when the requested change is processed and implemented in accordance with Section 3.10.1, Time Line for Network Operations Model Changes, and ERCOT shall also provide the submitting TSP a link to a Network Operations Model containing the change for verifying the implementation of the NOMCR and associated one-line displays.  ERCOT shall post all NOMCRs on the MIS Certified Area for TSPs only within five Business Days following receipt of the NOMCR, consistent with Critical Energy Infrastructure Information (CEII) standards.  When posting a NOMCR, each change must be posted using the CIM data exchange format showing incremental changes to the last Network Operations Model for TSPs only, to facilitate TSPs in updating their internal network models to reflect changes made at ERCOT.  For each NOMCR, ERCOT shall post on the MIS Certified Area for TSPs only the current status on the in-service date for each NOMCR, including any prerequisite NOMCRs provided by the requestor.

(9)	ERCOT shall update the Network Operations Model under this Section and coordinate it with the planning models for consistency to the extent applicable.

(10)	Any requestor of any changes in system topology or telemetry must receive approval from ERCOT before connecting of any associated equipment to the ERCOT Transmission Grid.  ERCOT shall notify a requestor of any deficiencies in its submittal for changes in system topology or telemetry.  ERCOT shall accept corrections to the submittal if the requestor has corrected any deficiencies by the required submittal date specified in Section 3.10.1.  ERCOT shall post any changes to an NOMCR on the MIS Certified Area for TSPs within three Business Days of accepting corrections.

(11)	On receipt of the information set forth in Section 3.10.7, ERCOT System Modeling Requirements, ERCOT shall review the information and notify the requestor of any required modifications.  ERCOT may, at its discretion, require changes or more details regarding the work plan for any new or relocated facilities.  The requestor shall notify ERCOT and any other affected Entities as soon as practicable of any ERCOT requested changes to the work plan.  The requestor shall consult with other Entities likely to be affected and shall revise the work plan, following any necessary or appropriate discussions with ERCOT and other affected Entities.  ERCOT shall approve or reject the request, including any revisions made by the requestor, within 15 days of receipt of the complete request and any revisions.  Following ERCOT approval, ERCOT shall publish a summary of the revised NOMCR on the MIS Certified Area for TSPs.

3.10.1	Time Line for Network Operations Model Changes

(1)	ERCOT shall perform periodic updates to the Network Operations Model.  Market Participants may provide Network Operations Model updates to ERCOT to implement planned transmission and Resource construction one year before the required submittal date below.  TSPs and Resource Entities must timely submit Network Operations Model changes pursuant to the schedule in this Section to be included in the updates.

(2)	For a facility addition, revision, or deletion to be included in any Network Operations Model update, all technical modeling information must be submitted to ERCOT pursuant to the ERCOT NOMCR process or the applicable Resource asset registration process for Resource Entities.

(3)	TSPs and Resource Entities shall submit Network Operations Model updates at least three months prior to the physical equipment change.  ERCOT shall update the Network Operations Model according to the following table:

| Deadline to Submit Information to ERCOT Note 1 | Model Complete and Available for Test Note 2 | Updated Network Operations Model Testing Complete Note 3 Paragraph (5) | Update Network Operations Model Production Environment | Target Physical Equipment included in Production Model Note 4 |
| --- | --- | --- | --- | --- |
| Jan 1 | Feb 15 | March 15 | April 1 | Month of April |
| Feb 1 | March 15 | April 15 | May 1 | Month of May |
| March 1 | April 15 | May 15 | June 1 | Month of June |
| April 1 | May 15 | June 15 | July 1 | Month of July |
| May 1 | June 15 | July 15 | August 1 | Month of August |
| June 1 | July 15 | August 15 | September 1 | Month of September |
| July 1 | August 15 | September 15 | October 1 | Month of October |
| August 1 | September 15 | October 15 | November 1 | Month of November |
| September 1 | October 15 | November 15 | December 1 | Month of December |
| October 1 | November 15 | December 15 | January 1 | Month of January (the next year) |
| November 1 | December 15 | January 15 | February 1 | Month of February (the next year) |
| December 1 | January 15 | February 15 | March 1 | Month of March (the next year) |

Notes:

1.	TSP and Resource Entity data submissions complete per the NOMCR process or other ERCOT-prescribed process applicable to Resource Entities for inclusion in next update period.

2.	Network Operations Model data changes and preliminary fidelity test complete by using the Network Operations Model test facility described in paragraph (3) of Section 3.10.4, ERCOT Responsibilities.  A test version of the Redacted Network Operations Model will be posted to the MIS Secure Area for Market Participants and Network Operations Model to the MIS Certified Area for TSPs as described in paragraph (8) of Section 3.10.4, for market review and further testing by Market Participants.

3.	Testing of the Redacted Network Operations Model by Market Participants and Network Operations Model by TSPs is complete and ERCOT begins the Energy Management System (EMS) testing prior to placing the new model into the production environment.

4.	Updates include changes starting at this date and ending within the same month.  The schedule for Operations Model load dates will be published by ERCOT on the MIS Public Area.

(4)	ERCOT shall only approve energization requests when the Transmission Element is satisfactorily modeled in the Network Operations Model.

(5)	Changes to an existing NOMCR that modify only Inter-Control Center Communications Protocol (ICCP) data object names shall be provided 15 days prior to the Network Operations Model load date.  NOMCR modifications containing only ICCP data object names shall not be subject to interim update reporting to the Independent Market Monitor (IMM) and Public Utility Commission of Texas (PUCT) (reference paragraph (5) of Section 3.10.4), according to the following:

| NOMCR that contains ICCP Data and is submitted … | ERCOT shall … | Subject to IMM & PUC Reporting |
| --- | --- | --- |
| Beyond 90 days of the energization date | Allow modification of only ICCP data for an existing NOMCR | No |
| Between 90 and 15 days prior to the scheduled database load. | Allow modification of only ICCP data for an existing NOMCR | No |
| Less than 15 days before scheduled database load. | Require a new NOMCR to be submitted containing the ICCP data | Yes |

3.10.2	Annual Planning Model

(1)	For each of the next five years, ERCOT shall develop models for annual planning purposes that contain, as much as practicable, information consistent with the Network Operations Model.  The “Annual Planning Model” for each of the next five years is a model of the ERCOT power system (created, approved, posted, and updated regularly by ERCOT) as it is expected to operate during peak Load conditions for the corresponding future year.

(2)	ERCOT shall perform updates to the ERCOT Annual Planning Models for each of the next five years as follows:

(a)	Annual Planning Model updates are due September 1st; and

(b)	Annual Planning Models are released October 15th.

(3)	ERCOT shall make available to TSPs and/or Distribution Service Provider (DSPs) and all appropriate Market Participants, consistent with applicable policies regarding release of CEII, the transmission model used in transmission planning.  ERCOT shall provide model information through the use of the Electric Power Research Institute (EPRI) and North American Electric Reliability Corporation (NERC) sponsored CIM and web-based Extensible Markup Language (XML) communications or Power System Simulator for Engineering (PSS/E) format.

(4)	ERCOT shall establish a detailed submittal schedule for updating transmission information.  ERCOT shall post such information and the model on the MIS Secure Area.

(5)	ERCOT shall coordinate updates to the Annual Planning Model with the Network Operations Model to ensure consistency of data within and between the Annual Planning Model and Network Operations Model to the extent practicable.

3.10.3	CRR Network Model

(1)	ERCOT shall develop models for CRR Auctions that contain, as much as practicable, information consistent with the Network Operations Model.  Names of Transmission Elements in the Network Operations Model and the CRR Network Model must be identical for the same physical equipment.

(2)	ERCOT shall verify that the names of Hub Buses and Electrical Buses used to describe the same device in any Hub are identically named in both the Network Operations Model and the CRR Network Model.

(3)	Each CRR Network Model must include:

(a)	A complete one-line diagram with all Settlement Points (indicating the Settlement Point that the Electrical Bus is a part of) and including all Hub Buses used to calculate Hub prices (if applicable);

(b)	Generation Resource locations;

(c)	Transmission Elements;

(d)	Transmission impedances;

(e)	Transmission ratings;

(f)	Contingency lists;

(g)	Data inputs used in the calculation of Dynamic Ratings, and

(h)	Other relevant assumptions and inputs used for the CRR Network Model.

(4)	ERCOT shall make available to TSPs and/or DSPs and all appropriate Market Participants, consistent with applicable policies regarding release of CEII, the CRR Network Model.  ERCOT shall provide model information through the use of the EPRI and NERC-sponsored CIM and web based XML communications or PSS/E format.

3.10.4	ERCOT Responsibilities

(1)	ERCOT shall design, install, operate, and maintain its systems and establish applicable related processes to meet the Technical Advisory Committee (TAC) approved State Estimator (SE) performance standard for Transmission Elements that under typical system conditions potentially affect the calculation of Locational Marginal Prices (LMPs) as described in Section 3.10.7.5, Telemetry Criteria, and Section 3.10.9, State Estimator Performance Standard.  ERCOT shall post all documents relating to the State Estimator Performance Standard on the MIS Secure Area.

(2)	During Real-Time, ERCOT shall calculate LMPs and take remedial actions to ensure that actual flow on a given Transmission Element is less than the Normal Rating and any calculated flow due to a contingency is less than the applicable Emergency Rating and 15-Minute Rating.

(3)	ERCOT shall install Network Operations Model test facilities that will accommodate execution of a test Real-Time sequence and preliminary test LMP calculator to demonstrate the correct operation of new Network Operations Models prior to releasing the model to Market Participants for detail testing and verification.  The Network Operations Model test facilities support power flow and contingency analyses to test the data set representation of a proposed transmission model update and simulate LMP calculations using typical test data.

(4)	ERCOT shall install EMS test and simulation facilities that accommodate execution of the SE and LMP calculator, respectively.  These facilities will be used to conduct tests prior to placing a new model into ERCOT’s production environment to verify the new model’s accuracy.  The EMS test facilities allow a potential model to be tested before replacing the current production environment model.  The EMS test and simulation facilities must perform Real-Time security analysis to test a proposed transmission model before replacing the current production environment model. The EMS SE test facilities must have Real-Time ICCP links to test the state estimation function using actual Real-Time conditions.  The EMS LMP test facilities must accept data uploads from the production environment providing Qualified Scheduling Entity (QSE) Resource offers, and telemetry via ICCP.  If the production data are unavailable, ERCOT may employ a data simulation tool or process to develop test data sets for the LMP test facilities.  For TSPs, ERCOT shall acquire model comparison software that will show all differences between subsequent versions of the Network Operations Model and shall make this information available to TSPs only within one week following test completion.  For non-TSP Market Participants, ERCOT shall post the differences within one week following test completion between subsequent versions of the Redacted Network Operations Model on the MIS Secure Area.  This comparison shall indicate differences in device parameters, missing or new devices, and status changes.

(5)	When implementing Transmission Element changes, ERCOT shall correct errors uncovered during testing that are due to submission of inaccurate information.  Each TSP and Resource Entity shall provide reasonably accurate information at the time of the original submission.

(6)	ERCOT may update the model on an interim basis, outside of the timeline described in Section 3.10.1, Time Line for Network Operations Model Changes, for the correction of temporary configuration changes in a system restoration situation, such as after a storm, or correction of impedances and ratings.

(7)	Interim updates to the Network Operations Model caused by unintentional inconsistencies of the model with the physical transmission grid may be made.  If an interim update is implemented, ERCOT shall report changes to the PUCT Staff and the IMM.  ERCOT shall provide Notice via electronic means to all Market Participants and post the Notice on the MIS Secure Area detailing the changed model information and the reason for the interim update within two Business Days following the report to PUCT Staff and the IMM.

(8)	When ERCOT identifies active or binding transmission constraints on a repeated basis, ERCOT shall contact the appropriate TSP and Resource Entity to:

(a)	Verify that ratings of Transmission Facilities in the Network Operations Model and in the Updated Network Model causing the event are current and correctly represented;

(b)	Verify, when the TSP’s and Resource Entity’s analysis results differ from those of ERCOT, that the configuration of the transmission grid in the Network Operations Model and in the Updated Network Model matches that in use by the TSP and Resource Entity.  To recognize operational time constraints, that verification must focus on Transmission Elements believed to have affected the event; and

(c)	Mutually identify with the TSP and Resource Entity any additional operational intervention or system monitoring that could be implemented to manage recurring congestion due to a recurring cause.

(9)	A TSP and Resource Entity, with ERCOT’s assistance, shall validate its portion of the Network Operations Model according to the timeline provided in Section 3.10.1.  ERCOT shall provide TSPs access, consistent with applicable policies regarding release of CEII, to an environment of the ERCOT EMS where the Network Operations Model and the results of the Real-Time SE are available for review and analysis within five minutes of the Real-Time solution.  This environment is provided as a tool to TSPs to perform power flow studies, contingency analyses and validation of SE results.

(10)	ERCOT shall make available to TSPs, consistent with applicable policies regarding release of CEII, the Network Operations Model used to manage the reliability of the transmission system as well as proposed Network Operations Models to be implemented at a future date.  ERCOT shall post on the MIS Secure Area the Redacted Network Operations Model, consistent with applicable policies regarding release of CEII as well as proposed Redacted Network Operations Models to be implemented at a future date.  ERCOT shall provide model information through the use of the EPRI and NERC-sponsored CIM and web-based XML communications.

3.10.5	TSP Responsibilities

(1)	Each TSP shall design, implement, operate, and maintain its systems to meet the TAC-approved ERCOT telemetry criteria under Section 3.10.7.5, Telemetry Criteria, for measurements facilitating the observability of the Electrical Buses used for Security-Constrained Economic Dispatch (SCED).  However, there is no obligation to re-construct or retrofit already existing installations except as shown to be needed in order to achieve TAC-approved observability criteria and SE performance standard.

(2)	TSPs shall add telemetry at ERCOT’s request to maintain observability and redundancy requirements as specified herein, and under Section 3.10.7.5.  ERCOT shall request such additions when a lack of data telemetry has caused, or can be demonstrated to result in, inaccuracies between Real-Time measurements and modeling outcomes that could result in incorrect LMP prices or potential reliability problems.

(3)	Each TSP shall provide to ERCOT planned construction information, including Certificate of Convenience and Necessity (CCN) application milestone dates if applicable, all of which shall be updated quarterly according to a schedule established by ERCOT.

(4)	Each TSP shall provide to ERCOT project status updates of Transmission Facilities that are part of an Reliability Must-Run (RMR) or Must Run Alternative (MRA) exit strategy corresponding to a specific RMR or MRA Agreement that has not been terminated, which shall be updated by the first Business Day of each month, noting any acceleration or delay in planned completion date.

3.10.6	Resource Entity Responsibilities

(1)	QSEs and Resource Entities shall provide ERCOT and TSPs with information describing each Generation Resource and Load Resource that it represents under Section 3.10.7.2, Modeling of Resources and Transmission Loads.

(2)	Resource Entities will provide information on step-up transformers to TSPs under Section 3.10.7.1.4, Transmission and Generation Resource Step-Up Transformers.

3.10.7	ERCOT System Modeling Requirements

The following subsections contain the fidelity requirements for the ERCOT Network Operations Model.

3.10.7.1	Modeling of Transmission Elements and Parameters

(1)	ERCOT, each TSP, and each Resource Entity shall coordinate to define each Transmission Element such that the TSP’s control center operational model and ERCOT’s Network Operations Model are consistent.

(2)	Each Transmission Element must have a unique identifier using a consistent naming convention used between ERCOT and TSPs.  ERCOT shall develop the naming convention with the assistance of the TSP and the approval of TAC.  In addition to the Network Operations Model releases described in Section 3.10.1, Time Line for Network Operations Model Change Requests, ERCOT shall provide all names and parameters of all Transmission Elements to Market Participants posted on MIS Secure Area by 0600 each day.

(3)	If the responsible TSP submits a NOMCR for non-operational changes, such as name changes for Transmission Elements, ERCOT shall implement the request.

3.10.7.1.1	Transmission Lines

(1)	ERCOT shall model each transmission line that operates in excess of 60 kV.

(2)	For each of its transmission lines operated as part of the ERCOT Transmission Grid, each TSP and if applicable, Resource Entity, shall provide ERCOT with the following information consistent with the ratings methodology prescribed in the ERCOT Operating Guides:

(a)	Equipment owner(s);

(b)	Equipment operator(s);

(c)	Transmission Element name;

(d)	Line impedance;

(e)	Normal Rating, Emergency Rating, 15-Minute Rating, and Conductor/Transformer 2-Hour Rating; and

(f)	Other data necessary to model Transmission Element(s).

(3)	The TSP and Resource Entity may submit special transfer limits and stability limits for secure and reliable grid operations for ERCOT approval.  ERCOT has sole decision-making authority and responsibility to determine the limits to be applied in grid operations.

(4)	The TSP and Resource Entity may implement protective relay and control systems and set values appropriate to de-energize faulted equipment and meet the TSP and Resource Entity obligations for public or employee safety, and when necessary to prevent in-service or premature equipment failure consistent with Good Utility Practice and accepted industry standards.  The TSP and Resource Entity shall include those limits when providing ERCOT with ratings or proposed transfer limits.

(5)	The Network Operations Model must use rating categories for Transmission Elements as defined in the ERCOT Operating Guides.

3.10.7.1.2	Transmission Buses

(1)	ERCOT shall model each Electrical Bus that operates as part of the ERCOT Transmission Grid in excess of 60 kV and that is required to model switching stations or transmission Loads.

(2)	Each TSP and if applicable, Resource Entity, shall provide ERCOT with the following information, subject to the naming conventions in Section 3.10.7.1, Modeling of Transmission Elements and Parameters:

(a)	Equipment owner(s);

(b)	Equipment operator(s);

(c)	The Transmission Element name;

(d)	The substation name;

(e)	A description of all transmission circuits that may be connected through breakers or switches; and

(f)	Other data necessary to model Transmission Element(s).

(3)	To accommodate the Outage Scheduler, the TSP and Resource Entity may define a separate name and Transmission Element for any Electrical Bus that can be physically separated by a manual switch or breaker within a substation.

3.10.7.1.3	Transmission Breakers and Switches

(1)	ERCOT’s Network Operations Model must include all transmission breakers and switches, the operation of which may cause a change in the flow on transmission lines or Electrical Buses.  Breakers and switches may only be connected to defined Electrical Buses.

(2)	Each TSP and Resource Entity shall provide ERCOT with the following information, subject to the naming conventions in Section 3.10.7.1, Modeling of Transmission Elements and Parameters:

(a)	Equipment owner(s);

(b)	Equipment operator(s);

(c)	The Transmission Element name;

(d)	The substation name;

(e)	Connectivity;

(f)	Normal status; and

(g)	Other data necessary to model Transmission Element(s).

(3)	ERCOT shall develop methods to accurately model changes in transmission line loading resulting from Load rollover schemes transferring more than ten MW.  This may include modeling distribution circuit breakers, dead line sensing, or other methods that signal when the Load should be transferred from one transmission line to another transmission line.  ERCOT may employ heuristic rule sets for all manual Load transfers and for automated transfers where feasible.  ERCOT application software is required to model the effects of automatic or manual schemes in the field transfer Load under line outage conditions.  Each TSP and as applicable, Resource Entity, shall define the Load rollover schemes under Section 3.10.7.2, Modeling of Resources and Transmission Loads, and furnish this information to ERCOT.  Transmission field (right-of-way) switches must be connected to a named Electrical Bus and be included in the Network Operations Model.

3.10.7.1.4	Transmission and Generation Resource Step-Up Transformers

(1)	ERCOT shall model all transformers with a nominal low side (i.e., secondary, not tertiary) voltage above 60 kV.

(2)	ERCOT shall model all Generation Resource step-up transformers greater than ten MVA to provide for accurate representation of generator voltage control capability including the capability to accept a system operator entry of a specific no-load tap position, or if changeable under Load, accept telemetry of the current tap position.

(3)	Each TSP and Resource Entity shall provide ERCOT with information to accurately describe each transformer in the Network Operations Model including any tertiary Load as required by ERCOT.  Each TSP and Resource Entity shall provide ERCOT with the following information, subject to the naming conventions in Section 3.10.7.1, Modeling of Transmission Elements and Parameters:

(a)	Equipment owner(s);

(b)	Equipment operator(s);

(c)	The Transmission Element name;

(d)	The substation name;

(e)	Winding ratings;

(f)	Connectivity;

(g)	Transformer parameters, including all tap parameters; and

(h)	Other data necessary to model Transmission Element(s).

(4)	The Generation Entity shall provide parameters for each step-up transformer to ERCOT, which shall provide the information to TSPs.  Each TSP shall coordinate with the operators of the Resources connected to their respective systems to establish the proper transformer tap positions (no-load taps) and report any changes to ERCOT using the NOMCR process or other ERCOT prescribed means.  Each Generation Entity and each TSP shall schedule generation Outages at mutually agreeable times to implement tap position changes when necessary.  If mutual agreement cannot be reached, then ERCOT shall decide where to set the tap position to be implemented by the Generation Entity at the next generation Outage, considering expected impact on system security, future Outage plans, and participants.  TSPs shall provide ERCOT and Market Participants with notice in accordance with paragraph (4) of 3.10.4, ERCOT Responsibilities, paragraph (4) (except for emergency) prior to the tap position change implementation date.

(5)	ERCOT shall post to the MIS Secure Area information regarding all transformers represented in the Network Operations Model.

3.10.7.1.5	Reactors, Capacitors, and other Reactive Controlled Sources

(1)	ERCOT shall model all controlled reactive devices.  Each Market Participant shall provide ERCOT with complete information on each device’s capabilities and normal switching schema.

(2)	Each Market Participant shall provide ERCOT with the following information, subject to the naming conventions in Section 3.10.7.1, Modeling of Transmission Elements and Parameters:

(a)	Equipment owner(s);

(b)	Equipment operator(s);

(c)	The Transmission Element name;

(d)	The substation name;

(e)	Voltage or time switched on;

(f)	Voltage or time switched off;

(g)	Associated switching device name;

(h)	Connectivity;

(i)	Nominal voltage and associated capacitance or reactance; and

(j)	Other data necessary to model Transmission Element(s).

(3)	The ERCOT Operating Guides must include parameters for standard reactor and capacitor switching plans for use in the Network Operations Model.  ERCOT shall model the devices under Section 3.10.4, ERCOT Responsibilities, in all applicable ERCOT applications and systems.  ERCOT shall provide copies of the switching plan to the Market Participants via the MIS Secure Area.  Any change in TSP guidelines or switching plan must be provided to ERCOT before implementation (except for emergency).  Any change in guidelines or switching plan must be provided in accordance with the NOMCR process or other ERCOT-prescribed process.

3.10.7.2	Modeling of Resources and Transmission Loads

(1)	Each Resource Entity shall provide ERCOT and TSPs with information describing each of its Generation Resources and Load Resources connected to the transmission system.  All Resources greater than ten MW, Generation Resources less than ten MW but providing Ancillary Service, Split Generation Resources where the physical generator being split is greater than ten MW, Private Use Networks containing Resources greater than ten MW, Wind-powered Generation Resources (WGRs) or Aggregated Generation Resources (AGRs) with an aggregate interconnection to the ERCOT System greater than ten MW, Direct Current Tie (DC Tie) Resources, and the non-TSP owned step-up transformers greater than ten MVA, must be modeled to provide equivalent generation injections to the ERCOT Transmission Grid.  ERCOT shall coordinate the modeling of Generation Resources, Private Use Networks, DC Tie Resources and Load Resources with their owners to ensure consistency between TSP models and ERCOT models.

(2)	Each Resource Entity representing a Split Generation Resource shall provide information to ERCOT and TSPs describing an individual Split Generation Resource for its share of the generation facility to be represented in the Network Operations Model in accordance with Section 3.8, Special Considerations for Split Generation Meters, Combined Cycle Generation Resources, Quick Start Generation Resources, and Hydro Generation Resources.  The Split Generation Resource must be modeled as connected to the ERCOT Transmission Grid on the low side of the generation facility main power transformer.

(3)	ERCOT shall create a DC Tie Resource to represent an equivalent generation injection to represent the flow into the ERCOT Transmission Grid from operation of DC Ties.  The actual injection flow on the DC Tie from telemetry provided by the facility owner(s) is the DC Tie Resource output.

(4)	TSPs shall provide ERCOT with information describing all transmission Load connections on the ERCOT Transmission Grid.  Individual Load connections may be combined, at the discretion of ERCOT, with other Load connections on the same transmission line to represent a Model Load to facilitate state estimation of Loads that do not telemeter Load measurements.  ERCOT shall define “Model Loads”, which may be one or more combined Loads, for use in its Network Operations Model.  A Model Load cannot be used to represent Load connections that are in different Load Zones.

(5)	ERCOT may require TSPs to provide additional Load telemetry to provide adequate modeling of the transmission system in accordance with Section 3.10.7.5, Telemetry Criteria.  When the TSP does not own the station for which additional Load telemetry is being requested, the TSP shall request that the owner make the telemetry available.  The TSP shall notify ERCOT if the owner does not comply with the request.

(6)	ERCOT shall create a DC Tie Load to represent an equivalent Load withdrawal to represent the flow from the ERCOT Transmission Grid from operation of DC Ties.  The actual withdrawal flow on the DC Tie from telemetry provided by the facility owner(s) is the DC Tie Load output.

(7)	Each TSP shall also provide information to ERCOT describing automatic Load transfer (rollover) plans and the events that trigger which Loads are switched to other Transmission Elements on detection of Outage of a primary Transmission Element.  ERCOT shall accommodate Load rollover plans in the Network Operations Model

(8)	Loads associated with a Generation Resource in a common switchyard as defined in Section 10.3.2.3, Generation Netting for ERCOT-Polled Settlement Meters, and served through a transformer owned by the Generation Entity is treated as an auxiliary Load and must be netted first against any generation meeting the requirements under Section 10.3.2.3.

3.10.7.3	Modeling of Private Use Networks

ERCOT shall create and use network models describing Private Use Networks according to the following:

(1)	A Generation Entity with a Resource located within a Private Use Network shall provide data to ERCOT, for use in the Network Operations Model, for each of its individual generating unit(s) located within the Private Use Network in accordance with Section 3.3.2.1, Information to Be Provided to ERCOT, if it meets any one of the following criteria:

(a)	Contains a generator greater than ten MW and is registered with the PUCT according to P.U.C. Subst. R. 25.109, Registration of Power Generation Companies and Self-Generators, as a power generation company; or

(b)	Is part of a Private Use Network which contains more than one connection to the ERCOT Transmission Grid; or

(c)	Contains generation registered to provide Ancillary Services.

(2)	A Generation Entity with a generator greater than ten MW located within a Private Use Network which does not meet any of the criteria of item (1) above shall provide to ERCOT annually, or more often upon change, the following information for ERCOT’s use in the Network Operations Model, for each of its individual generating unit(s) located within the Private Use Network:

(a)	Equipment owner(s);

(b)	Equipment operator(s);

(c)	TSP substation name connecting the Private Use Network to the ERCOT System;

(d)	At the request of ERCOT, a description of Transmission Elements within the Private Use Network that may be connected through breakers or switches;

(e)	Net energy delivery metering, as required by ERCOT, to and from a the Private Use Network and the ERCOT System at the Point of Interconnection (POI) with the TSP;

(f)	For each individual generator located within the Private Use Network, the gross capacity in MW and its reactive capability curve;

(g)	Maximum and minimum reasonability limits of the Load located within the Private Use Network;

(h)	Outage schedule for each generation unit located within the Private Use Network, updated as changes occur from the annually submitted information; and

(i)	Other interconnection data as required by ERCOT.

(3)	Energy delivered to ERCOT from a non-modeled generator shall be settled in accordance with Section 6.6.3.2, Real-Time Energy Imbalance Payment or Charge at a Load Zone.

(4)	ERCOT shall ensure the Network Operations Model properly models the physical effect of the loss of generators and Transmission Elements on the ERCOT Transmission Grid equipment loading, voltage, and stability.

(5)	ERCOT may require the owner or operator of a Private Use Network to provide information to ERCOT and the TSP on Transmission Facilities located within the Private Use Network for use in the Network Operations Model if the information is required to adequately model and determine the security of the ERCOT Transmission Grid, including data to perform loop flow analysis of Private Use Networks.

(6)	ERCOT shall review submittals of modeling data from owners or operators of Private Use Networks assure that it will result in correct analysis of ERCOT Transmission Grid security.

3.10.7.4	Definition of Special Protection Systems and Remedial Action Plans

(1)	All Special Protection Systems (SPSs) and Remedial Action Plans (RAPs) used by ERCOT and the TSPs to maintain a secure system must be defined in the Network Operations Model.

(2)	Proposed new SPSs and RAPs and proposed changes to SPSs and RAPs must be submitted to ERCOT for review and approval by ERCOT and all directly affected TSPs and Resource Entities under the applicable procedures in the Operating Guides.  Once a new or changed SPS or RAP is approved by ERCOT and all directly affected TSPs and Resource Entities, the TSP shall submit the approved SPS or RAP to ERCOT using an NOMCR.  The NOMCR must include a detailed description of the system conditions required to implement the SPS or RAP.  Execution of an SPS or RAP must be included or assumed in the calculation of LMPs as well as the Network Operations Model.   ERCOT shall post all SPSs and RAPs under consideration on the MIS Secure Area within five Business Days of receipt by ERCOT.

(3)	ERCOT shall model, and include in the security analysis, approved SPSs and RAPs. ERCOT shall post on the MIS Secure Area all approved SPSs and RAPs at least two Business Days before implementation, identifying the date of implementation.

3.10.7.5	Telemetry Criteria

(1)	The appropriate TAC subcommittee shall establish a task force that is open to Market Participants, comprised of technical experts, to develop a set of Telemetry Criteria consistent with the minimum requirements of the Protocols.  TAC shall approve a set of telemetry criteria and the appropriate TAC subcommittee shall update the telemetry criteria annually each October or more often on a periodic basis as deemed necessary.

(2)	The telemetry criteria must define the performance and observability requirements of voltage and power flow measurements, including requirements for redundancy of telemetry measurement data, necessary to support the SE in meeting the approved performance standard, and to support TAC-approved accuracy standards for the calculation of LMPs.

(3)	The telemetry provided to ERCOT by each TSP must be updated at a ten second or less scan rate and be provided to ERCOT at the same rate.  Each TSP and QSE shall install appropriate condition detection capability to notify ERCOT of potentially incorrect data from loss of communication or scan function.  Condition codes must accompany the data to indicate its quality and whether the data has been measured within the scan rate requirement.  Also, ERCOT shall analyze data received for possible loss of updates.  Similarly, ERCOT shall provide condition detection capability on loss of telemetry links with the TSP and QSE.  ERCOT shall represent data condition codes from each TSP and QSE in a consistent manner for all applicable ERCOT applications.

(4)	Each TSP and QSE shall use fully redundant data communication links (ICCP) between its control center systems and ERCOT systems such that any single element of the communication system can fail and:

(a)	For server failures, complete information must be re-established within five minutes by automatic failover to alternate server(s); and

(b)	For all other failures, complete information must continue to flow between the TSP’s, QSE’s, and ERCOT’s control centers with updates of all data continuing at a 30 second or less scan rate.

(5)	When ERCOT identifies a reliability concern, a deficiency in system observability, or a deficiency in measurement to support the representation of Model Loads, and that concern or deficiency is not due to any inadequacy of the SE program, ERCOT may request that a TSP or QSE provide additional telemetry measurements, beyond those required by the telemetry criteria, in a reasonable time frame for providing such measurements.  Such requests must be submitted to the TSP or QSE with a written justification for the additional telemetry measurements.  Such written justification must include documentation of the deficiency in system observability or representation of Model Loads.  In making the determination to request additional telemetry measurements, ERCOT shall consider the economic implications of inaccurate representation of Load models in LMP results versus the cost to remedy.

(6)	Within 30 days of submittal by ERCOT to the designated contact of a TSP or QSE with a written request justifying additional telemetry measurements, the TSP or QSE shall acknowledge the request and either:

(a)	Agree with the request and make reasonable effort to install new equipment providing measurements to ERCOT within the timeframe specified;

(b)	Provide ERCOT an analysis of the cost to comply with the request, so that, ERCOT can perform a cost justification with respect to the LMP market; or

(c)	If the TSP or QSE disagrees with the request, appeal that request to TAC or present an alternate solution to ERCOT for consideration.

(7)	If ERCOT rejects the alternate solution, the TSP or QSE may appeal the original request to TAC within 30 days.  If, after receiving an appeal, TAC does not resolve the appeal within 65 days, the TSP or QSE may present its appeal to the ERCOT Board.  Notwithstanding the foregoing, a TSP or QSE is not required to provide telemetry measurements from a location not owned by that TSP or QSE, if the location owner does not grant access to the TSP or QSE for the purpose of obtaining such measurements.  ERCOT shall report such cases to the IMM.

3.10.7.5.1	Continuous Telemetry of the Status of Breakers and Switches

(1)	Each TSP and QSE shall provide telemetry, as described in this subsection, to ERCOT on the status of all breakers and switches used to switch any Transmission Element or Load modeled by ERCOT.  Each TSP and QSE is not required to install telemetry on individual breakers and switches, where the telemetered status shown to ERCOT is current and free from ambiguous changes in state caused by the TSP or QSE switching operations and TSP or QSE personnel.  Each TSP or QSE shall update the status of any breaker or switch through manual entries, if necessary, to communicate the actual current state of the device to ERCOT, except if the change in state is expected to return to the prior state within one minute.  If in the sole opinion of ERCOT, the manual updates of the TSP or QSE have been unsuccessful in maintaining the accuracy required to support SE performance to a TAC-approved predefined standard as described in Section 3.10.9, State Estimator Performance Standard, ERCOT may request that the TSP or QSE install complete telemetry from the breaker or switch to the TSP or QSE, and then to ERCOT.  In making the determination to request installation of additional telemetry from a breaker or switch, ERCOT shall consider the economic implications of inaccurate representation of Model Loads in LMP results versus the cost to remedy.

(2)	ERCOT shall measure TSP or QSE performance in providing accurate data that do not include ambiguous changes in state and shall report the performance metrics on the MIS Secure Area on a monthly basis.

(3)	Unless there is an emergency condition, a TSP or QSE must obtain approval from ERCOT to purposely open a breaker or switch unless that breaker or switch is shown in a Planned Outage in the Outage Scheduler, or the device will return to its previous state within 60 minutes, or the device is a generator output circuit breaker.  Also, a TSP or QSE must obtain approval from ERCOT before closing any breaker or switch, except in response to a Forced Outage, or an emergency, or the device will return to its previous state within 60 minutes, or the device is a generator output circuit breaker.

(4)	ERCOT shall monitor the data condition codes of all breakers and switches showing loss of communication or scan function in the Network Operations Model.  When the telemetry of breakers and switches is lost, ERCOT shall use the last known state of the device for security analysis as updated by the Outage Scheduler and through verbal communication with the TSP or QSE.  ERCOT’s systems must identify probable errors in switch or breaker status and ERCOT shall act to resolve or correct such errors in a timely manner as described in Section 6, Adjustment Period and Real-Time Operations.

(5)	ERCOT shall establish a system that provides alarms to ERCOT Operators when there is a change in status of any monitored transmission breaker or switch, and an indication of whether the device change of status was planned in the Outage Scheduler.  ERCOT Operators shall monitor any changes in status not only for reliability of operations, but also for accuracy and impact on the operation of the SCED functions and subsequent potential for calculation of inaccurate LMPs.

(6)	Each QSE that represents a Split Generation Resource, with metering according to Section 3.8, Special Considerations for Split Generation Meters, shall provide ERCOT with telemetry of the actual generator breakers and switches continuously providing ERCOT with the status of the individual Split Generation Resource.

3.10.7.5.2	Continuous Telemetry of the Real-Time Measurements of Bus Load, Voltages, Tap Position, and Flows

(1)	Each TSP or QSE shall provide telemetry of voltages, flows, and Loads on any modeled Transmission Element to the extent such may be required to estimate all transmission Load withdrawals and generation injections to and from the ERCOT Transmission Grid using the SE and as needed to achieve the TAC-approved SE performance standard with consideration given to the economic implications of inaccurate LMP results versus the cost to remedy.

(2)	Each QSE that represents a Split Generation Resource, with metering according to Section 3.8, Special Considerations for Split Generation Meters, Combined Cycle Generation Resources, Quick Start Generation Resources, and Hydro Generation Resources, shall provide ERCOT with telemetry of the actual equivalent generator injection of its Split Generation Resource and the Master QSE shall provide telemetry in accordance with Section 6.5.5.2, Operational Data Requirements, on a total Generation Resource basis.  ERCOT shall calculate the sum of each QSE’s telemetry on a Split Generation Resource and compare the sum to the telemetry for the total Generation Resource.  ERCOT shall notify each QSE representing a Split Generation Resource of any errors in telemetry detected by the SE.

(3)	Each TSP shall provide telemetered measurements on modeled Transmission Elements to ensure SE observability, per TAC-approved telemetry criteria, of any monitored voltage and power flow between their associated transmission breakers to the extent such can be shown to be needed in achieving the TAC-approved SE performance standard.  On monitored non-Load substations, each TSP shall install, at the direction of ERCOT, sufficient telemetry such that there is an “N-1 Redundancy.”  An N-1 Redundancy exists if the substation remains observable on the loss of any single measurement pair (kW, kVAr) excluding station RTU communication path failures.  In making the determination to request additional telemetry, ERCOT shall consider the economic implications of inaccurate representation of Load models in LMP results versus the cost to remedy.

(4)	The accuracy of the SE is critical to successful market operations.  For this reason it is a critical objective for ERCOT to maintain reasonable and accurate results of the SE.  ERCOT shall use all reasonable efforts to achieve that objective, including the provision of legitimate constraints used in calculating LMPs.

(5)	Each TSP, QSE and ERCOT shall develop a continuously operated program to maintain telemetry of all Transmission Element measurements to provide accurate results using TAC-approved accuracy standards from the SE.  For any location where there is a connection of multiple, measured, Transmission Elements, ERCOT shall have an automated process to detect and notify ERCOT System operators if the residual sum of all telemetered measurements is more than:

(a)	Five percent of the largest line Normal Rating at the SE Bus; or

(b)	Five MW, whichever is greater.

If a location chronically fails this test, ERCOT shall notify the applicable TSP or QSE and suggest actions that the TSP or QSE could take to correct the failure.  Within 30 days, the TSP or QSE shall take the actions necessary to correct the failure or provide ERCOT with a detailed plan with a projected time frame to correct the failure.  ERCOT shall post a notice on the MIS Secure Area of any SE Buses not meeting TAC-approved accuracy requirements, including a list of all measurements and the residual errors on a monthly basis.

(6)	ERCOT shall implement a study mode version of the SE with special tools designed for troubleshooting and tuning purposes that can be used independently of any other ERCOT process that is dependent on the Real-Time SE.  ERCOT shall implement a process to recognize inaccurate SE results and shall create and implement alternative Real-Time LMP calculation processes for use when inaccurate results are detected.  ERCOT must be guided in this by TAC-approved accuracy standards.

(7)	ERCOT shall establish a system to provide overload and over/under limit alarming on all Transmission Elements monitored as constraints in the LMP models.

3.10.7.6	Modeling of Generic Transmission Limits

(1)	For the sole purpose of creating transmission flow constraints between areas of the ERCOT Transmission Grid for systems unable to recognize system stability limits and voltage limits on Electrical Buses, ERCOT may create GTLs for use in reliability and market analysis.  ERCOT shall not use GTLs for constraints in ERCOT systems capable of being directly modeled as security actions required to enforce stability and voltage limits.

(2)	Except as provided in paragraph (3) below, ERCOT shall post all GTLs on the MIS Secure Area no later than the day prior to the GTL becoming effective in any ERCOT application.  Posting of GTLs shall include the identity of all constrained transmission flows, old limits, if applicable, and new flow limits, effective date, and an explanation for each flow limit and for the change, if applicable.  ERCOT shall provide detailed information on the methodology, including data and studies used for determination of each GTL, on the MIS Secure Area.  Market Participants may review and comment on ERCOT’s methodology.  Within seven days following receipt of any comments, ERCOT shall post the comments with the subject GTL.

(3)	If an unexpected change to ERCOT System conditions requires a new GTL to manage ERCOT System reliability not posted pursuant to paragraph (2) above, ERCOT will declare a Watch and post on the MIS Secure Area the new GTL, including the detail information described above.  ERCOT shall include an explanation regarding why it did not post the limit change on the previous day.

3.10.8	Dynamic Ratings

(1)	ERCOT shall use Dynamic Ratings, where available, in the Network Operations Model and the CRR Network Models.

(2)	ERCOT shall use Dynamic Ratings in place of the Normal Rating, Emergency Rating and 15-Minute Rating as applicable as provided under paragraphs (a) or (b) below for Transmission Elements established in the Network Operations Model.

(a)	A TSP may provide Dynamic Ratings via ICCP for implementation in the next Operating Hour.  ERCOT shall use the Dynamic Ratings in its Supervisory Control and Data Acquisition (SCADA) alarming, Real Time Security Analysis, and SCED process.  In addition, the TSP shall provide ERCOT with a table of equipment rating versus temperature for use in operational planning studies.

(b)	Each TSP may alternatively elect to provide ERCOT with a table of equipment rating versus temperature and a temperature value in Real-Time for each Weather Zone in which the Transmission Element is located.  ERCOT shall apply the table of temperature and rating relationships and ERCOT’s current temperature measurements to determine the rating of each such designated piece of equipment for each Operating Hour.  ERCOT shall use the TSP-provided table in operational planning studies.

(3)	Each Operating Hour, ERCOT shall post on the MIS Secure Area updated Dynamic Ratings adjusted for the current temperature.

(4)	ERCOT may request that a TSP submit temperature-adjusted ratings on Transmission Elements that ERCOT identifies as contributing to significant congestion costs.  Each TSP shall provide the additional ratings within two months of such a request using one of the two mechanisms for supplying temperature-adjusted ratings identified above.  Ratings for Transmission Elements operated by multiple TSPs must be supplied by each TSP that has control.  ERCOT shall use the most limiting rating and report the circumstance to the IMM.

3.10.8.1	Dynamic Ratings Delivered via ICCP

(1)	The TSP shall supply the following, via ICCP, updated at least every ten minutes:

(a)	Line ID;

(b)	From station;

(c)	To station; and

(d)	Each of the three ratings: Normal Rating, Emergency Rating, and 15-Minute Rating.

(2)	ERCOT shall link each provided line rating with the ERCOT Network Operations Model and implement the ratings for the next Operating Hour.  ERCOT shall use the Dynamic Ratings in its SCADA alarming, real-time Security Analysis, and SCED process.  When the telemetry is not operational, ERCOT shall use a temperature appropriate for current conditions, and employ the required Dynamic Rating lookup table to determine the appropriate rating.

3.10.8.2	Dynamic Ratings Delivered via Static Table and Telemetered Temperature

(1)	ERCOT shall define a set of tables implementing the dynamic characteristics provided by the TSP(s) and as applicable, Resource Entity(s), of selected transmission lines, including:

(a)	Line ID;

(b)	From station;

(c)	To station;

(d)	Weather Zone(s);

(e)	TSP(s) and Resource Entity(s); and

(f)	Each of the three ratings: Normal Rating, Emergency Rating, and 15-Minute Rating.

(2)	Each TSP shall provide a current temperature for each applicable Weather Zone through SCADA telemetry.  ERCOT shall determine the appropriate rating based upon the telemetered temperature, and adjust the Normal Rating, Emergency Rating, and 15-Minute Rating within five minutes of receipt for the next Operating Hour.  ERCOT shall use the Dynamic Ratings in its SCADA alarming, real-time Security Analysis, and SCED process.

3.10.8.3	Dynamic Rating Network Operations Model Change Requests

ERCOT shall use the NOMCR process by which TSPs provide electronically to ERCOT the dynamic rating table described in Section 3.10.8.2, Dynamic Ratings Delivered via Static Table and Telemetered Temperature.

3.10.8.4	ERCOT Responsibilities Related to Dynamic Ratings

(1)	ERCOT shall provide a system to accept and implement Dynamic Ratings or temperatures to be applied to rating tables for each hour in the Day-Ahead and in the Operating Hour.  ERCOT shall also:

(a)	Provide software and processes that allow secure access for TSPs and Market Participants and that maintains a log of data provided and the actions of the TSP and ERCOT, to implement the Dynamic Ratings as described above;

(b)	Use Dynamic Ratings for alarming, compliance with ERCOT and NERC requirements, and SCED purposes in both Real-Time Operations and operational planning;

(c) 	Approve or reject the new Dynamic Rating request within 24 hours of receipt; and

(d)	Implement the approved Dynamic Rating automatically within 24 hours of approval.

(2)	ERCOT shall provide a system to implement Dynamic Ratings and to obtain monthly expected ambient air temperatures to be applied to rating tables for the CRR Network Models. Temperatures applied to the rating tables shall be determined using the same method as described in item (3) (f) of Section 7.5.5.4, Simultaneous Feasibility Test.  Transmission Elements that have Dynamic Ratings implemented in the Network Operations Model must have Dynamic Ratings in the CRR Network Models.

(3)	ERCOT shall identify additional Transmission Elements that have a high probability of providing significant added economic efficiency to the ERCOT market through Dynamic Rating and request such Dynamic Ratings from the associated TSP.  ERCOT shall post semi-annually the list of the Transmission Elements and identify if the TSP has agreed to provide the rating on the MIS Secure Area.

3.10.8.5	Transmission Service Provider Responsibilities Related to Dynamic Ratings

Each TSP shall:

(a)	Provide ERCOT with tables of ratings for different ambient temperatures for Transmission Elements, as requested by ERCOT.

(b)	Submit within two months a temperature adjusted rating table when a request is received from ERCOT unless multiple requests are made by ERCOT within the two-month period or unusual circumstances prevent the request from being accommodated in a timely fashion.  Such circumstances must be explained to ERCOT in writing and must be posted by ERCOT on the MIS Secure Area within five Business Days of receipt.

(c)	Provide Real-Time temperatures for each Weather Zone in which the TSP has existing dynamically rated transmission equipment, or alternatively provide rating updates for each temperature-adjusted line rating updated at least once every ten minutes.

3.10.9	State Estimator Performance Standard

(1)	The appropriate TAC subcommittee shall establish a task force that is open to Market Participants, comprised of technical experts to develop a State Estimator Performance Standard consistent with the minimum requirements of the Protocols.  TAC shall approve the State Estimator Performance Standards, and the appropriate TAC subcommittee shall update the State Estimator Performance Standards annually each October or more often on a periodic basis as deemed necessary.

(2)	The State Estimator Performance Standard must define the performance requirements necessary to provide State Estimator results within a TAC-defined level of confidence and results for LMP calculation that meet TAC-approved accuracy standards.  The appropriate TAC subcommittee shall coordinate with Market Participants to ensure a common understanding of the level of State Estimator performance required to enable LMP calculation that meets TAC-approved accuracy standards.  Further, the standard must address the State Estimator’s ability to detect, correct, or otherwise accommodate communications system failures, failed data points, stale data condition codes, and missing or inaccurate measurements to the extent these capabilities contribute to LMP accuracy and State Estimator performance or as needed to meet reliability requirements.

3.10.9.1	Considerations for Performance Standards

In developing the State Estimator Performance Standard recommendations to TAC, the following may be considered:

(a)	Desired confidence levels of State Estimator results.

(b)	Measurement requirements to estimate power injections and withdrawals at transmission voltage Electrical Buses defined in the SCED transmission model, which may provide for variations in criteria based on:

(i)	The number of Transmission Elements connected to a given transmission voltage Electrical Bus;

(ii)	The peak demand of the Load connected to a transmission voltage Electrical Bus;

(iii)	The total of Resource capacity connected to a transmission voltage Electrical Bus;

(iv)	The nominal transmission voltage level of a Electrical Bus;

(v)	The number of Electrical Buses with injections or withdrawals along a circuit between currently monitored transmission voltage Electrical Bus;

(vi)	Connection of Loads along a continuous, non-branching circuit that may be combined for modeling purposes;

(vii)	The quantity of Load at a Electrical Bus that may have its connection to the transmission system automatically transferred to an Electrical Bus other than the one to which it is normally connected (rollover operation);

(vii)	Electrical proximity to more than one Resource Node;

(viii)	Degree or quality of continued observability following the loss of telemetry measurements resulting from a common mode failure of telemetry-related equipment (i.e., an N-1 telemetry condition); and

(ix)	Other parameters or circumstances, as appropriate;

(c)	Sensitivity of State Estimator results with respect to variations in input parameters;

(d)	Reasonable safeguards to assure State Estimator results are calculated on a non-discriminatory basis; and

(e)	Other parameters as deemed appropriate.

3.10.9.2	Telemetry and State Estimator Performance Monitoring

ERCOT shall monitor the performance of the State Estimator, Network Security Analysis, SCED, and LMP Calculator.  ERCOT shall post a monthly report of these items on the MIS Secure Area.  ERCOT shall notify affected TSPs of any lapses of observability of the transmission system.

3.11	Transmission Planning

3.11.1	Overview

(1)	Any stakeholder, regardless if it is a Transmission Service Provider (TSP) and/or Distribution Service Provider (DSP), may develop and submit proposed projects to the Regional Planning Groups (RPGs), and review projects developed and proposed by the RPGs.  Broad participation in the process will result in a thorough development of projects.  However, confidentiality provisions prevent participation of non-TSPs and/or DSPs in the studies leading to interconnection agreements with generators until they become public.

(2)	Project endorsement through the ERCOT Regional Planning process is intended to support, to the extent applicable, a finding by the Public Utility Commission of Texas (PUCT) that a project is necessary for the service, accommodation, convenience, or safety of the public within the meaning of Public Utility Regulatory Act, Tex. Util. Code Ann. § 37.056 (Vernon 1998 and Supp. 2007) (PURA) and P.U.C. Subst. R. 25.101, Certification Criteria.

3.11.2	Planning Criteria

(1)	ERCOT and TSPs shall evaluate the need for transmission system improvements and shall evaluate the relative value of alternative improvements based on established technical and economic criteria.

(2)	The technical reliability criteria are established by the Planning Guide, Operating Guides, and the North American Electric Reliability Corporation (NERC) Reliability Standards.  ERCOT and TSPs shall strongly endeavor to meet these criteria, identify current and future violations thereof and initiate solutions necessary to ensure continual compliance.

(3)	ERCOT shall attempt to meet these reliability criteria as economically as possible and shall actively identify economic projects to meet this goal.

(4)	For economic projects, the net economic benefit of a proposed project, or set of projects, will first be assessed over the project’s life based on the net societal benefit that is reasonably expected to accrue from the project.  The project will be recommended if it is reasonably expected to result in positive net societal benefits.  If the proposed project is not expected to provide positive net societal benefits, then the net consumer benefit of the project will be assessed, and the project will be recommended if the net consumer benefits are reasonably expected to be positive.

(5)	To determine the societal benefit of a proposed project, the revenue requirement of the capital cost of the project is compared to the expected savings in system production costs resulting from the project over the expected life of the project.  Indirect benefits and costs associated with the project should be considered as well, where appropriate.  The current set of financial assumptions upon which the revenue requirement calculations is based will be posted on the Market Information System (MIS) Secure Area.  The expected production costs are based on a chronological simulation of the security-constrained unit commitment and economic dispatch of the generators connected to the ERCOT Transmission Grid to serve the expected ERCOT System Load over the planning horizon.  This market simulation is intended to provide a reasonable representation of how the ERCOT System is expected to be operated over the simulated time period.  From a practical standpoint, it is not feasible to perform this production cost simulation for the entire 30 to 40 year expected life of the project.  Therefore, the production costs are projected over the period for which a simulation is feasible and a qualitative assessment is made of whether the factors driving the production cost savings due to the project can reasonably be expected to continue.  If so, the levelized annual production cost savings over the period for which the simulation is feasible is calculated and compared to the first year annual revenue requirement of the transmission project.  If this production cost savings exceeds this annual revenue requirement for the project, the project is economic from a societal perspective and will be recommended.

(6)	For projects that do not provide sufficient societal benefit to be recommended, the net consumer benefit of the proposed project will be calculated.  Outputs from the same market simulation described in paragraph (5) above will be used to provide an estimate of the expected reduction in total system generator revenues due to the project, which is a reasonable indication in the ERCOT market of the impact on consumer costs due to the project.  Expected above-market generator revenues not included in the simulation, such as Reliability Must-Run (RMR) payments as prescribed in Section 6.6.6.2, RMR Payment for Energy, may need to be included in this evaluation.  If the levelized generator revenue reduction exceeds the first year annual revenue requirement for the project, the project is economic from the consumer benefit perspective and will be recommended.

(7)	Other indicators based on analyses of ERCOT System operations may be considered as appropriate in the determination of consumer benefits.  In order for such an alternate indicator to be considered, the costs must be reasonably expected to be on-going and be adequately quantifiable and unavoidable given the physical limitation of the transmission system.  These alternate indicators include:

(a)	Reliability Unit Commitment (RUC) Settlement for unit operations;

(b)	Visible ERCOT market indicators such as clearing prices of Congestion Revenue Rights (CRRs); and

(c)	Actual Locational Marginal Prices (LMPs) and observed congestion.

3.11.3	Regional Planning Group

ERCOT shall lead and facilitate a Regional Planning Group (RPG) to consider and review proposed projects to address transmission constraints and other ERCOT System needs.  The RPG will be a non-voting, consensus-based organization focused on identifying needs, identifying potential solutions, communicating varying viewpoints and reviewing analyses related to the ERCOT Transmission Grid in the planning horizon.  Participation in the RPG is required of all TSPs and is open to all Market Participants, consumers, other stakeholders, and PUCT Staff.

- 3.11.4	Regional Planning Group Project Review Process

3.11.4.1	Project Submission

(1)	Any stakeholder may initiate an RPG Project Review through the submission of a document describing the scope of the proposed project to ERCOT.  Projects should be submitted with sufficient lead-time to allow the RPG Project Review to be completed prior to the date on which the project must be initiated by the designated TSP.

(2)	Stakeholders may submit projects for RPG Project Review within any project Tier.  All transmission projects in Tiers 1, 2 and 3 should be submitted.  TSPs are not required to submit Tier 4 projects for RPG review, but should include any Tier 4 projects that are known in advance in the cases used for development of the Five-Year Transmission Plan.

(3)	All system improvements that are necessary for the project to achieve the system performance improvement, or to correct the system performance deficiency, for which the project is intended should be included into a single project submission.

3.11.4.2	Project Comment Process

ERCOT shall conduct a comment process which is open to the stakeholders for all proposed Tier 1, 2 and 3 projects.  The proposer of the project will have a reasonable period of time, as established by ERCOT, to answer questions and respond to comments submitted during this process.  The Planning Guide provides details of this process.

3.11.4.3	Categorization of Proposed Transmission Projects

(1)	ERCOT classifies all proposed transmission projects into one of four categories (or Tiers).  Each Tier is defined so that projects with a similar cost and impact on reliability and the ERCOT market are grouped into the same Tier.  The criteria used to classify a specific project into the appropriate Tier are described in Section 3.11.4.4, Tier 4, through Section 3.11.4.7, Tier 1, in increasing order of the level of review to which the projects within the Tier are subjected.

(2)	ERCOT may use its reasonable judgment to increase the level of review of a proposed project (e.g., from Tier 3 to Tier 2) from that which would be strictly indicated by these criteria, based on stakeholder comments, ERCOT analysis or the system impacts of the project.

(3)	Any project that would be built by an Entity that is exempt (e.g., a Municipally Owned Utility (MOU)) from getting a Certificate of Convenience and Necessity (CCN) for transmission projects but would require a CCN if it were to be built by a regulated Entity will be treated as if the project would require a CCN for the purpose of defining the Tier of the project.

3.11.4.4	Tier 4

(1)	This category consists of small system upgrades with estimated capital cost less than or equal to $15,000,000 and that do not require a CCN, as well as certain “Neutral” projects.  Neutral projects are:

(a)	The addition of or upgrades to radial transmission lines; the addition of equipment that does not affect the transfer capability of a line;

(b)	Repair and replacement-in-kind projects;

(c)	Projects that are directly associated with the interconnection of new generation; and

(d)	The addition of static reactive devices.

(2)	A project, irrespective of estimated capital cost, to serve a new Load is considered to be a Neutral project even if a CCN is required, unless such project would create a new transmission line connection between two stations (other than looping an existing line into the new Load-serving station).

3.11.4.5	Tier 3

This category consists of projects with estimated capital costs between $15,000,000 and $50,000,000 not requiring a CCN.

(a)	ERCOT shall accept a Tier 3 project if no concerns, questions or objections are provided during the project comment process;

(b)	If reasonable ERCOT or stakeholder concerns about a Tier 3 project cannot be resolved during the time period allotted by ERCOT, the project may be processed as a Tier 2 project, unless ERCOT assesses that reasonable progress is being made toward resolving these concerns; and

(c)	Projects that are required to meet an individual TSP’s Planning Criteria and that are not required by the NERC Reliability Standards or ERCOT Planning Criteria shall also be processed in this Tier, and shall be reclassified as a Tier 4 Neutral project if comments are resolved.

3.11.4.6	Tier 2

This category consists of projects with estimated capital costs less than $50,000,000 requiring a CCN.  ERCOT shall conduct an independent review of the submitted Tier 2 project to include the following:

(a)	ERCOT’s independent review shall consist of studies and analyses necessary for ERCOT to make its assessment of whether the proposed project is needed and whether the proposed project is the preferred solution to the identified system performance deficiency that the project is intended to resolve;

(b)	ERCOT shall consider all comments received during the project comment process and factor reasonable comments into its independent review of the project;

(c)	ERCOT will attempt to complete its independent review for a project in 90 days or less.  If ERCOT is unable to complete their independent review based on RPG input within 90 days, ERCOT shall provide the project submitter a reason for the delay and expected completion time;

(d)	ERCOT may, at its discretion, discuss submitted transmission projects at meetings of the RPG in order to obtain additional input into its independent review; and

(e)	ERCOT shall prepare a written report documenting the results of its independent review and recommendation on the project and shall distribute this report to the RPG.

3.11.4.7	Tier 1

(1)	This category is for all projects whose estimated capital cost is $50,000,000 or greater.  ERCOT shall conduct an independent review of the submitted Tier 1 project to include the following:

(a)	ERCOT’s independent review will consist of studies and analyses necessary for ERCOT to make its assessment of whether the proposed project is needed and whether the proposed project is the preferred solution to the identified system performance deficiency that the project is intended to resolve;

(b)	ERCOT will consider all comments received during the project comment process and factor reasonable comments into its independent review of the project;

(c)	ERCOT will attempt to complete its independent review for a project in 90 days or less.  If ERCOT is unable to complete their independent review based on RPG input within 90 days, ERCOT shall provide the project submitter a reason for the delay and expected completion time;

(d)	ERCOT may, at its discretion, discuss submitted transmission projects at meetings of the RPG in order to obtain additional input into its independent review; and

(e)	ERCOT shall prepare a written report documenting the results of its independent review and recommendation on the project and shall distribute this report to the RPG.

(2)	Tier 1 Projects require ERCOT Board endorsement.

3.11.4.8	Determine Designated Providers of Transmission Additions

Upon completion of the RPG Project Review, ERCOT shall determine designated providers for the recommended transmission projects.  The default TSPs will be those TSPs that own the end points of the new projects.  Those TSPs can agree to provide or delegate the new facilities.  If different TSPs own the two ends of the recommended project, ERCOT will designate them as co-providers of the recommended project, and they can decide between themselves what parts of the recommended project they will each provide.  If they cannot agree, ERCOT will determine their responsibility following a meeting with the parties.  If a designated TSP agrees to provide a project and that designated TSP does not diligently pursue the project (during the time frame before a CCN is filed, if required) in a manner that will meet the required in-service date, then upon concurrence of the ERCOT Board, ERCOT will solicit interest from TSPs through the RPG and will designate an alternate TSP.

3.11.4.9	Regional Planning Group Acceptance and ERCOT Endorsement

(1)	For Tier 3 projects, successful resolution of all comments received from ERCOT and stakeholders during the project comment process will result in RPG acceptance of the proposed project.  A RPG acceptance letter shall be sent to the designated TSP for the project, the project submitter (if different from the designated TSP), and copied to the RPG.  For Tier 2 projects, ERCOT’s recommendation as a result of its independent review of the proposed project will constitute ERCOT endorsement of the project.  For Tier 1 projects, ERCOT’s endorsement is obtained upon affirmative vote of the ERCOT Board.  An ERCOT endorsement letter shall be sent to the designated TSP for the project, the project submitter (if different from the designated TSP), the PUCT and copied to the RPG upon receipt of ERCOT’s endorsement for Tier 1 and Tier 2 projects.

(2)	Following the completion of its independent review, ERCOT shall present all Tier 1 projects to the ERCOT Board with its recommendation as to whether the project should be endorsed by the ERCOT Board.  Prior to presenting the project to the ERCOT Board, ERCOT shall present the project to the Technical Advisory Committee (TAC) for review and comment.  Comments from TAC shall be included in the presentation to the ERCOT Board.  ERCOT will make a reasonable effort to make these presentations to TAC and the ERCOT Board at the next regularly scheduled meetings following completion of its independent review of the project.

3.11.4.10	Modifications to ERCOT Endorsed Projects

If the designated TSP for an ERCOT-endorsed project determines a need to make a significant change to the facilities included in the project (such as the line endpoint(s), number of circuits, voltage level, decrease in rating or similar major aspect of the project) prior to filing a CCN application (if required) for the project (or prior to beginning the final design of the project, if no CCN is required), the TSP shall notify ERCOT in a timely manner of the details of that change.  If ERCOT concurs that the proposed change is significant, the change shall be processed as a Tier 3 project.

3.11.5	Assessment of Chronic Congestion

(1)	ERCOT shall monitor the differences in LMPs from the Security-Constrained Economic Dispatch (SCED) process to identify geographic areas potentially experiencing chronic congestion.  On determination of chronic congestion, ERCOT shall:

(a)	Validate with the TSP that the data from the Network Operating Model and the Updated Network Model are correct.   If the models are valid, ERCOT shall use the planning criteria in the transmission planning process, through the RPG, to develop recommendations for resolution, if applicable.

(b)	Post all the results from this process on the MIS Secure Area and provide them to the PUCT Staff, the Independent Market Monitor (IMM), the appropriate TAC subcommittee(s), and the ERCOT Board.

(2)	ERCOT shall provide specific interval data for Load and generation to TSPs and/or DSPs, upon request, in accordance with confidentiality as defined in Section 1.3, Confidentiality.

(a)	The TSP’s and/or DSP’s request for interval data shall identify the reason for requesting the information in regards to impact to the planning process (e.g. build power flow cases, conduct a specific study, etc.).

(b)	ERCOT shall evaluate the TSP and/or DSP request and validate reasons provided.

(c)	Upon ERCOT validation of the TSP and/or DSP request, the data provided shall include meter data measured at points of injection and points of delivery which will measurably impact the TSP’s and/or DSP’s planning and operations as determined by ERCOT (e.g., determination of the TSP’s and/or DSP’s system Load or power flows).

(d) 	If ERCOT determines that the request is invalid and denies it, ERCOT shall provide the reasoning for denying the request.

3.11.6	Generation Interconnection Process

The generation interconnection process facilitates the interconnection of new generation units in the ERCOT Region by assessing the transmission upgrades necessary for new generating units to operate reliably.  The process to study interconnecting new generation or modifying an existing generation interconnection to the ERCOT Transmission Grid is covered in the Planning Guide.  The generation interconnection study process primarily addresses the direct connection of generation Facilities to the ERCOT Transmission Grid and directly-related projects.  Projects that are identified through this process and are regional in nature may be reviewed through the RPG Project Review process upon recommendation by the TSP or ERCOT, subject to the confidentiality provisions of the generation interconnection procedure.  ERCOT shall perform an independent economic analysis of the transmission projects that are identified through this process that are expected to cost more than $25,000,000.  This economic analysis is performed only for informational purposes; as such, no ERCOT endorsement will be provided.  The results of the economic analysis shall be included in the interconnection study posting.  Additional upgrades to the ERCOT Transmission Grid that might be cost-effective as a result of new or modified generation may be initiated by any stakeholder through the RPG Project Review procedure described in Section 3.11.4, Regional Planning Group Project Review Process, at the appropriate time, subject to the confidentiality provisions of the generation interconnection procedure.

3.12	Load Forecasting

ERCOT shall produce and use Load forecasts to serve operations and planning objectives.

(a)	ERCOT shall update and post hourly on the Market Information System (MIS) Public Area, a “Seven-Day Load Forecast” as described in Section 3.12.1, Seven-Day Load Forecast, that provides forecasted hourly Load over the next 168 hours for each of the Weather Zones and for each of the Forecast Zones.

(b)	ERCOT shall develop and post monthly on the MIS Secure Area a “36-Month Load Forecast” that provides a daily minimum and maximum Load forecast for the next 36-months for the ERCOT Region, for each of the Weather Zones, and for each of the Forecast Zones.  The 36-Month Load Forecast is used in the Outage coordination process and for Resource adequacy reporting.

3.12.1	Seven-Day Load Forecast

(1)	ERCOT shall use the Seven-Day Load Forecast to predict hourly Loads for the next 168 hours based on current weather forecast parameters within each Weather Zone.  Preparation for Day-Ahead Operations requires an accurate forecast of the Loads for which generation capacity must be secured.  The Seven-Day Load Forecast must have a “self-training” mode that allows ERCOT to review historic Load data and provide the ability to retrain the Seven-Day Load Forecast algorithm.

(2)	The inputs for the Seven-Day Load Forecast are as follows:

(a)	Hourly forecasted weather parameters for the weather stations within the Weather Zones, which are updated at least once per hour; and

(b)	Training information based on historic hourly integrated Weather Zone Loads.

(3)	ERCOT shall review the forecast suggested by Seven-Day Load Forecast and shall use its judgment, if necessary, to modify the result prior to implementation in the Ancillary Service capacity Monitor, Day-Ahead Reliability Unit Commitment (DRUC), Hour-Ahead Reliability Unit Commitment (HRUC), and Resource adequacy reporting.

3.13	Renewable Production Potential Forecasts

(1)	ERCOT shall produce forecasts of Renewable Production Potential (RPP) for Wind-powered Generation Resources (WGRs) to be used as an input into the Day-Ahead Reliability Unit Commitment (DRUC) and Hour-Ahead Reliability Unit Commitment (HRUC).  ERCOT shall produce the forecasts using information provided by WGR Entities, meteorological information, and Supervisory Control and Data Acquisition (SCADA).  WGR Entities shall install telemetry at their WGRs and transmit the ERCOT-specified site-specific meteorological information to ERCOT.  WGR Entities shall also provide detailed equipment status at the WGR facility as specified by ERCOT to support the RPP forecast.  ERCOT shall post forecasts for each WGR to the Qualified Scheduling Entities (QSEs) representing WGRs on the Market Information System (MIS) Certified Area.  QSEs shall use the ERCOT-provided forecasts for WGRs throughout the Day-Ahead and Operating Day for applicable markets and Reliability Unit Commitments (RUCs).  Similar requirements for solar power and run-of-the-river hydro must be developed as needed.

(2)	ERCOT shall develop cost-effective tools or services to forecast energy production from Intermittent Renewable Resources (IRRs) with technical assistance from QSEs scheduling IRRs.  ERCOT shall use its best efforts to develop accurate and unbiased forecasts, as limited by the availability of relevant explanatory data.  ERCOT shall post on the MIS Secure Area objective criteria and thresholds for unbiased, accurate forecasts within five Business Days of change.

3.14	Contracts for Reliability Resources and EILS Loads

ERCOT shall procure Reliability Must-Run (RMR) Service, Black Start Service (BSS) or Emergency Interruptible Load Service (EILS) through Agreements.

[NPRR451: Replace Section 3.14 above with the following on June 1, 2012:] 3.14 Contracts for Reliability Resources and Emergency Response Service Resources ERCOT shall procure Reliability Must-Run (RMR) Service, Black Start Service (BSS) or Emergency Response Service (ERS) through Agreements.

3.14.1	Reliability Must Run

(1)	RMR Service is the use by ERCOT, under contracts with Resource Entities, of  capacity and energy from Generation Resources that otherwise would not operate and that are necessary to provide voltage support, stability or management of localized transmission constraints under first contingency criteria, as described in the ERCOT Operating Guides, where market solutions do not exist.  This includes service provided by RMR Units and Must-Run Alternative (MRA) Resources.

(a)	Upon receiving notice from a Resource Entity as described in Section 3.14.1.1, Notification of Suspension of Operations, ERCOT may enter into RMR Agreements and begin procurement of RMR Service under this Section.

(b)	Before entering into an RMR Agreement, ERCOT shall assess alternatives to the proposed RMR Agreement.  ERCOT shall evaluate and present in a written report posted on the Market Information System (MIS) Secure Area the information in items (i) through (v) below.  ERCOT is not limited in the number of additional scenarios it chooses to evaluate.  The written report shall include an explanation as to why the items below are insufficient, either alone or in combination, to fill the requirement that will be met by the potential RMR Unit.  The report shall be posted in the time frame required under paragraph (3) of Section 3.14.1.2, ERCOT Evaluation.  The list of alternatives ERCOT must consider includes (as reasonable for each type of reliability concern identified):

(i)	Redispatch/reconfiguration through operator instruction;

(ii)	Remedial Action Plans (RAPs);

(iii)	Special Protection Systems (SPSs) initiated on unit trips or Transmission Facilities’ Outages;

(iv)	Load response alternatives once a suitable Load response service is defined and available; and

(v)	Resource alternatives, including capabilities of Distributed Generation (DG), Load Resources, Direct Current Ties (DC Ties), Block Load Transfers (BLTs), etc.

(c)	ERCOT shall minimize the use of RMR Units as much as practicable subject to the other provisions of these Protocols.  ERCOT may Dispatch an RMR Unit at any time for ERCOT System security.

(d)	Each RMR Unit must meet technical requirements specified in Section 8.1.1.1, Ancillary Service Qualification and Testing.

(e)	ERCOT may execute RMR Agreements for no less than one month and no more than one year, with one exception.  ERCOT may execute an RMR Agreement for a term longer than 12 months if the Resource Entity must make a significant capital expenditure to meet environmental regulations or to ensure availability to continue operating the RMR Unit so as to make an RMR Agreement in excess of 12 months appropriate, in ERCOT’s opinion.  The term of a multi-year RMR Agreement must take into account the appropriate RMR exit strategy discussed in Section 3.14.1.4, Exit Strategy from an RMR Agreement.  In the event ERCOT chooses to contract for an RMR Unit for longer than one year, ERCOT shall annually re-evaluate the need for the RMR Unit under the criteria set forth in paragraph (b) above.  If ERCOT determines the RMR Unit is no longer needed, ERCOT shall enter into exit negotiations with the contract signatories to attempt to exit the contract early.  However, ERCOT shall not enter into such negotiations until a Market Notice is issued providing the anticipated RMR exit time frame.  The RMR standard Agreement is included in Section 22, Attachment B, Standard Form Reliability Must-Run Agreement.  ERCOT shall post each RMR Agreement in its entirety, including amendments or modifications thereto, within five Business Days of execution on the MIS Secure Area.

(f)	A Generation Resource is eligible for RMR status based on criteria established by ERCOT indicating its operation is necessary to support ERCOT System reliability according to the Operating Guides.  A combined-cycle generation facility must be treated as a single unit for RMR purposes unless the combustion turbine and the steam turbine can operate separately.  If the steam turbine and combustion turbine can operate separately, and the steam turbine is powered by waste heat from more than one combustion turbine, the combustion turbine accepted for RMR Service and a proportionate part of the steam turbine must be treated as a single unit for RMR purposes.  If the combustion turbine accepted for RMR Service can operate separately from the steam turbine, and only the combustion turbine is accepted as an RMR Unit, the RMR energy price will be reduced by the value of the combustion turbine’s waste heat calculated at the Fuel Index Price (FIP), except when the steam turbine is Off-Line.  ERCOT shall post to the MIS Secure Area the criteria upon which it evaluates whether an RMR Unit meets the test of operational necessity to support ERCOT System reliability within five Business Days of change and shall issue a Market Notice stating the determination is available.  This includes the case where a unit previously identified by ERCOT as potentially needed for RMR Service is no longer needed regardless of whether an RMR Agreement was ever signed.

(g)	A Resource Entity cannot be compelled to enter into an RMR Agreement.  A Resource Entity that owns a Generation Resource that is uneconomic to remain in service can voluntarily petition ERCOT for contracted RMR status by following the process in this subsection.  ERCOT shall determine whether the Generation Resource is necessary for system reliability based on the criteria set forth in this Section.

(h)	ERCOT must contract for the entire capacity of each RMR Unit.

(i)	ERCOT shall post on the MIS Secure Area all information relative to the use of RMR Units including energy deployed monthly.

(j)	The Resource Entity  that owns the RMR Unit may not use the RMR Unit for:

(i)	Participating in the bilateral energy market;

(ii)	Self-providing of energy except for plant auxiliary Load obligations under the RMR Agreement; and

(iii)	Providing of Ancillary Service to any Entity.

(k)	ERCOT shall issue a Market Notice on the need for an RMR Unit prior to entering negotiations for the RMR Unit.  Such Market Notice shall include the link to the ERCOT final RMR evaluation, the Resource name and pneumonic, the name of the Resource Entity, the name of the QSE for the Resource, the Resource MW rating by Season, and potential duration of the RMR Agreement, including anticipated start and end dates.

(l)	ERCOT shall, through the issuance of Market Notices, provide the same information, contemporaneously, about the need for, or elimination of an RMR Unit to all registered Market Participants, including QSEs and Resource Entities with RMR Units.

3.14.1.1	Notification of Suspension of Operations

(1)	Except for the occurrence of a Forced Outage, a Resource Entity must notify ERCOT in writing no less than 90 days before the date on which the Resource Entity intends to cease or suspend operation of a Generation Resource for a period of greater than 180 days by submitting a completed Part I of the Notification of Suspension of Operations (found in Section 22, Attachment E, Notification of Suspension of Operations).  The Resource Entity may also complete Part II of the Notification and submit it along with Part I, or may wait to submit Part II until ERCOT makes an initial determination of the need for the Generation Resource as an RMR Unit.  The Part I Notification must include the attestation of an officer of the Resource Entity that the Generation Resource is uneconomic to remain in service and will be unavailable for Dispatch by ERCOT for a period specified in the Notification.

(2)	A Resource Entity ceasing or suspending operations as a result of a Forced Outage lasting greater than 180 days shall notify ERCOT as soon as practicable.  A Notification of Suspension of Operations submitted due to a Forced Outage will not be evaluated for RMR status and will not be posted on the MIS.

(3)	At least 60 days before the expiration of an existing RMR Agreement, the Resource Entity may apply to renew the RMR Agreement by submitting a new Notification (including both Part I and Part II).  Upon receipt of such a renewal request, ERCOT shall update and post to the MIS Secure Area, studies as set forth in Section 3.14.1, Reliability Must Run, within 15 Business Days.

3.14.1.2	ERCOT Evaluation

(1)	Upon receipt of a Notification under Section 3.14.1.1, Notification of Suspension of Operations, ERCOT shall post the Notification on the MIS Secure Area and shall post all existing relevant studies and data and provide a Market Notice of the application and posting of the studies and data.

(2)	Within 14 days after receiving the Notification described in paragraph (1) above, unless otherwise notified by ERCOT that a shorter comment period is required, Market Participants may submit comments to ERCOT on whether the proposed RMR Unit meets the test of operational necessity to support ERCOT System reliability or whether the proposed RMR Unit should qualify for a multi-year RMR Agreement.  ERCOT shall consider and post all submitted comments on the MIS Secure Area.

(3)	Within 24 days after receiving the Notification, ERCOT shall make an initial determination of whether the Generation Resource is required to support ERCOT System reliability.  ERCOT shall develop a Load value for use in the RMR study as follows:  For the Load in the RMR local area, ERCOT shall use the regional Load value provided by the appropriate Transmission Service Provider (TSP) as part of the annual Steady State Working Group (SSWG) study case development process.  For Load for the rest of the system, ERCOT shall use maximum system peak Load forecast for the next 12 months based on the weekly Load forecast data posted pursuant to P.U.C. Subst. R. 25.505, Resource Adequacy in the Electric Reliability Council of Texas Power Region.  Additionally, ERCOT shall conduct any other analysis as required and shall post all study data and results and all analyses and its determination on the MIS Secure Area and issue a Market Notice of its determination.

(4)	Within ten days after a determination by ERCOT that the Generation Resource is required to support ERCOT System reliability, the Resource Entity shall, if it has not already done so, complete and submit to ERCOT Part II of the Notification of Suspension of Operations (Section 22, Attachment E, Notification of Suspension of Operations).  ERCOT shall post the Part II information on the MIS Secure Area.  On the 11th day after the determination or on receipt of Part II of the Notification, whichever comes first, ERCOT and the Resource Entity shall begin good faith negotiations on an RMR Agreement.  These negotiations shall include the budgeting process for Eligible Costs and for fuel costs as detailed in Section 3.14.1.11, Budgeting Eligible Costs, and Section 3.14.1.15, Budgeting Fuel Costs.

(5)	Within 60 days after receiving the Part I Notification, ERCOT shall make a final assessment of whether the Generation Resource is required to support ERCOT System reliability.  ERCOT shall issue a Market Notice of its determination prior to entering RMR Agreement negotiations with the Generation Resource.  If ERCOT determines that the Generation Resource is required, and the RMR Agreement between ERCOT and the Generation Resource has not yet been finalized, good faith negotiations must continue.  At the end of 60 days, ERCOT shall issue a Market Notice on the status of negotiations containing an indication as to whether negotiations are ongoing and the expected time frame for conclusion of negotiations.  If ERCOT determines that the Generation Resource is not needed to support ERCOT System reliability, then the Generation Resource may cease or suspend operations according to the schedule in its Notification, and ERCOT shall issue a Market Notice to this effect.

(6)	ERCOT shall issue a Market Notice on the status of the RMR Unit, including the start date, duration of the RMR Agreement, the Standby Cost per MW and the amount of MW under contract, within 24 hours of signing an RMR Agreement with a Resource Entity.

(7)	If, after 90 days following ERCOT’s receipt of the Part I Notification, either ERCOT has not informed the Resource Entity that the Generation Resource is not needed for ERCOT System reliability or both parties have not signed a RMR Agreement for a Generation Resource that ERCOT has determined to be required for ERCOT System reliability, then the Resource Entity may file a complaint with the Public Utility Commission of Texas (PUCT) under subsection (e)(1) of P.U.C. Subst. R. 25.502, Pricing Safeguards in Markets Operated by the Electric Reliability Council of Texas.

(8)	If, after 90 days following receipt of the Part I Notification, ERCOT and the Resource Entity have not finalized an RMR Agreement for a Generation Resource that ERCOT has determined to be required for ERCOT System reliability, then the Resource Entity shall maintain that Generation Resource(s) so that it is available for Reliability Unit Commitment (RUC) commitment until no longer required to do so under P.U.C. Subst. R. 25.502(e)(2).

3.14.1.3	ERCOT Report to Board on Signed RMR Agreements

(1)	After receiving a Notification of Suspension of Operations and conducting the analysis required by the Protocols and after the date on which it executes an RMR Agreement, ERCOT shall provide notice to the ERCOT Board, at the next ERCOT Board meeting after ERCOT has signed the RMR Agreement, that the following steps have been completed with respect to any RMR Agreement signed by ERCOT:

(a)	The Resource Entity provided a complete and timely Notification of Suspension of Operations including a sworn attestation supporting its claim of pending Generation Resource closure;

(b)	ERCOT received all the data requested from the applicant necessary to evaluate the need for and provisions of the RMR Agreement, that information was posted on the MIS Secure Area by ERCOT, as it became available to ERCOT;

(c)	The signed RMR Agreement complies with the ERCOT Protocols and is posted on the MIS Secure Area;

(d)	ERCOT evaluated:

(i)	The reasonable alternatives to a specific RMR Agreement as set forth in Section 3.14.1, Reliability Must Run, and compared the alternatives against the feasibility, cost and reliability impacts of the signed RMR Agreement;

(ii)	The timeframe in which ERCOT expects each unit to be needed for reliability; and

(iii)	The specific type and scope of reliability concerns identified for each RMR Unit.

(2)	ERCOT shall post on the MIS Secure Area, as they become available, unit-specific studies, reports, and data, by which ERCOT justified entering into the RMR Agreement.

3.14.1.4	Exit Strategy from an RMR Agreement

No later than 90 days after the execution of an RMR Agreement, ERCOT shall report to the Board and post on the MIS Secure Area a list of feasible alternatives that may, at a future time, be more cost-effective than the continued renewal of the existing RMR Agreement.  Through the ERCOT System planning process, ERCOT shall develop a list of potential alternatives to the service provided by the RMR Unit.  At a minimum, the list of potential alternatives that ERCOT must consider include, building new or expanding existing Transmission Facilities, installing voltage control devices, soliciting or buying by auction interruptible Load from Retail Electric Providers (REPs), or extending the existing RMR Agreement on an annual basis.  If a cost-effective alternative to the service provided by the RMR Unit is identified, ERCOT shall provide a proposed timeline to study and/or implement the alternative.

3.14.1.5	Potential Alternatives to RMR Agreements

(1)	ERCOT shall provide reasonably available information that would enable potential MRA Resources to assess the feasibility of submitting a proposal to provide a more cost-effective alternative to an RMR Unit through the regional planning process, including any known minimum technical requirements and/or operational characteristics required to eliminate the need for the RMR Unit.  The Technical Advisory Committee (TAC) shall review the output of the regional planning process and provide guidance prior to entering into an agreement with an MRA Resource (MRA Agreement).

(2)	After the process identified in paragraph (1) above, and subsequent to the issuance of a Market Notice on the intent to enter into an MRA Agreement detailing the solution, location and MW as applicable, ERCOT may negotiate a contract for an MRA Resource that:

(a)	Technically provides an acceptable solution to the reliability concern that would otherwise be solved by the RMR Unit(s);

(b)	Will provide a more cost effective alternative to continued service by the RMR Unit (evaluated over the exit strategy period); provided, however, that no proposed MRA Resource will be considered if it does not provide at least $1 million in annual savings over the projected net annualized costs for the RMR Unit; and

(c)	Satisfies objective financial criteria to demonstrate that the seller is reasonably able to fulfill its performance obligations as determined by ERCOT.

(3)	If the resulting MRA Agreement would result in significantly lower total costs than continued service by the RMR Agreement, and otherwise meets the requirements of this subsection, ERCOT may sign the MRA Agreement.  ERCOT shall issue a Market Notice documenting the solution, location(s), and expected MW and duration of supply, as applicable, within 24 hours of signing the MRA Agreement.  The term of the MRA Agreement must be limited to the time period until the cost effective exit strategy can be implemented.

(4)	If the execution of an MRA Agreement would result in the foreclosure of other technically viable solutions (e.g., the RMR Unit that is being replaced by the MRA Agreement retires and is no longer available as an alternative to the MRA Agreement), the MRA Agreement shall include terms and conditions that limit the MRA Resource owner’s ability to withdraw or raise the price of the MRA Agreement in future years until an exit strategy can be implemented.

(5)	For any MRA Agreement entered into by ERCOT, ERCOT shall annually update the list of feasible alternatives developed in Section 3.14.1.4, Exit Strategy from an RMR Agreement, and provide an update of that information to the TAC and the ERCOT Board.

3.14.1.6	Transmission System Upgrades Associated with an RMR and/or MRA Exit Strategy

This section applies only to RMR exit strategies corresponding to specific RMR or MRA Agreements that have not been terminated.

(a)	ERCOT and the TSP(s) responsible for constructing any upgrades to the Transmission Facilities that are part of an RMR or MRA exit strategy shall coordinate construction clearances necessary to allow timely completion of all planned Transmission Facilities upgrades.

(b)	The TSP(s) responsible for constructing upgrades to the Transmission Facilities that are part of an RMR or MRA exit strategy shall establish and send to ERCOT estimated Outage information, including completion dates and associated model information to ERCOT per Section 3.1.4, Communications Regarding Resource and Transmission Facilities Outages.  For purposes of this Section, a Transmission Facility upgrade will be considered initiated upon the TSP authorizing any expenditures on the upgrade including, but not limited to, material procurement, right-of-way acquisition, and regulatory approvals.

(c)	Upon initiation of the project, the TSP(s) responsible for constructing upgrades relating to the Transmission Facilities that are part of an RMR or MRA exit strategy shall provide to ERCOT monthly updates of the project’s status, noting any acceleration or delay in planned completion date. ERCOT shall report this data through the MIS as described in Section 12.2, ERCOT Responsibilities. Within 60 days of the completion date shown in the Notice provided per Section 3.1.4, for the Transmission Facilities upgrades, the TSP shall coordinate more timely updates if the timeline changes significantly.

(d)	Within ten Business Days after completion of the Transmission Facilities upgrades that are part of an RMR or MRA exit strategy, ERCOT shall publish a Market Notice of such completion and the effective date of termination of the associated RMR or MRA Agreement.

3.14.1.7	RMR or MRA Contract Termination

(1)	This section applies only to RMR exit strategies corresponding to specific RMR or MRA Agreements that have not been terminated.

(2)	Once a suitable RMR or MRA exit strategy has been developed as defined in Section 3.14.1.4, Exit Strategy from an RMR Agreement, and the strategy has been approved by the ERCOT Board and the affected TSP(s), the TSP(s) responsible for the Transmission Facilities upgrades, when requested by ERCOT, shall submit to ERCOT:

(a)	A preliminary construction outage schedule necessary to complete the Transmission Facilities upgrades. Submissions, changes, approvals, rejections, and withdrawals regarding the preliminary construction outage schedule shall be processed through the ERCOT Outage Scheduler on the ERCOT MIS.  Such construction outage schedule shall be updated monthly; or

(b)	A Certificate of Convenience and Necessity (CCN) application timeline for projects requiring such PUCT certification.  Once a CCN has been granted by the PUCT, the TSP(s) shall be required to meet the requirements in item (a) above.

(3)	ERCOT shall review and approve or reject each construction outage schedule as provided in accordance with procedures developed by ERCOT in compliance with Section 3.1, Outage Coordination.

(4)	The TSP(s) responsible for the Transmission Facilities upgrades that are part of an RMR or MRA exit strategy shall provide to ERCOT a project status and an estimated project completion date within five Business Days of ERCOT’s request.

(5)	If ERCOT determines that a mutually agreeable preliminary construction outage schedule can be accommodated during the fall, winter, or spring, ERCOT and the TSP shall collaborate to determine if the 90 day termination notice for the RMR and/or MRA can be issued as soon after the summer load season of the preceding year as possible and publish a Market Notice of these terminations.  ERCOT and the TSP may give consideration to the risk of the decision to terminate the RMR and/or MRA Agreement and any options, such as RAPs and/or Mitigation Plans that could be used to mitigate transmission construction delays.

3.14.1.8	RMR and/or MRA Contract Extension

This section applies only to RMR exit strategies corresponding to specific RMR or MRA Agreements that have not been terminated.

(a)	Forty-five days prior to the termination date of an existing RMR or MRA Agreement, pursuant to the 90-day termination notice as described in paragraph A(2) of Section 3, Term and Termination, of Section 22, Attachment B, Standard Form Reliability Must-Run Agreement, ERCOT shall assess the likelihood of completion of the Transmission Facilities upgrade project(s) or other exit strategies necessary to allow termination of an existing RMR or MRA Agreement based on the updates of project status provided by the TSP(s).  If ERCOT determines that a delay in the termination date of the existing RMR or MRA Agreement is necessary to allow completion of the Transmission Facilities upgrade(s), it shall provide written Notice to the Resource Entity that owns the RMR Unit or MRA Resource of its intent to execute an extension to the existing RMR or MRA Agreement no later than 30 days prior to the planned termination date.  Within 24 hours of ERCOT providing this Notice to the Resource Entity that owns the RMR Unit or MRA Resource, ERCOT shall issue a Market Notice on its intent to execute an extension to the existing RMR or MRA Agreement.  The Market Notice must contain the name and seasonal MW ratings of the RMR Unit or MRA Resource and the expected duration of the contract extension, including the expected termination date.

(b)	Forty-five days prior to the expiration date of an existing RMR or MRA Agreement for which the Resource Entity has applied for renewal, ERCOT shall assess the likelihood of completion of the Transmission Facilities upgrade project(s) necessary to eliminate the reliability need for a Resource with an existing RMR or MRA Agreement based on the updates of project status provided by the TSP(s).  If ERCOT determines that an extension of the existing RMR or MRA Agreement of no more than 90 days would allow completion of the Transmission Facilities upgrade(s), it shall provide written Notice to the Resource Entity that owns the RMR Unit or MRA Resource of its intent to execute an extension to the existing RMR or MRA Agreement no later than 30 days prior to the planned expiration date.  Within 24 hours of ERCOT providing this Notice to the Resource Entity that owns the RMR Unit or MRA Resource, ERCOT shall issue a Market Notice on its intent to execute an extension to the existing RMR or MRA Agreement.  The Market Notice must contain the name and seasonal MW ratings of the RMR Unit or MRA Resource and the expected duration of the contract extension, including the expected termination date.

(c)	ERCOT may extend the existing RMR or MRA Agreement as necessary to allow completion of the Transmission Facilities upgrade(s), but in no event shall the extension last more than 90 days from the termination or expiration date of the existing RMR or MRA Agreement.

(d)	Forty-five days prior to the end of the period for which the existing RMR or MRA Agreement has been extended, ERCOT shall assess whether the transmission upgrades are likely to be completed.  If ERCOT determines that the upgrades are not likely to be completed, ERCOT shall enter into negotiations with the Resource Entity that owns the RMR or MRA Resource to negotiate a new RMR or MRA Agreement to allow completion of the planned transmission upgrades.  ERCOT shall issue a Market Notice on or before the date that extension negotiations begin with the Resource Entity that owns the RMR or MRA Resource.  The Market Notice must contain the name and seasonal MW ratings of the RMR Unit or MRA Resource and the expected duration of the contract extension, including the expected termination date.  Additionally, the Market Notice must contain a description of the exit strategy and the status of progress of exit strategy projects.

3.14.1.9	Generation Resource Return to Service Updates

(1)	By April 1st and October 1st of each year and when material changes occur, every Resource Entity that owns or controls a Mothballed Generation Resource or an RMR Unit shall report to ERCOT, on a unit-specific basis, the estimated lead time required for each Resource to be capable of returning to service and, in percentage terms, report probable generation capacity from each Resource that the Resource Entity expects to return to service in each Season of each of the next ten years.

(2)	For modeling purposes, ERCOT and TSPs shall rely on the most recent submittal of the following two Notifications with respect to an RMR Unit, Mothballed Generation Resource or Decommissioned Generation Resource: Section 22, Attachment E, Notification of Suspension of Operations, or Section 22, Attachment H, Notification of Change of Generation Resource Designation.

(3)	A Resource Entity with a Mothballed Generation Resource that has been in mothballed status for 90 days or more shall notify ERCOT in writing no less than 30 days prior to the date on which the Resource Entity intends to return a Mothballed Generation Resource to service by completing a Notification of Change of Generation Resource Designation.  A Resource Entity with a Mothballed Generation Resource that has been in mothballed status for less than 90 days shall notify ERCOT in writing no less than 90 days prior to the date on which the Resource Entity intends to return a Mothballed Generation Resource to service by completing a Notification of Change of Generation Resource Designation.  ERCOT shall post the Notification of Change of Generation Resource Designation on the MIS Secure Area as soon as practicable, but no later than five Business Days after receipt.  If a Resource Entity wishes to change the operational designation of a Generation Resource upon conclusion of an RMR Agreement, it must submit a Notification of Change of Generation Resource Designation no later than 60 days prior to the conclusion of the RMR Agreement.  ERCOT shall post on the MIS Secure Area information relating to a change of the operational designation of a Generation Resource pending conclusion of an RMR Agreement as soon as practicable but no later than five Business Days after receipt of such information.

(4)	A Resource Entity that submitted a Notification of Suspension of Operations as a result of a Forced Outage must notify ERCOT of its intent to return to service as soon as practicable by updating its status in the Outage Scheduler and Current Operating Plan (COP) and is not required to submit a Notification of Change of Generation Resource Designation.

(5)	If a Generation Resource is designated as decommissioned and retired under either Notification, ERCOT will permanently remove the Generation Resource from the ERCOT registration systems in accordance with Section 3.10.1, Time Line for Network Operations Model Changes.  If a Resource Entity decides to bring a Decommissioned Generation Resource back to service at a later date, it will be considered a new Resource and must follow the Generation Resource Interconnection or Change Request process detailed in the Planning Guide.  If the Generation Resource is designated as mothballed, ERCOT and TSPs will consider the Generation Resource mothballed until the Resource Entity indicates a definitive return to service date pursuant to this Section.

3.14.1.10	Eligible Costs

“Eligible Costs” are costs that would be incurred by the RMR Unit owner to provide the RMR Service, excluding fuel costs, above the costs, excluding fuel costs, the RMR Unit would have incurred anyway had it been mothballed or shut down.

(a)	Examples of Eligible Costs include the following to the extent they each meet the standard for eligibility:

(i)	Labor to operate the RMR Unit during the term of the RMR Agreement;

(ii)	Materials and supplies consumed or used in operation of the RMR Unit during the term of the RMR Agreement;

(iii)	Services necessary to operate the RMR Unit during the term of the RMR Agreement;

(iv)	Costs associated with emissions credits used as a direct result of operation of the RMR Unit under direction from ERCOT, or emissions reduction equipment as may be required according to terms of the RMR Agreement;

(v)	Costs associated with maintenance:

(A)	Due to required equipment maintenance;

(B)	Due to replacement to alleviate unsafe operating conditions;

(C)	Due to regulatory requirements, with compliance dates during the term of the RMR Agreement (any such compliance dates and requirements shall be explicitly defined in the RMR Agreement); or

(D)	To ensure the ability to operate the RMR Unit consistent with Good Utility Practice;

(vi)	Reservation and transportation costs associated with firm fuel supplies not recovered under Section 6.6.6.2, RMR Payment for Energy;

(vii)	Property taxes and other taxes attributable to continuing to operate the RMR Unit during the term of the RMR Agreement; and

(viii)	Nodal implementation surcharges.

(b)	Examples of costs not included as Eligible Costs are:

(i)	Depreciation expense, return on equity, and debt and interest costs;

(ii)	Property taxes and other taxes not attributable to continuing to operate the RMR Unit;

(iii)	Income taxes of the RMR Unit owner or operator;

(iv)	Labor costs associated with other, non-RMR Generation Resources at the same facility; and

(v)	Any other costs the Resource Entity that owns the RMR Unit would have incurred even if the RMR Unit had been mothballed or shutdown.

3.14.1.11	Budgeting Eligible Costs

(1)	The owner of the RMR Unit shall provide good faith detailed estimates of its Eligible Costs to ERCOT as part of the RMR Agreement negotiation process.  ERCOT shall review and approve the budget and use these figures as the basis for Initial Settlement for RMR Service.  Actual Eligible Costs incurred by the RMR Unit will be used for subsequent Final, Resettlement, or True-Up Settlements as agreed upon in Section 6.6.6, Reliability Must-Run Settlement.

(2)	The Eligible Cost budgeting process is as follows:

(a)	The RMR Unit owner shall supply ERCOT a preliminary Eligible Cost budget for the 12-month period starting with the anticipated effective date of the RMR Agreement.  The budget will include Eligible Costs categorized in terms of:

(i)	Base Cost of Operations, which includes Eligible Costs that are independent of the levels of operation, Outages and non-Outage maintenance;

(ii)	Outage Maintenance Cost, which includes Eligible Costs attributable to Planned or Maintenance Outages and/or inspections occurring during the term of the RMR Agreement.  Maintenance alternatives available during any Planned or Maintenance Outage must be presented to ERCOT for determination of the alternative to be performed and paid for under the RMR Agreement.  The RMR Unit owner must present ERCOT with a budget for each option, benefits of each alternative, unit availability impact associated with not performing each alternative, and a recommendation to facilitate ERCOT’s selection process;

(iii)	Non-Outage Maintenance Cost, which includes non-recurring Eligible Costs that are independent of a particular scheduled Outage.  Non-Outage maintenance alternatives available during any scheduled Outage must be presented to ERCOT for determination of the alternative to be performed and paid for under the RMR Agreement.  The RMR Unit owner must present ERCOT with a budget for each option, benefits of each alternative, unit availability impact associated with not performing each alternative, and a recommendation to facilitate ERCOT’s selection process;

(iv)	Other budget items means Eligible Costs not clearly identifiable in the previous three categories including:

(A)	Environmental emission credit consumption (or purchase as explicitly defined under the RMR Agreement, to operate the unit) includes the opportunity cost for using emission credits through the combustion of fuel feedstock by the RMR Unit.  Costs must be based on verifiable market data as supplied by the RMR Unit owner; and

(B)	“Compliance Costs,” which includes foreseeable costs to comply with regulations, Federal or state that have a compliance deadline that occurs during the term of the RMR Agreement.

(b)	Thirty days after receipt of the preliminary Eligible Costs budget, ERCOT shall notify the RMR Unit owner of its selections under the alternatives provided in the preliminary budget.  The RMR Unit owner and ERCOT shall set the Target Availability consistent with the options presented to and selected by during the budgeting process.  The “Target Availability” shall be determined by taking into account a negotiated amount of predicted Forced Outages and Planned Outages identified during the budgeting process.

3.14.1.12	Reporting Actual Eligible Cost

The RMR Unit owner shall provide ERCOT with actual Eligible Costs on a monthly basis in a level of detail sufficient for ERCOT to verify that all Eligible Costs are actual and appropriate.  Actual cost data must be submitted on time by the Resource Entity for the RMR Unit and then verified by ERCOT so the actual cost data can be reflected in the True-Up Settlement Statement. To be considered timely for the final, actual cost data for month ‘x’ must be submitted by the 20th of the month following month ‘x’.  To be considered timely for the true-up, actual cost data for month ‘x’ must be submitted 30 days prior to the publishing date of the True-Up Settlement Statement for the first day in month ‘x’.  Any deviation in filing actual cost data in accordance with this calendar must be requested of ERCOT, by the Qualified Scheduling Entity (QSE) representing an RMR unit.  Such request for deviation shall contain the reason for the inability to meet the calendar and an expected date that the cost data will be provided to ERCOT.  At its discretion ERCOT may choose to honor such a request.  ERCOT shall post on the MIS Public Area any such request and response thereto.  In the event, that actual cost data is not submitted  in accordance with the calendar or approved deviation for the true-up, then the cost for the portion of eligible cost that has not been submitted is deemed to be zero.

3.14.1.13	Incentive Factor

(1)	Subject to the reductions described in items (2) and (3), the Incentive Factor for RMR Agreements is equal to 10% of the actual Eligible Costs excluding fuel costs incurred by the RMR Unit.  The Incentive Factor for RMR Agreements is not applied to capital expenditures as described in Section 3.14.1, Reliability Must Run, nor is the Incentive Factor applied to nodal implementation surcharges.  The Incentive Factor shall never be less than zero.

(2)	The Incentive Factor payment shall be reduced if the RMR Unit fails to perform to the contracted capacity during a Capacity Test as described in the RMR Agreement.  The reduction will be linear, with a two percent reduction in the Incentive Factor payment for every one percent of reduced Capacity.

(3)	The Incentive Factor payment shall be reduced if the “Hourly Rolling Equivalent Availability Factor” of the RMR Unit is less than the Target Availability (i.e. the “Actual Availability”, as defined below, is less than the Target Availability).  The reduction will be linear; with a two percent reduction in the Incentive Factor payment for every one percent of the Hourly Rolling Equivalent Availability Factor is less than the Target Availability stated in the RMR Agreement.  The RMR Unit’s Actual Availability shall be calculated on an hourly rolling six-month average basis by dividing the number of hours that the RMR Unit was available according to its final COP for each hour of the previous 4380 hours by 4380.  If less than 4380 hours have elapsed since the start of the RMR Agreement (“Elapsed Time”), then, for each hour that Elapsed Time is less than 4380, that hour shall be considered as if the RMR Unit was available.

3.14.1.14	Major Equipment Modifications

During the term of an RMR Agreement, in the event that major equipment modifications are required in order for the RMR Unit to provide RMR Service (such as installation of environmental control equipment), ERCOT and the RMR Unit owner shall negotiate in good faith concerning changes to the terms of the RMR Agreement.

3.14.1.15	Budgeting Fuel Costs

(1)	The RMR Unit owner shall supply ERCOT a preliminary fuel cost budget for the 12-month period starting with the anticipated effective date of the RMR Agreement.  The budget must include information pertaining to the cost of the fuel feedstock, including where appropriate transportation costs and terms, as well as fuel storage costs and terms, and any other fuel contract provisions (e.g. “take or pay” provisions) that may impact the cost of all fuels anticipated to be used by the RMR Unit over the life of the RMR Agreement and must include fuel costs categorized in terms of:

(a)	primary fuel; and

(b)	secondary fuel.

(2)	The RMR Unit owner shall provide good faith estimates of the RMR Unit input/output curve to ERCOT in its application for an RMR Agreement.  Based on production figures provided to the RMR Unit owner by ERCOT, the RMR Unit owner shall also provide ERCOT fuel supply options available for the RMR Unit.  For each option, RMR Unit owner shall detail the associated impacts on the fuel and non-fuel budgets and on the availability of the unit.  No less than 30 days after the receipt of the fuel supply options, ERCOT shall notify the RMR Unit owner of its fuel supply option selection.

3.14.1.16	Reporting Actual Eligible Fuel Costs

(1)	The RMR Unit owner shall provide ERCOT with actual fuel costs on a monthly basis for the RMR Unit in a level of detail sufficient for ERCOT to verify that all fuel costs are actual and appropriate.  The estimated fuel payments may include a fuel adder to better approximate expected actual fuel costs.  The fuel adder shall represent the difference between the forecasted average actual future fuel price paid and the forecasted average of the relevant index price (Fuel Index Price (FIP), Fuel Oil Price (FOP) or solid fuel) over the RMR contract period.  The fuel adder must also include the forecasted cost of transporting, delivering and fuel imbalances to the Resource.  QSEs must provide to ERCOT supporting documentation indicating how the fuel adder was determined.  ERCOT shall perform a true-up of the estimated fuel costs using the submitted and verified actual fuel costs for the RMR Unit.  Actual cost data must be submitted on time by the Resource Entity for the RMR Unit and then verified by ERCOT so the actual cost data can be reflected in the True-Up Settlement Statement.  To be considered timely for the final, actual cost data for month ‘x’ must be submitted by the 20th of the month following month ‘x.’  To be considered timely for the true-up, actual cost data for month ‘x’ must be submitted 30 days prior to the publishing date of the True-Up Settlement Statement for the first day in month ‘x.’  Any deviation in filing actual cost data in accordance with this calendar must be requested of ERCOT, by the QSE representing an RMR Unit.  Such request for deviation shall contain the reason for the inability to meet the calendar and an expected date that the cost data will be provided to ERCOT.  At its discretion ERCOT may choose to honor such a request.  ERCOT shall post on the MIS Public Area any such request and response thereto.  In the event that actual cost data is not submitted in accordance with the calendar or approved deviation for the true-up, then the cost for the portion of Eligible Cost that has not been submitted is deemed to be zero.

(2)	Actual fuel costs must be appropriate actual costs attributable to ERCOT’s scheduling and/or deployment of the RMR Unit.  Actual fuel costs may include cost of fuel (including the cost of exceeding swing gas contract limits, additional gas demand costs set by fuel supply, or transportation contracts); demand fees, imbalance penalties, transportation charges, and cash out premiums.

3.14.2	Black Start

(1)	Each Generation Resource providing BSS must meet the requirements specified in North American Electric Reliability Corporation (NERC) Reliability Standards and the Operating Guides.

(2)	Each Generation Resource providing BSS must meet technical requirements specified in Section 8.1.1, QSE Ancillary Service Performance Standards, and Section 8.1.1.1, Ancillary Service Qualification and Testing.

(3)	Bids for BSS are due on or before June 1st of each two year period.  Bids must be evaluated based on evaluation criteria attached as an appendix to the request for bids and contracted by December 31st for the following two year period.  ERCOT shall ensure BSSs are arranged, provided, and deployed as necessary to reenergize the ERCOT System following a Blackout or Partial Blackout.

(4)	ERCOT shall schedule random testing or simulation, or both, to verify BSS is operable according to the ERCOT System restoration plan.  Testing and verification must be done under established qualification criteria.

(5)	QSEs representing Generation Resources contracting for BSSs shall participate in training and restoration drills coordinated by ERCOT.

(6)	ERCOT shall periodically conduct system restoration seminars for all TSPs, Distribution Service Providers (DSPs), QSEs, Resource Entities and other Market Participants.

(7)	ERCOT shall periodically determine and review the location and number of Black Start Resources required, as well as any special transmission or voice communication needs required.  ERCOT and providers of this service shall meet the requirements as specified in the Operating Guides and in NERC Reliability Standards.

(8)	A Resource Entity representing a Black Start Resource may request that an alternate Generation Resource which is connected to the same black start primary and secondary cranking path as the original Black Start Resource be substituted in place of the original Black Start Resource during the two year term of an executed Standard Form Black Start Agreement (Section 22, Attachment D, Standard Form Black Start Agreement) if the alternate Generation Resource meets testing and verification under established qualification criteria to ensure BSS.

(a) 	ERCOT, in its sole discretion, may reject a Resource Entity’s request for an alternate Generation Resource and will provide the Resource Entity an explanation of such rejection.

(b) 	If ERCOT accepts the alternative Generation Resource as the substituted Black Start Resource, such acceptance shall not affect the original terms, conditions and obligations of the Resource Entity under the Standard Form Black Start Agreement.  The Resource Entity shall submit to ERCOT an Amendment to Standard Form Black Start Agreement (Section 22, Attachment I, Amendment to Standard Form Black Start Agreement) after qualification criteria has been met.

(9)	For the purpose of the Black Start Hourly Standby Fee as described in Section 6.6.8.1, Black Start Hourly Standby Fee, the Black Start Service Availability Reduction Factor shall be determined by using the availability for the original Black Start Resource and any substituted Black Start Resource(s), as appropriate for the rolling 4380 hour period of the evaluation.

3.14.3	Emergency Interruptible Load Service (EILS)

(1)	ERCOT shall procure EILS for EILS Contract Periods.  The standing EILS Contract Periods are as follows:

(a)	June through September;

(b)	October through January; and

(c)	February through May.

(2)	ERCOT may restructure EILS Contract Periods in order to facilitate additional Load participation in EILS.  ERCOT shall provide Notice of any changes to the standing EILS Contract Periods no less than 90 days prior to the start date of that EILS Contract Period.

(3)	ERCOT will solicit offers to provide EILS prior to each EILS Contract Period.

(4)	EILS offers may be submitted to ERCOT only by QSEs capable of receiving Verbal Dispatch Instructions (VDIs) on behalf of represented EILS Loads.  A QSE may submit offers on behalf of multiple EILS Loads for any EILS Contract Period.

(5)	ERCOT shall solicit EILS offers.  QSEs on behalf of EILS Load may submit offers for one or more EILS Time Periods within an EILS Contract Period.  An EILS offer is specific to an EILS Time Period.  In submitting an offer, a QSE and the EILS Load are committing to provide EILS for that EILS Time Period if selected.

(6)	The minimum amount of EILS that may be offered in an offer to ERCOT is one MW.  EILS Loads may be aggregated to reach the one MW offer requirement.

(7)	An offer to provide EILS shall include:

(a)	The name of the QSE representing the EILS Load;

(b)	The name of the Entity supplying the EILS Loads;

(c)	A description of the Load(s) that will provide EILS if selected, including name(s) and Electric Service Identifier(s) (ESI ID(s));

(d)	The EILS Time Period for which the offer is submitted;

(e)	A dollars per MW price for the capacity offer unless the offer is for EILS Self-Provision;

(f)	The quantity of capacity for which the offer price is effective;

(g)	For EILS Loads assigned to the alternate baseline, the maximum base Load, in MW, defined as the maximum level of Load at which the EILS Load may operate throughout the Sustained Response Period in an EILS deployment event;

(h)	For EILS Loads that are not metered by a dedicated ESI ID in a competitive choice area of the ERCOT Region, including those situated in territories served by Non-Opt-In Entities (NOIEs) or within Private Use Networks, historical Interval Data Recorder (IDR) data as prescribed by ERCOT in a format specified by ERCOT;

(i)	QSEs opting for EILS Self-Provision must provide ERCOT with the maximum amount of capacity they plan to provide through this option before ERCOT begins to accept EILS offers;

(j)	A QSE opting for EILS Self-Provision may also offer separate capacity into EILS in the form of a priced offer in the same manner as any other QSE; and

(k)	Affirmation that the capacity being offered into EILS is not capacity that is separately obligated to provide demand response during any of the same hours, and receiving a separate reservation payment for such obligation, occurring in the contracted EILS Time Period.  For any Loads found to be dually committed, ERCOT shall treat their Load as zero for that Contract Period and may prohibit their participation in the next EILS Contract Period following the discovery.

(8)	QSEs may self-provide EILS.  Self-providing QSEs must adhere to the following steps for offering EILS in an EILS Contract Period:

(a)	A QSE electing to self-provide part or all of its EILS obligation for an EILS Contract Period shall provide ERCOT with the following, while adhering to a schedule published by ERCOT:

(i)	The maximum MW of capacity it is willing to offer through EILS Self-Provision, per EILS Time Period; and

(ii)	A Proxy Load Ratio Share (LRS) specific to the EILS Time Period.  Proxy LRS shall be a number between zero and one and determined by the self-providing QSE to represent its estimate of its final LRS to be used in EILS Settlement.

(b)	EILS Self-Provision Capacity Upper Limit is defined as the maximum level of self-provided EILS MW capacity for which a QSE may receive credit at Settlement.  A proxy version of the EILS Self-Provision Capacity Upper Limit may be used during the procurement phase to afford self-providing QSEs the opportunity to reduce their EILS Self-Provision MW offers, if the total of their original EILS Self-Provision MW offer is projected to exceed their obligation based on their LRS, as defined in Section 6.6.11.2, EILS Capacity Charge.  After receiving EILS Self-Provision information, ERCOT will award offers for additional MWs of EILS capacity such that the sum of the following does not exceed 1,000 MW:

(i)	EILS capacity awarded through EILS competitive offers; and

(ii)	EILS capacity awarded through EILS Self-Provision offers, where for each self-providing QSE the self-provided capacity offer is the lesser of the amount offered or the QSE’s proxy EILS Self-Provision Capacity Upper Limit.

(c)	The calculations used to determine a QSE’s proxy EILS Self-Provision Capacity Upper Limit for the EILS procurement phase are the same as those used to determine the actual EILS Self-Provision Capacity Upper Limit for Settlement, as described in Section 6.6.11.1, EILS Capacity Payments, except that:

(i)	Offered EILS capacity will be substituted for delivered EILS capacity; and

(ii)	A QSE’s Proxy LRS will be substituted for its actual LRS; and

(iii)	The total of a QSE’s self-provision offers will be the lower of the offered total or 1,000 MW times the QSE’s Proxy LRS; and

(iv)	The total EILS capacity offered by QSEs through competitive offers will be no higher than 1,000 MW minus the total of all QSEs’ self-provision offers determined in item (8)(c)(iii) above.

(d)	ERCOT shall compute and provide QSEs offering EILS Self-Provision their proxy EILS Self-Provision Capacity Upper Limit.  A QSE may then reduce any or all of its self-provision offers such that its revised total EILS Self-Provision capacity is greater than or equal to its proxy EILS Self-Provision Capacity Upper Limit provided by ERCOT.

(e)	A QSE with reduced EILS Self-Provision capacity may reduce the commitment(s) of specific EILS Loads by providing Notification to ERCOT.  Such Notification must be received by ERCOT within two Business Days following ERCOT’s Notification to the QSE of its reduced obligation.

(f)	If a QSE reduces its EILS commitment according to these procedures, it will not be obligated to pay EILS charges so long as the amount of its delivered EILS Self-Provision capacity remains equal to or greater than its final LRS of the total EILS capacity delivered through offers and EILS Self-Provision, as described in paragraph (2) of Section 6.6.11.2.

(9)	ERCOT shall not procure more than $50,000,000 of EILS in any 12 month period beginning on February 1st and ending on January 31st (“EILS Cap”).  ERCOT may determine cost limits for each EILS Contract Period in order to ensure that the EILS Cap is not exceeded.  In order to minimize the cost of EILS, ERCOT may reject any offer it determines to be unreasonable or outside the parameters of an acceptable offer.  ERCOT shall establish a written process for determining the cost limits for each EILS Contract Period and for the reasonableness of offers.

(10)	ERCOT shall reduce the EILS Cap by the value of the amount of EILS Self-Provision.  ERCOT shall value EILS Self-Provision at the weighted average cost per MW of the EILS delivered multiplied by the total MW of EILS Self-Provision during each relevant EILS Time Period and EILS Contract Period.

(11)	The maximum amount of EILS for which ERCOT may contract in an EILS Contract Period is 1,000 MW for each EILS Time Period.

(12)	ERCOT shall evaluate each offer to determine the actual capacity an EILS Load is capable of providing and may limit any award to that EILS Load based on the results of the evaluation.

(13)	ERCOT shall select EILS Loads for each EILS Time Period to serve during an EILS Contract Period based upon least cost offer per MW of capacity offered based upon the payment as offered for selected EILS Loads; provided that ERCOT may consider geographic location and its effect on zonal or local congestion in selecting EILS Load.  ERCOT may prorate awards when there are more MWs available at a given price than ERCOT can procure, if acceptable to the offering QSE.  An EILS offer may declare a minimum amount of MW that the EILS Load is willing to provide and, if proration would result in an award below that amount, the offer will be excluded from the EILS procured.

(14)	QSEs representing selected EILS Loads, except for Load designated for EILS Self-Provision, will be entitled to payment as offered, subject to adjustment, pursuant to these Protocols.  Deployment of EILS Loads will not result in additional payments other than any payment received through Real-Time Energy Imbalance.

(15)	QSEs representing EILS Loads selected to provide EILS shall execute a Standard Form EILS Agreement, as provided in Section 22, Attachment G, Standard Form Emergency Interruptible Load Service (EILS) Agreement, for each committed EILS Time Period and EILS Contract Period.

(16)	An EILS Load shall be subject to a maximum of two EILS deployment events per EILS Contract Period.  Additionally, an EILS Load shall be subject to a maximum of eight hours of deployment per EILS Contract Period, unless an EILS deployment is still in effect when the eighth hour lapses, in which case the EILS Load must continue to meet its event performance requirements until ERCOT releases the EILS Load even if the deployment exceeds the eight-hour limit.

(17)	Unless ERCOT has received a notice of unavailability in a format prescribed by ERCOT, ERCOT shall assume that such a contracted EILS Load is fully available to provide EILS.

(18)	EILS Loads shall meet the following technical requirements:

(a)	Each EILS Load must have an ESI ID or other unique service identifier, as defined by ERCOT.  Each individual EILS Load must have an installed IDR or equivalent, subject to ERCOT approval, dedicated to the Load site providing EILS.  ERCOT shall analyze 15-minute interval meter data for each EILS Load for purposes of offer analysis, availability and performance measurement.  EILS Loads behind a NOIE meter point shall arrange, preferably with the NOIE TSP, to provide ERCOT with 15-minute interval meter data subject to ERCOT’s specifications and approval.  EILS Loads behind a Private Use Network’s Settlement Meter point shall provide ERCOT 15-minute interval meter data subject to ERCOT’s specifications and approval.  Notwithstanding the aforementioned, ERCOT may accept offers or self-provision offers from QSEs representing non-IDR metered aggregated EILS Loads if the QSE submits and ERCOT approves a statistically valid alternative to universal IDR metering for measurement and verification consistent with industry best practices.  ERCOT shall publish guidelines and schedules for submittal of such alternatives.

(b)	An EILS Load must be capable of meeting its performance obligations relevant to its assigned baseline methodology within ten minutes of an ERCOT Dispatch Instruction to its QSE and must be able to maintain such performance for the entire period of the deployment event and shall not return to normal operations until released to do so by ERCOT.

(c)	Any QSE representing an EILS Load must be capable of communicating with its EILS Loads within the prescribed time constraints for deployment of EILS.

(d)	QSEs are responsible for communicating material changes in the availability status of their EILS Loads to ERCOT, irrespective of whether the change in availability is scheduled with ERCOT as described in paragraph (5) of Section 8.1.3.1, Performance Criteria for EILS Loads.

(e)	An EILS Load deployed for EILS must be able to return to a condition such that it is capable of meeting its EILS performance requirements within ten hours following a release Dispatch Instruction.

(f)	EILS Loads and their QSEs are subject to qualification based on ERCOT’s evaluation of their historic meter data and, if applicable, their historic performance in providing other comparable ERCOT services.  EILS Loads and their QSEs are subject to testing requirements as described in Section 8.1.3.2, Testing of EILS Loads.

(g)	EILS Loads are not subject to the modeling, telemetry and COP requirements of other Resources.

(19)	The contracted capacity of EILS Loads may not be used to provide Ancillary Services during the contracted EILS Time Period of the contracted EILS Contract Period.  Nothing herein shall be construed to limit passive (voluntary) Load response, provided the EILS performance requirements as described in Section 8.1.3.1 are met.

(20)	ERCOT will review the effectiveness and benefits of EILS every 12 months from the start of the program and report its findings to TAC.

(21)	Prior to the start of an EILS Contract Period, ERCOT shall post on the MIS Public Area the number of MW procured per EILS Time Period, the number of EILS Loads selected, and the projected total cost of EILS for that EILS Contract Period.

(22)	The EILS obligation of QSEs representing EILS Loads, for the QSE’s portfolio, is to meet the requirements specified in Section 8.1.3.3.1, Performance Criteria for EILS QSEs.

(23)	ERCOT shall post the following documents to the MIS Certified Area:

(a)	EILS Award Notification for the upcoming Contract Period;

(b)	EILS Loads Submission Form – Approved;

(c)	EILS Load Event Performance Evaluation Results;

(d)	EILS Load Availability Summary for Contract Period;

(e)	EILS Load Shed Test Results;

(f)	EILS Pre-populated EILS Load Identification Forms;

(g)	EILS Load Group Assignments;

(h)	EILS Load Submission Form – Error Reports;

(i)	EILS Preliminary Baseline Review Results;

(j)	EILS QSE Portfolio Availability Summary for a Contract Period;

(k)	EILS QSE Portfolio Event Performance Summary for a Contract Period; and

(l)	EILS Meter Data Error Report.

(24)	At least 24 hours before an EILS Contract Period begins, ERCOT shall provide each affected Transmission and/or Distribution Provider (TDSP) with a list of EILS Loads and members of aggregated EILS Loads located in the TDSP’s service area that will be participating in EILS during the upcoming EILS Contract Period.  TDSPs shall maintain the confidentiality of this information.

[NPRR379 & 451: Replace Section 3.14.3 above as applicable with the following upon system implementation and June 1, 2012, respectively:] - 3.14.3 Emergency Response Service ERCOT shall issue Requests for Proposals to procure ERS for the purpose of promoting reliability during energy emergencies. 3.14.3.1 Emergency Response Service Procurement (1) ERCOT shall issue Requests for Proposals to procure ERS for each Standard Contract Term. The ERS Standard Contract Terms are as follows: (a) February through May; (b) June through September; and (c) October through January. (2) ERS offers shall be submitted only by QSEs capable of receiving both Extensible Markup Language (XML) messaging and Verbal Dispatch Instructions (VDIs) on behalf of represented ERS Resources. (3) An ERS Generator consisting of an aggregation of generators must be composed entirely of a single generator type: either self-serving or non-self-serving. (4) Each generator in an ERS Generator must have an interconnection agreement with its Transmission and/or Distribution Service Provider (TDSP) prior to submitting an ERS offer. (5) QSEs representing ERS Resources may submit offers for one or more ERS Time Periods within an ERS Contract Period. ERS Time Periods shall be defined by ERCOT in the Request for Proposal for that ERS Standard Contract Term. An ERS offer is specific to an ERS Time Period. In submitting an offer, both the QSE and the ERS Resource are committing to provide ERS for that ERS Time Period if selected. (6) The minimum amount of ERS that may be offered is one-tenth (0.1) MW. ERS Resources may be aggregated to reach this requirement. (7) ERCOT may establish an upper limit, in MWs, on the amount of ERS capacity it will procure for any ERS Time Period in any ERS Standard Contract Term. (8) A QSE’s offer to provide ERS shall include: (a) The name of the QSE representing the ERS Resource and the name of an individual authorized by the QSE to represent the QSE and its ERS Resource(s); (b) The name of an Entity that controls the ERS Resource, and an affirmation that the QSE has obtained written authorization from the Entity to submit ERS offers on its behalf and to represent the Entity in all matters before ERCOT concerning the Entity’s provision of ERS; (c) Any information or data specified by ERCOT, including access to historical meter data, and affirmation by the QSE that it has obtained written authorization from the controlling Entity of the ERS Resource for the QSE to obtain such data; (d) Affirmation that the controlling Entity of the ERS Resource has reviewed P.U.C. Subst. R. 25.507, Electric Reliability Council of Texas (ERCOT) Emergency Response Service (ERS), these Protocols and Other Binding Documents relating to the provision of ERS, and has agreed to comply with and be bound by such provisions; (e) An agreement by the QSE to produce any written authorization or agreement between the QSE and any ERS Resource it represents, as described in this Section, upon request from ERCOT or the PUCT; (f) Affirmation that the capacity being offered into ERS is not capacity that is separately obligated to respond during any of the same hours, and receiving a separate reservation payment for such obligation, occurring in the contracted ERS Time Period. ERCOT shall treat an ERS Resource containing sites found to be dually committed as failing to meet its ERS obligations and may prohibit participation by the ERS Resource and/or the dually committed sites in the next ERS Standard Contract Term following the discovery; (g) An affirmation that the QSE and the controlling Entity the ERS Resource are familiar with any applicable federal, state or local environmental regulations that apply to the use of any generator in the provision of ERS, and that the use of such generator(s) to provide of ERS would not violate those regulations. This provision applies to both ERS Generators and to the use of backup generation by ERS Loads; and (h) For an ERS Generator, a designation of the ERS Generator as either a self-serving generator or a non-self-serving generator, based on the performance criteria in Sections 8.1.3.1.3.2, Time Period Availability Calculations for Emergency Response Service Generators, and 8.1.3.1.4, Event Performance Criteria for Emergency Response Service Resources. (9) An ERS Standard Contract Term may consist of a single ERS Contract Period or multiple non-overlapping ERS Contract Periods, as follows: (a) If no ERS Resources’ obligations are exhausted during an ERS Contract Period pursuant to paragraph (1) of Section 3.14.3.3, Emergency Response Service Provision and Technical Requirements, the ERS Contract Period shall end at the end of the last Operating Day of the ERS Standard Contract Term. (b) If some but not all ERS Resources’ obligations are exhausted pursuant to paragraph (1) of Section 3.14.3.3 during an ERS Contract Period, that ERS Contract Period shall end at the end of the Operating Day in which the exhaustion occurred, and a new ERS Contract Period shall begin at hour ending 0100 on the following Operating Day. (c) If all ERS Resources’ obligations are exhausted pursuant to paragraph (1) of Section 3.14.3.3 during an ERS Contract Period that ERS Contract Period shall end at the end of the Operating Day in which the exhaustion occurred. In this case, ERCOT may initiate a new ERS Contract Period beginning no earlier than hour ending 0100 on the following Operating Day. (10) ERS Resources shall be obligated in ERS Contract Periods as follows: (a) For the first ERS Contract Period in an ERS Standard Contract Term, all ERS Resources awarded by ERCOT shall be obligated. (b) For any subsequent ERS Contract Periods in an ERS Standard Contract Term, any ERS Resource with remaining obligation due to cumulative deployment time of less than eight hours at the end of the last ERS Contract Period shall have their remaining obligation transferred to the new ERS Contract Period. In such a case the ERS Resource’s deployment time will be carried over from the previous ERS Contract Period and will be applied toward the maximum deployment time in the new ERS Contract Period, as described in paragraph (1) of Section 3.14.3.3. (c) For any subsequent ERS Contract Periods in an ERS Standard Contract Term, in addition to any ERS Resources that may be obligated pursuant to item (9)(b) above, any ERS Resources whose obligations were exhausted in the previous ERS Contract Period may be re-obligated at ERCOT’s discretion according to the following procedures: (i) During the offer submission process, QSEs shall designate on the ERS offer form, which is posted on the ERCOT website, whether an ERS Resource is available for mandatory participation in a subsequent ERS Contract Period (“renewal opt-in”). (ii) Prior to the start of a subsequent ERS Contract Period, ERCOT shall notify QSEs representing ERS Resources of its decision to include renewal opt-ins in the subsequent ERS Contract Period. Such Notification shall include a list of the QSEs’ renewal opt-in Resources’ capacity obligations by ERS Time Period. (iii) For purposes of managing ERS expenditures within the maximum ERS expenditure established by the PUCT (ERS Cost Cap), ERCOT may limit the obligation of renewal opt-in ERS Resources in a subsequent ERS Contract Period to a subset of the four ERS Time Periods. (iv) If ERCOT elects to include renewal opt-in ERS Resources in a subsequent ERS Contract Period, the renewal opt-ins shall be procured automatically under the same offer parameters including capacity, price, maximum base Load (if applicable), performance evaluation methodology, and ERS Time Periods as originally awarded. (v) By the end of the second Business Day in any ERS Contract Period other than the first day within an ERS Standard Contract Term, a QSE may revoke the renewal opt-in status of any of its committed ERS Resources for any subsequent ERS Contract Periods within that ERS Standard Contract Term. ERCOT shall develop a method for QSEs to communicate such information. (vi) By the end of the third Business Day in any ERS Contract Period other than the first within an ERS Standard Contract Term, ERCOT shall communicate to QSEs a confirmation of the terms of participation for all of their committed ERS Resources. Notwithstanding this provision, participation by obligated ERS Resources is binding from the start time of each ERS Contract Period. (11) In any 12-month period beginning on February 1st and ending on January 31st, ERCOT shall not commit dollars toward ERS in excess of the ERS Cost Cap. ERCOT may determine cost limits for each ERS Contract Period in order to ensure that the ERS Cost Cap is not exceeded. In order to minimize the cost of ERS, ERCOT may reject any offer it determines to be unreasonable or outside the parameters of an acceptable offer. ERCOT shall establish a written process for determining the cost limits for each ERS Contract Period and for the reasonableness of offers. (12) ERCOT shall reduce the ERS Cost Cap by the value of the amount of ERS Self-Provision. ERCOT shall value ERS Self-Provision at the weighted average cost per MW of each QSE’s ERS Self-Provision obligation multiplied by the total MW of ERS Self-Provision during each relevant ERS Time Period and ERS Contract Period. (13) ERCOT shall evaluate each offer to determine whether it comports with the actual capacity an ERS Resource is capable of providing and may limit any award to that ERS Resource based on the results of the evaluation. (14) For the first ERS Contract Period in an ERS Standard Contract Term, ERCOT shall select ERS Resources for each ERS Time Period based upon least cost offer per MW of capacity offered, provided that ERCOT may consider geographic location and its effect on congestion in making ERS awards. ERCOT may prorate awards when there are more MWs available at a given price than ERCOT decides to procure, if the proration is acceptable to each offering QSE. An ERS offer may declare a minimum amount of MW that the ERS Resource is willing to provide. If proration would result in an award below an ERS Resource’s designated minimum, the offer will not be awarded. (15) Payments and Self-Provision credits to QSEs representing ERS Resources are subject to adjustments as described in Section 8.1.3.3.1, Performance Criteria for Qualified Scheduling Entities Representing Emergency Response Service Resources. Deployment of ERS Resources will not result in additional payments other than any payment for which the QSE may be eligible through Real-Time energy imbalance or other ERCOT settlement process. (16) QSEs representing ERS Resources selected to provide ERS shall execute a Standard Form Emergency Response Service Agreement, as provided in Section 22, Attachment G, Standard Form Emergency Response Service Agreement. 3.14.3.2 Emergency Response Service Self-Provision (1) QSEs may self-provide ERS. QSE’s shall offer all self-provided ERS capacity at a price of $0. A QSE electing to self-provide all or part of its ERS obligation shall provide ERCOT with the following, while adhering to a schedule published by ERCOT: (a) The maximum MW of capacity the QSE is willing to offer through ERS Self-Provision for each ERS Time Period; and (b) A proxy Load Ratio Share (LRS) specific to the ERS Time Period. Proxy LRS shall be a number between zero and one and determined by the self-providing QSE to represent its estimate of its final LRS to be used in ERS Settlement. (2) ERS Self-Provision Capacity Upper Limit is defined as the maximum level of self-provided ERS MW capacity for which a QSE may receive credit at Settlement. During the procurement process, a QSE may elect to use a proxy ERS Self-Provision Capacity Upper Limit (based on the proxy LRS it submitted) to reduce its ERS Self-Provision MW. After receiving ERS Self-Provision information, ERCOT will award offers for additional MWs of ERS capacity such that the sum of the following does not exceed the total amount of ERS capacity intends to procure in any one ERS Time Period: (a) ERS capacity awarded through ERS competitive offers; and (b) ERS capacity awarded through ERS Self-Provision offers, where for each self-providing QSE the self-provided capacity offer is the lesser of the amount offered or the QSE’s proxy ERS Self-Provision Capacity Upper Limit. (3) The calculations used to determine a QSE’s proxy ERS Self-Provision Capacity Upper Limit for the ERS procurement phase are the same as those used to determine the actual ERS Self-Provision Capacity Upper Limit for Settlement, as described in Section 6.6.11.1, Emergency Response Service Capacity Payments, except that: (a) Offered ERS capacity is substituted for delivered ERS capacity; and (b) A QSE’s proxy LRS is substituted for its actual LRS. (4) ERCOT shall compute and provide QSEs offering ERS Self-Provision their proxy ERS Self-Provision Capacity Upper Limit. A QSE may then reduce any or all of its self-provision offers such that its revised total ERS Self-Provision capacity is greater than or equal to its proxy ERS Self-Provision Capacity Upper Limit provided by ERCOT. (5) A QSE with reduced ERS Self-Provision capacity shall notify ERCOT of the ERS Resources whose obligations are reduced and the quantity of the revised obligations. The QSE must provide this information to ERCOT within two Business Days of receiving Notice of the reduced obligation. (6) If a QSE reduces its ERS commitment according to these procedures, it will not be obligated to pay ERS charges so long as the ERS Self-Provision capacity it delivers is equal to or greater than its final LRS of the total ERS capacity delivered through offers and ERS Self-Provision, as described in paragraph (2) of Section 6.6.11.2, Emergency Response Service Capacity Charge. (7) A QSE opting for ERS Self-Provision may also offer separate capacity into ERS in the form of a priced offer in the same manner as any other QSE. (8) The capacity obligation of a self-provided ERS Resource that is designated as a renewal opt-in, as described in paragraph (10) of Section 3.14.3.1, Emergency Response Service Procurement, will be fixed at the original awarded MW level for any subsequent ERS Contract Periods in the ERS Standard Contract Term. 3.14.3.3 Emergency Response Service Provision and Technical Requirements (1) An ERS Resource shall be subject to a maximum of eight hours of deployment per ERS Contract Period, unless the ERS Resource is carrying over hours of deployment time from the previous ERS Contract Period within the Standard Contract Term as described in paragraph (10)(b) of Section 3.14.3.1, Emergency Response Service Procurement. In the latter case, the ERS Resource’s maximum hours of deployment in the new ERS Contract Period will be eight hours minus the deployment time carried over from the prior ERS Contract Period. Notwithstanding this provision, if an ERS deployment is still in effect when the ERS Resource’s maximum deployment time is equaled or exceeded, the ERS Resource must continue to meet its event performance requirements until ERCOT releases the ERS Resource even if the deployment exceeds the limit. (2) Unless ERCOT has received a notice of unavailability in a format prescribed by ERCOT, ERCOT shall assume that a contracted ERS Resource is fully available to provide ERS. (3) QSEs and ERS Resources they represent shall meet the following technical requirements: (a) Each ERS Resource, including each member of an aggregated ERS Resource, must have an Electric Service Identifier (ESI ID) and dedicated metering, as defined by ERCOT. An ERS Resource located outside of a competitive service area may use a unique service identifier in lieu of an ESI ID. ERCOT shall analyze 15-minute interval meter data for each ERS Resource for purposes of offer analysis, availability and performance measurement. ERS Resources behind a Non-Opt-In Entity (NOIE) meter point shall arrange, preferably with the NOIE TDSP, to provide ERCOT with 15-minute interval meter data subject to ERCOT’s specifications and approval. ERS Resources behind a Private Use Network’s Settlement Meter point shall provide ERCOT 15-minute interval meter data subject to ERCOT’s specifications and approval. All generators in an ERS Generator must have TDSP metering capable of measuring energy exported to the ERCOT System and TDSP metering capable of measuring energy imported from the ERCOT System. (b) An ERS Resource must be capable of meeting its event performance obligations relevant to its assigned performance evaluation methodology within ten minutes of an ERCOT Dispatch Instruction to its QSE, must be able to maintain such performance for the entire Sustained Response Period. An ERS Resource shall not return to normal operations until released to do so by ERCOT. (c) A QSE must be capable of communicating with its ERS Resources in sufficient time to ensure deployment within ten minutes. (d) QSEs shall communicate to ERCOT, in a method prescribed by ERCOT, material changes in the availability status of their ERS Resources. (e) An ERS Resource deployed for ERS must be able to return to a condition such that it is capable of meeting its ERS performance requirements within ten hours following a release Dispatch Instruction. (f) ERS Resources and their QSEs are subject to qualification based on ERCOT’s evaluation of their historical meter data and, if applicable, their historic performance in providing other comparable ERCOT services. ERS Resources and their QSEs are subject to testing requirements as described in Section 8.1.3.2, Testing of Emergency Response Service Resources. (g) ERS Resources are not subject to the modeling, telemetry and COP requirements of other Resources. (4) The contracted capacity of ERS Resources may not be used to provide Ancillary Services during a contracted ERS Time Period. Nothing herein shall be construed to limit passive (voluntary) Load response, provided the ERS Resource meets its performance and availability requirements, as described in Section 8.1.3.1, Performance Criteria for Emergency Response Service Resources. (5) QSEs representing ERS Resources must meet the requirements specified in Section 8.1.3.3.1, Performance Criteria for Qualified Scheduling Entities Representing Emergency Response Service Resource. 3.14.3.4 Emergency Response Service Reporting and Market Communications (1) ERCOT shall review the effectiveness and benefits of ERS every 12 months from the start of the program and report its findings to TAC no later than April 15 of each calendar year. (2) Prior to the start of the first ERS Contract Period in an ERS Standard Contract Term, and no later than the end of the third Business Day following the start of any subsequent ERS Contract Period in an ERS Standard Contract Term, ERCOT shall post on the MIS Public Area the number of MW procured per ERS Time Period, the number and type of ERS Resources selected, and the projected total cost of ERS for that ERS Contract Period. (3) ERCOT shall post the following documents to the MIS Certified Area: (a) ERS Award Notification; (b) ERS Resources Submission Form – Approved; (c) ERS Resource Event Performance Evaluation Results; (d) ERS Resource Availability Summary for Contract Period; (e) ERS Test Portfolio Designation Notification; (f) ERS Resource Test Results; (g) ERS Pre-populated ERS Resource Identification Forms; (h) ERS Resource Group Assignments; (i) ERS Resource Submission Form – Error Reports; (j) ERS Preliminary Baseline Review Results; (k) ERS QSE Portfolio Availability Summary for a Contract Period; (l) ERS QSE Portfolio Event Performance Summary for a Contract Period; and (m) ERS Meter Data Error Report. (4) At least 24 hours before an ERS Contract Period begins, ERCOT shall provide each affected TDSP with: (a) A list of ERS Resources and members of aggregated ERS Resources located in the TDSP’s service area that will be participating in ERS during the upcoming ERS Contract Period; (b) The name of the QSE representing each ERS Resource; (c) All applicable ESI IDs associated with each ERS Resource; and (d) The date(s) of the interconnection agreement(s) for each generator in any ERS Generator. (5) TDSPs shall maintain the confidentiality of the information provided pursuant to paragraph (4) above.

3.15	Voltage Support

(1)	ERCOT in coordination with the Transmission Service Providers (TSPs) shall establish and update, as necessary, the ERCOT System Voltage Profile for all Electrical Buses used for Voltage Support in the ERCOT System and shall post all Voltage Profiles on the Market Information System (MIS) Secure Area.  ERCOT may temporarily modify its requirements based on current system conditions.

(2)	All Generation Resources (including self-serve generating units) that have a gross generating unit rating greater than 20 MVA or those units connected at the same Point of Interconnection (POI) that have gross generating unit ratings aggregating to greater than 20 MVA, that supply power to the ERCOT Transmission Grid, shall provide Voltage Support Service (VSS).

(3)	Generation Resources required to provide VSS must be capable of producing a defined quantity of Reactive Power to maintain a Voltage Profile established by ERCOT. Generation Resources shall comply with the following Reactive Power Requirements:  an over-excited (lagging) power factor capability of 0.95 or less and an under-excited (leading) power factor capability of 0.95 or less, both determined at the generating unit's maximum net power to be supplied to the ERCOT Transmission Grid and at the transmission system Voltage Profile established by ERCOT, and both measured at the POI.  The Reactive Power requirements shall be available at all MW output levels and may be met through a combination of the Generation Resource’s Unit Reactive Limit (URL), which is the generating unit’s dynamic leading and lagging operating capability, and/or dynamic VAr capable devices.  This Reactive Power profile is depicted graphically as a rectangle.  For Intermittent Renewable Resources (IRRs), the Reactive Power requirements shall be available at all MW output levels at or above 10% of the IRR’s nameplate capacity.  When an IRR is operating below 10% of its nameplate capacity and is unable to support voltage at the POI, ERCOT may require an IRR to disconnect from the ERCOT System for purposes of maintaining reliability.  As part of the technical Resource requirements to begin commercial operations, all Generation Resources must conduct an engineering study, or demonstrate through performance testing, compliance with the Reactive Power capability requirements of this paragraph.  Any study or testing results must be accepted by ERCOT prior to commercial operations.  The Reactive Power requirements of this paragraph shall apply to all Generation Resources except as otherwise provided in paragraphs (4) through (6) below.

(4)	Wind-powered Generation Resources (WGRs) that commenced operation on or after February 17, 2004, and have a signed Standard Generation Interconnection Agreement (SGIA) on or before December 1, 2009 (“Existing Non-Exempt WGRs”), must be capable of producing a defined quantity of Reactive Power to maintain a Voltage Profile established by ERCOT in accordance with the Reactive Power requirements established in paragraph (3) above, except in the circumstances described in paragraph (a) below.

(a)	Existing Non-Exempt WGRs whose current design does not allow them to meet the Reactive Power requirements established in paragraph (3) above must conduct an engineering study using the Summer/Fall 2010 on-peak/off-peak Voltage Profiles, or conduct performance testing to determine their actual Reactive Power capability.  Any study or testing results must be accepted by ERCOT.  The Reactive Power requirements applicable to these Existing Non-Exempt WGRs will be the greater of: (i) the leading and lagging Reactive Power capabilities established by the Existing Non-Exempt WGR’s engineering study or testing results; or (ii) Reactive Power proportional to the real power output of the Existing Non-Exempt WGR (this Reactive Power profile is depicted graphically as a triangle) sufficient to provide an over-excited (lagging) power factor capability of 0.95 or less and an under-excited (leading) power factor capability of 0.95 or less, both determined at the transmission system Voltage Profile established by ERCOT, and both measured at the POI.

(i)	Existing Non-Exempt WGRs shall submit the engineering study results or testing results to ERCOT no later than five Business Days after its completion;

(ii)	Existing Non-Exempt WGRs shall update any and all Resource registration information regarding their Reactive Power capability documented by the engineering study results or testing results;

(iii)	If the Existing Non-Exempt WGR’s engineering study results or testing results indicate that the WGR is not able to provide Reactive Power capability that meets the triangle profile described in paragraph (4)(a) above, then the Existing Non-Exempt WGR will take steps necessary to meet that Reactive Power requirement depicted graphically as a triangle by a date mutually agreed upon by the Existing Non-Exempt WGR and ERCOT.  The Existing Non-Exempt WGR may meet the Reactive Power requirement through a combination of the WGR’s URL and/or automatically switchable static VAr capable devices and/or dynamic VAr capable devices.  No later than five Business Days after completion of the steps to meet that Reactive Power requirement, the Existing Non-Exempt WGR will update any and all Resource registration information regarding its Reactive Power and provide written notice to ERCOT that it has completed the steps necessary to meet its Reactive Power requirement.

(iv)	For purposes of measuring future compliance with Reactive Power requirements for Existing Non-Exempt WGRs, results from performance testing or the Summer/Fall 2010 on-peak/off-peak Voltage Profiles utilized in the Existing Non-Exempt WGR’s engineering study shall be the basis for measuring compliance, even if the Voltage Profiles provided to the Existing Non-Exempt WGR are revised for other purposes.

(b)	Existing Non-Exempt WGRs whose current design allows them to meet the Reactive Power requirements established in paragraph (3) above (depicted graphically as a rectangle) shall continue to comply with that requirement.  ERCOT, with cause, may request that these Existing Non-Exempt WGRs provide further evidence, including an engineering study, or performance testing, to confirm accuracy of Resource registration information supporting their Reactive Power capability.

(5)	Qualified Renewable Generation Resources (as described in Section 14, State of Texas Renewable Energy Credit Trading Program) in operation before February 17, 2004, required to provide VSS and all other Generation Resources required to provide VSS that were in operation prior to September 1, 1999, whose current design does not allow them to meet the Reactive Power requirements established in paragraph (3) above, will be required to maintain a Reactive Power requirement as defined by the Generation Resource’s URL that was submitted to ERCOT and established per the criteria in the ERCOT Operating Guides.

(6)	New generating units connected before May 17, 2005, whose owners demonstrate to ERCOT’s satisfaction that design and/or equipment procurement decisions were made prior to February 17, 2004, based upon previous standards, whose design does not allow them to meet the Reactive Power requirements established in paragraph (3) above, will be required to maintain a Reactive Power requirement as defined by the Generation Resource’s URL that was submitted to ERCOT and established per the criteria in the ERCOT Operating Guides.

(7)	For purposes of meeting the Reactive Power requirements in paragraphs (3) and (4) above, multiple generation units including wind turbines shall, at a Generation Entity’s option, be treated as a single Generation Resource or WGR if the units are connected to the same transmission bus.

(8)	Generation Entities may submit to ERCOT specific proposals to meet the Reactive Power requirements established in paragraph (3) above by employing a combination of the URL and added VAr capability, provided that the added VAr capability shall be automatically switchable static and/or dynamic VAr devices.  A Generation Resource and TSP may enter into an agreement in which the proposed static VAr devices can be switchable using Supervisory Control and Data Acquisition (SCADA).  ERCOT may, at its sole discretion, either approve or deny a specific proposal, provided that in either case, ERCOT shall provide the submitter an explanation of its decision.

(9)	A Generation Resource and TSP may enter into an agreement in which the Generation Resource compensates the TSP to provide VSS to meet the Reactive Power requirements of paragraph (3) above in part or in whole.  The TSP shall certify to ERCOT that the agreement complies with the Reactive Power requirements of paragraph (3).

(10)	Unless specifically approved by ERCOT, no unit equipment replacement or modification at a Generation Resource shall reduce the capability of the unit below the Reactive Power requirements that applied prior to the replacement or modification.

(11)	Generation Resources shall not reduce high reactive loading on individual units during abnormal conditions without the consent of ERCOT unless equipment damage is imminent.

(12)	WGRs must provide a Real-Time SCADA point that communicates to ERCOT the number of wind turbines that are available for real power and/or Reactive Power injection into the ERCOT Transmission Grid.  WGRs must also provide two other Real Time SCADA points that communicate to ERCOT the following:

(a)	The number of wind turbines that are not able to communicate and whose status is unknown; and

(b)	The number of wind turbines out of service and not available for operation.

WGRs must comply with the requirements of paragraph (12) by no later than June 1, 2010.

(13)	For the purpose of complying with the Reactive Power requirements under this Section, Reactive Power losses that occur on privately-owned transmission lines behind the POI may be compensated by automatically switchable static VAr capable devices.

3.15.1	ERCOT Responsibilities Related to Voltage Support

(1)	ERCOT, in coordination with the TSPs, shall establish, and update as necessary, Voltage Profiles at POI of Generation Resources required to provide VSS to maintain system voltages within established limits.

(2)	ERCOT shall communicate to the Qualified Scheduling Entity (QSE) and TSPs the desired voltage at the point of generation interconnection by providing Voltage Profiles.

(3)	ERCOT, in coordination with TSPs, shall deploy static Reactive Power Resources as required to continuously maintain dynamic reactive reserves from QSEs, both leading and lagging, adequate to meet ERCOT System requirements.

(4)	For any Market Participant’s failure to meet the Reactive Power voltage control requirements of these Protocols, ERCOT shall notify the Market Participant in writing of such failure and, upon a request from the Market Participant, explain whether and why the failure must be corrected.

(5)	ERCOT shall notify all affected TSPs of any alternative requirements it approves.

(6)	Annually, ERCOT shall review Distribution Service Provider (DSP) power factors using the actual summer Load and power factor information included in the annual Load data request to assess whether DSPs comply with the requirements of this subsection.  At times selected by ERCOT, ERCOT shall require manual power factor measurement at substations and POIs that do not have power factor metering.  ERCOT shall try to provide DSPs sufficient notice to perform the manual measurements.  ERCOT may not request more than four measurements per calendar year for each DSP substation or POI where power factor measurements are not available.

(7)	If actual conditions indicate probable non-compliance of TSPs and DSPs with the requirements to provide voltage support, ERCOT shall require power factor measurements at the time of its choice while providing sufficient notice to perform the measurements.

(8)	ERCOT shall investigate claims of TSP and DSP alleged non-compliance with Voltage Support requirements. The ERCOT investigator shall advise ERCOT and TSP planning and operating staffs of the results of such investigations.

3.15.2	DSP Responsibilities Related to Voltage Support

Each DSP and Resource Entity within a Private Use Network shall meet the requirements specified in this subsection, or at their option, may meet alternative requirements specifically approved by ERCOT.  Such alternative requirements may include requirements for aggregated groups of Facilities.

(a)	Sufficient static Reactive Power capability shall be installed by a DSP or a Resource Entity within a Private Use Network not subject to a DSP tariff in substations and on the distribution voltage system to maintain at least a 0.97 lagging power factor for the maximum net active power measured in aggregate on the distribution voltage system.  In those cases where a Private Use Network’s power factor is established and governed by a DSP tariff, a Resource Entity within a Private Use Network shall ensure that the Private Use Network meets the requirements as defined and measured in the applicable tariff.

(b)	DSP substations whose annual peak Load has exceeded ten MW shall have and maintain Watt/VAr metering sufficient to monitor compliance; otherwise, DSPs are not required to install additional metering to determine compliance.

(c)	All DSPs shall report any changes in their estimated net impact on ERCOT as part of the annual Load data assessment.

(d)	As part of the annual Load data assessment, all Resource Entities owning Generation Resources shall provide an annual estimate of the highest potential affiliated MW and MVAr Load (including any Load netted with the generation output) and the highest potential MW and MVAr generation that could be experienced at the POI to the ERCOT Transmission Grid, based on the current configuration (and the projected configuration if the configuration is going to change during the year) of the Generation Resource and any affiliated Loads.

3.15.3	QSE Responsibilities Related to Voltage Support

(1)	QSE Generation Resources required to provide VSS shall have and maintain Reactive Power capability at least equal to the Reactive Power capability requirements specified in these Protocols and the ERCOT Operating Guides.

(2)	QSE Generation Resources providing VSS shall be compliant with the ERCOT Operating Guides for response to transient voltage disturbance.

(3)	QSE Generation Resources providing VSS must meet technical requirements specified in Section 8.1.1.1, Ancillary Service Qualification and Testing, and the performance standards specified in Section 8.1.1, QSE Ancillary Service Performance Standards.

(4)	Each QSE’s Generation Resource providing VSS shall operate with the unit’s Automatic Voltage Regulator (AVR) in the voltage control mode unless specifically directed to operate in manual mode by ERCOT, or when the unit is going On-Line or Off-Line or the QSE determines a need to operate in manual mode in the event of an Emergency Condition at the generating plant.  Each QSE shall send to ERCOT via telemetry, the AVR and Power System Stabilizer (PSS) status of each Generation Resource providing VSS.  For AVRs, an “On” status will indicate the AVR is on and set to regulate the Resource’s terminal voltage in the voltage control mode, and an “Off” status will indicate the AVR is off or in a manual mode.  Each QSE shall monitor the status of their regulators and stabilizers, and shall report abnormal status changes to ERCOT.

(5)	Each QSE shall meet, within established tolerances, and respond to changes in the Voltage Profile established by ERCOT subject to the stated QSE Reactive Power and actual power operating characteristic limits and voltage limits.

(6)	The reactive capability required must be maintained at all times that the Generation Resource is On-Line.

(7)	ERCOT shall post the information required under item (1) (b) of Section 1.3.1.2, Items Not Considered Protected Information, regarding the existence and status of any PSS of each interconnected Generation Resource on the MIS Secure Area.  Each Resource Entity shall provide information related to the tuning parameters, local or inter-area, of any PSS installed at a Generation Resource.

3.16	Standards for Determining Ancillary Service Quantities

(1)	ERCOT shall comply with the requirements for determining Ancillary Service quantities as specified in these Protocols and the ERCOT Operating Guides.

(2)	ERCOT shall, at least annually, determine with supporting data, the methodology for determining the minimum quantity requirements for each Ancillary Service needed for reliability, including the percentage of Load Resources excluding Controllable Load Resources, the percentage of Direct Current (DC) Tie, and the percentage of Controllable Load Resources allowed to provide Responsive Reserve (RRS) Service calculated on a monthly basis.

(3)	The ERCOT Board shall review and approve ERCOT's methodology for determining the minimum Ancillary Service requirements and the monthly percentage of Load Resources, Controllable Load Resources and DC Ties allowed to provide RRS.

(4)	If ERCOT determines a need for additional Ancillary Service Resources under these Protocols or the ERCOT Operating Guides, after an Ancillary Service Plan for a specified day has been posted, ERCOT shall inform the market by posting notice on the Market Information System (MIS) Secure Area, of ERCOT’s intent to procure additional Ancillary Service Resources under Section 6.4.8.2, Supplemental Ancillary Service Market.  ERCOT shall post the reliability reason for the increase in service requirements.

(5)	ERCOT shall post engineering studies on the MIS Secure Area representing specific Ancillary Service requirement on an annual basis.

(6)	The amount of Load Resources on high-set under-frequency relays providing RRS is limited to 50% of the total ERCOT RRS requirement.  ERCOT may reduce this limit if it believes that this amount will have a negative impact on reliability or if this limit would require additional regulation to be deployed.

(7)	The amount of RRS that a Qualified Scheduling Entity (QSE) can self-arrange using a Load Resource excluding Controllable Load Resources is limited to the lower of:

(a)	fifty percent (50%) of its RRS Obligation, or

(b)	a reduced percentage of its RRS Obligation based on the limit established by ERCOT in paragraph (6) above.

(8)	However, a QSE may bid more of the Load Resource above the percentage limit established by ERCOT for sale of RRS to other Market Participants.  The total amount of RRS Service using the Load Resource excluding Controllable Load Resources procured by ERCOT is also limited to the lesser of the 50% limit or the limit established by ERCOT in paragraph (6) above.

[NPRR434: Insert paragraph (9) below upon system implementation:] (9) ERCOT shall update the RRS threshold %, defined in paragraph (3)(a) in Section 3.18, Resource Limits in Providing Ancillary Service, in the event that the total amount of RRS procured changes. RRS must have minimum of 1150 MW of Primary Frequency Response which is maintained by Generation Resources capable of responding with a 5% droop for a 1% change in frequency.

3.17	Ancillary Service Capacity Products

3.17.1	Regulation Service

(1)	Regulation Up Service (Reg-Up) is a service that provides capacity that can respond to signals from ERCOT within three to five seconds to respond to changes from scheduled system frequency.  The amount of Reg-Up capacity is the amount of capacity available from a Resource that may be called on to change output as necessary to maintain proper system frequency. A Generation Resource providing Reg-Up must be able to increase energy output when deployed and decrease energy output when recalled.  A Load Resource providing Reg-Up must be able to decrease Load when deployed and increase Load when recalled.

(2)	Regulation Down Service (Reg-Down) is a service that provides capacity that can respond to signals from ERCOT within three to five seconds to respond to changes from scheduled system frequency.  The amount of Reg-Down capacity is the amount of capacity available from a Resource that may be called on to change output as necessary to maintain proper system frequency.  A Generation Resource providing Reg-Down must be able to decrease energy output when deployed and increase energy output when recalled. A Load Resource providing Reg-Down must be able to increase Load when deployed and decrease Load when recalled.

3.17.2	Responsive Reserve Service

(1)	Responsive Reserve (RRS) Service is a service used to restore or maintain the frequency of the ERCOT System:

(a)	In response to, or to prevent, significant frequency deviations;

(b)	As backup Regulation Service; and

(c)	By providing energy during an Energy Emergency Alert (EEA).

(2)	RRS may be provided through one or more of the following means:

(a)	By using frequency-dependent response from On-Line Resources as prescribed in the Operating Guides to help restore the frequency within the first few seconds of an event that causes a significant frequency deviation in the ERCOT System; and

(b)	Either manually or by using a four-second signal to provide energy on deployment by ERCOT.

(3)	RRS Service may be used to provide energy during the implementation of an EEA.  Under the EEA, RRS provides generation capacity, capacity from Controllable Load Resources or interruptible Load available for deployment on ten minutes’ notice.

(4)	Responsive Reserve (RRS) Service may be provided by:

(a)	Unloaded, On-Line Generation Resource capacity;

(b)	Load Resources controlled by high-set, under-frequency relays;

(c)	Controllable Load Resources;

(d)	Hydro Responsive Reserves as defined in the Operating Guides; and

(e)	Direct Current Tie (DC Tie) response that stops frequency decay as defined in the Operating Guides.

3.17.3	Non-Spinning Reserve Service

(1)	Non-Spinning Reserve Service (Non-Spin) is provided by using:

(a)	Generation Resources, whether On-Line or Off-Line, capable of:

(i)	being synchronized and ramped to a specified output level within 30 minutes; and

(ii)	running at a specified output level for at least one hour; or

(b)	Load Resources capable of:

(i)	being interrupted within 30 minutes; and

(ii)	remaining interrupted for at least one hour.

(2)	The Non-Spin may be deployed by ERCOT to increase available reserves in Real-Time Operations.

3.18	Resource Limits in Providing Ancillary Service

(1)	For both Generation Resources and Load Resources the High Sustained Limit (HSL) must be greater than or equal to the Low Sustained Limit (LSL) and the sum of the Resource-specific designation of capacity to provide Responsive Reserve (RRS), Regulation Up (Reg-Up), Regulation Down (Reg-Down), and Non-Spinning Reserve (Non-Spin).

(2)	For Non-Spin, the amount of Non-Spin provided must be less than or equal to the HSL for Off-Line Generation Resources.

(3)	For RRS Service:

(a)	The amount of RRS provided from a Generation Resource must be less than or equal to 20% of thermal unit HSL for an Ancillary Service Offer and must be less than or equal to ten times the Emergency Ramp Rate;

[NPRR434: Replace item (3)(a) above with the following upon system implementation:] (a) The full amount of RRS provided from a Generation Resource must be less than or equal to 24% of thermal unit HSL for an Ancillary Service Offer, must be less than or equal to ten times the Emergency Ramp Rate, and must be frequency responsive;

(b)	Hydro Generation Resources operating in the synchronous condenser fast-response mode may provide RRS up to the hydro Generation Resource’s proven 20-second response capability (which may be 100% of the HSL).  The initiation setting of the automatic under-frequency relay setting shall not be lower than 59.80 Hz;

(c)	For any hydro Generation Resource with a 5% droop setting operating as a generator, the amount of RRS provided may never be more than 20% of the HSL; and

[NPRR434: Replace item (3)(c) above with the following upon system implementation:] (c) For any hydro Generation Resource with a 5% droop setting operating as a generator, the amount of RRS provided may never be more than 24% of the HSL; and

(d)	The amount of RRS provided from a Load Resource must be less than or equal to the HSL minus the sum of the LSL, Reg-Up Resource Responsibility, Reg-Down Resource Responsibility, and Non-Spin Resource Responsibility.

3.19	Constraint Competitiveness Tests

(1)	Unless the Board approves changes, the “Competitive Constraints” are the contingency/limiting Transmission Element pairs that represent the Commercially Significant Constraints (CSCs) and Closely Related Elements (CREs), as those terms were defined in the ERCOT Protocols, immediately prior to Texas Nodal Market Implementation Date. The ERCOT Board may approve changes to the Competitive Constraints from time to time, whether before the Texas Nodal Market Implementation Date or after.  A contingency/limiting Transmission Element pair is designated a Competitive Constraint by Technical Advisory Committee (TAC) approval.  Among other relevant factors, TAC shall consider the results of the Test Procedures 1 and 2, as described in Section 3.19.1, Annual Competitiveness Test, in reaching its determination as to whether or not a Transmission Element pair should be considered as a Competitive Constraint.  Any contingency/limiting Transmission Element pair not designated as a Competitive Constraint is deemed to be a non-competitive constraint.  Notwithstanding the foregoing, as described in Section 4.4.11.2, Scarcity Pricing and Mitigated Offer Cap During Nodal Startup, for the first 45 Operating Days beginning with the Texas Nodal Market Implementation Date, all TAC approved Competitive Constraints will each be deemed to be a non-Competitive Constraint.

(2)	An appropriate subcommittee approved by TAC (“TAC Subcommittee”) may develop an alternative list through the analysis described below for determining Competitive Constraints.

(3)	The TAC Subcommittee shall perform the following analysis with the goal of developing an objective standard for determining Competitive Constraints:

(a)	Contingency analysis – based on reasonable generation dispatch that would lead into a set of elements to be studied.

(b)	Constraint Competitiveness Test (CCT) - using the parameters described in Section 3.19.1, Annual Competitiveness Test; Section 3.19.2, Monthly Competitiveness Test; and Section 3.19.3, Daily Competitiveness Test.

(c)	Initial analysis of the CSCs and CREs and additional proposed contingency/limiting Transmission Element pairs for possible modifications or designation to their status as a Competitive Constraint must be completed prior to the Texas Nodal Market Implementation Date and subsequent analysis shall be on-going.

(d)	At a minimum, the CCT should be performed at least once per month and the results compared to the existing TAC-approved Competitive Constraints list.  Based on the comparison, the TAC Subcommittee may evaluate alternative methodologies or alternative Competitive Constraints and report the results of these evaluations to the TAC.

(4)	The Independent Market Monitor (IMM) may suspend a Competitive Constraint from being designated as competitive for a specified period of time necessary to allow for analysis, but not to exceed 60 days.  The IMM shall notify the market of the estimated time needed to conduct the analysis.  The IMM shall notify the market of any suspended Competitive Constraint before suspension.

(5)	TAC shall approve the Competitive Constraints one month prior to the annual Congestion Revenue Right (CRR) Auction.  Prior to each monthly CRR Auction, TAC shall approve updates to the Competitive Constraints that are applicable for the following monthly auction.  Any Competitive Constraint not determined to be competitive by TAC shall be deemed to be non-competitive.

(6)	ERCOT shall post the Competitive Constraints to the Market Information System (MIS) Secure Area at least five Business Days before any change takes effect. ERCOT shall post any Competitive Constraints that have been suspended and the duration of the suspension as soon as practicable to the MIS Secure Area.

3.19.1	Annual Competitiveness Test

(1)	The procedures for an Annual Competitiveness Test for any constrained Transmission Element during a particular month are described in this Section.  In these descriptions, “Available Capacity” for a Resource is defined as:

(a)	The High Sustained Limit (HSL) of a Generation Resource, including a Switchable Generation Resource that is not on a Planned Outage for the month (except wind powered generation); or

(b)	For wind generation, the expected on-peak wind generation output; or

(c)	The full import capability of the Direct Current Tie (DC Tie) lines.

(2)	Test Procedure 1 – Determine if there is sufficient competition to resolve the constraint on the import and export side by performing the following steps:

(a)	Determine the effective capacity available to resolve the constraint on the import side, as follows:

(i)	Determine Shift Factors of all Electrical Buses relative to the import terminal of the constraint as the reference Electrical Bus for the monthly peak case used to auction on-peak CRRs.  The monthly peak case must include planned transmission and generation Outages for the month.  For voltage, stability, and thermal-limited constraints, as well as interfaces represented by thermal limits on monitored Transmission Elements, the “Base Shift Factors,” which are the Shift Factors used from the monthly peak case with no other contingencies included, must be used.  For contingency-limited constraints, the Outage Shift Factors relative to the import terminal of the limiting Transmission Element must be used.

(ii)	Determine the effective Load on the export side by multiplying all Load at Electrical Buses by the corresponding Electrical Bus Shift Factors identified in step (a)(i).

(iii)	Determine the effective capacity needed to meet Load and to supply power over the constraint on the export side by:

(A)	multiplying all Available Capacity at Electrical Buses by the corresponding Shift Factor from step (a)(i);

(B)	stacking the effective capacity in decreasing Shift Factor order; and then

(C)	selecting the sufficient effective capacity from the stack to meet the effective Load plus the flow limit on the constraint.  These Resources shall not be considered in determining effective Available Capacity to resolve the constraint on the import side.

(iv)	Determine the absolute value of Shift Factors of all Electrical Buses relative to the export terminal of the constraint as the reference Electrical Bus.

(v)	Determine the effective capacity to resolve the constraint on the import side taking the sum of the products determined by multiplying, for each Resource not excluded in step (a)(iii) and having Shift Factors greater than one-third of the highest Resource Shift Factor, (A) the Available Capacity for that Resource times (B) the Shift Factor of that Resource.

(b)	Determine the effective capacity available to resolve the constraint on the export side, as follows:

(i)	Determine the absolute value of Shift Factors of all Electrical Buses relative to the export terminal of the constraint as the reference Electrical Bus.

(ii)	Determine the effective Load on the import side by multiplying all Load at Electrical Buses by the corresponding Electrical Bus Shift Factors from step (b)(i).

(iii)	Determine the effective capacity needed to meet Load less imported power over the constraint on the import side by:

(A)	multiplying all Available Capacity at Electrical Buses by the corresponding Shift Factor from step (b)(i);

(B)	stacking the effective capacity in decreasing Shift Factor order; and then

(C)	selecting the sufficient effective capacity from the stack to meet the effective Load minus the flow limit on the constraint.  These Resources are not considered in determining effective capacity available to resolve the constraint on the export side.

(iv)	Determine the Shift Factors of all Electrical Buses relative to the export terminal of the constraint as the reference Electrical Bus.

(v)	Determine the effective capacity to resolve the constraint on the export side taking the sum of the products determined by multiplying, for each Resource not excluded in step (b)(iii) and having Shift Factors greater than one-third of the highest Resource Shift Factor, (A) the Available Capacity for that Resource times (B) the Shift Factor of that Resource.

(c)	Determine the Element Competitiveness Index (ECI) on the import and export side of the constraint for the month, as follows:

(i)	Determine the total Managed Capacity by each Entity and its Affiliates on the import and export side.  “Managed Capacity” for an Entity is a Resource or Split Generation Resource for which the Entity or its Affiliates has the decision-making authority over how the Resource or Split Generation Resource is offered or scheduled (e.g., Output Schedules), in accordance with subsection (e) of P.U.C. Subst. R. 25.502, Pricing Safeguards in Markets Operated by the Electric Reliability Council of Texas.  Each Resource Entity that owns a Resource shall submit a declaration to ERCOT, using a form designated by ERCOT, as to which Entity has the decision-making authority for each of its Resources.  The declaration shall be signed by the Authorized Representative of the Resource Entity.  In addition, each Resource Entity that owns a Resource shall notify ERCOT of any known changes in that declaration no later than 14 days prior to the date that the change takes effect or as soon as possible in a situation where the Resource Entity is unable to meet the 14-day notice requirement.  Upon ERCOT’s request, each Resource Entity that owns a Resource shall provide ERCOT with sufficient information or documentation to verify control of the Resource.  ERCOT shall apply decision-making authority to Managed Capacity effective the first Operating Hour of the Operating Day ERCOT satisfactorily confirms the Resource Entity’s most recent declaration, but not sooner than the effective date specified on the Resource Entity’s most recent declaration.

(ii)	Determine the percentage of Managed Capacity by each Entity and its Affiliates on the import and export side.

(iii)	The ECI on the import side is equal to the sum of the square of the percentages of Managed Capacity by each Entity and its Affiliates on the import side.

(iv)	The ECI on the export side is equal to the sum of the square of the percentages of Managed Capacity by each Entity and its Affiliates on the export side.

(d)	If the ECI is greater than 2,000 on the import side or the ECI is greater than 2,500 on the export side of the constraint for the month, then the constraint fails the Annual Competitiveness Test for the month.

(3)	Test Procedure 2 – Determining if there is a pivotal player:

If the constraint satisfies the test for sufficient competition as described in Test Procedure 1, determine if there is a pivotal player in resolving the constraint in the manner described below:  If the constraint cannot be resolved by eliminating all Available Capacity on the import side, except nuclear capacity and minimum-energy amounts of coal and lignite capacity as determined in Test Procedure 1 that is Managed Capacity by any one Entity and its Affiliates during peak Load conditions, then a pivotal player exists.  A constraint satisfies this Test Procedure 2 if no Entity is a pivotal player.

3.19.2	Monthly Competitiveness Test

(1)	Unless otherwise approved by TAC as a Competitive Constraint, the Monthly Competitiveness Test shall change the treatment of a Competitive Constraint to a non-competitive constraint for the particular month if the constraint meets the following conditions:

(a)	The ECI is greater than 2,500 on the import side or the ECI is greater than 3,000 on the export side.  The ECI is determined using the same procedure as the Annual Competitiveness Test but applied to the particular month only; or

(b)	There is a pivotal player in resolving the constraint, which occurs when the constraint cannot be resolved by eliminating all Available Capacity on the import side, except Nuclear capacity and Minimum-energy amounts of Coal and Lignite that is Managed Capacity by any one Entity and its Affiliates during the peak case of the month.

(2)	The ECI values established in the monthly test must be reviewed quarterly by the TAC Subcommittee for the proper value.

3.19.3	Daily Competitiveness Test

(1)	Based on the set of the Competitive Constraints as determined in the Monthly Competitive Test, the Daily Competitiveness Test shall change the treatment of a Competitive Constraint to a non-competitive constraint for the particular day if the constraints meet the following conditions:

(a)	The ECI is greater than 2,500 on the import side or the ECI is greater than 3,000 on the export side.  The ECI is determined using the same procedure as the Annual Competitiveness Test but applied to the peak hour of the particular day; or

(b)	There is a pivotal player in resolving the constraint, which occurs when the constraint cannot be resolved by eliminating all Available Capacity on the import side, except Nuclear capacity and Minimum-energy amounts of Coal and Lignite that is Managed Capacity by any one Entity and its Affiliates during the peak hour of the day.

(2)	ERCOT shall post the Competitive Constraints to the MIS Secure Area by 0600 in the Day-Ahead.

(3)	Available Capacity for the Daily Competitiveness Test is defined as the HSL of a Generation Resource, including a Switchable Generation Resource that is not the following: on Outage for the day (except wind powered generation), expected on-peak wind generation output, and full import capability of the DC Tie line.

(4)	The ECI values established in the daily test must be reviewed quarterly for the proper value by the TAC Subcommittee.

[NPRR327: Insert Sections 3.20, 3.20.1, and 3.20.2 below upon system implementation:] 3.20 Process for Redacting State Estimator Data for Real-Time Publication (1) State Estimator data that is published on the ERCOT Market Information System (MIS) Secure Area in Real-Time shall exclude information (including but not limited to, voltages, transmission flows and transformer flows) from which Resource-specific output levels or offer curves could continually and systematically be derived. (2) The appropriate Technical Advisory Committee (TAC) subcommittee shall develop a recommended list of State Estimator elements including transmission lines, transformers and Loads to be redacted using the methodology described in Section 3.20.1, Methodology for Redaction of State Estimator Data. TAC shall consider the recommended list at its regularly scheduled meetings in February, May, August, and November TAC of each year. (3) ERCOT shall develop a published list of State Estimator elements not included in the approved redacted list. ERCOT shall produce reports filtered according to the published list to provide redacted Real-Time State Estimator data as described in Section 6.5.7.1.13, Data Inputs and Outputs for the Real-Time Sequence and SCED. (4) Distribution Service Providers (DSPs) and Transmission Service Providers (TSPs) will have access to all State Estimator data in Real-Time and the data will not be subject to the redaction methodology as described in Section 3.20.1. - 3.20.1 Methodology for Redaction of State Estimator Data (1) This method seeks to introduce at least two transmission flow unknowns at, or near, every generation plant and Load station electrical connection, as identified in Section 3.20.2, Methodology of Identification of Redacted Load. (2) The State Estimator data for the following Transmission Elements shall be redacted for the entire ERCOT System: (a) Generator Step Up (GSU) transformers; (b) Radial lines serving generating plants; (c) Transformers serving redacted Load; and (d) Radial lines serving redacted Load. (3) At each substation where a Generation Resource exists, the State Estimator data for the Transmission Elements determined using one or more of the following methods shall be redacted: (a) A transmission branch path that provides connection from the plant generation bus or redacted Load to another plant generation bus or redacted Load where the same owner exists on both buses; (b) A transmission branch path that provides connection from the plant generation bus or redacted Load to two independently owned generation plants or redacted Loads; (c) A transmission branch path that provides connection from plant generation bus to substation Load whose summer peak value is equal to or greater than 25% of generation plant capability; or (d) A transmission branch path that provides connection from redacted Load to substation Load whose summer peak value is equal to or greater than 25% of redacted Load. - 3.20.2 Methodology of Identification of Redacted Load The following Loads will be considered redacted Load: (a) Individual Load on Electrical Buses for station codes that have ten or fewer Electric Service Identifiers (ESI IDs) in DSP or TSP competitive areas; and (b) Any Non-Opt-In Entity (NOIE) Load unless the NOIE informs ERCOT of the substation or Electrical Buses that can be published and does not conflict with Section 1.3.1, Restrictions on Protected Information.