## Slide 1
2015 RTP – Study Scope of Short Circuit Analysis
RPG Meeting
May 19, 2015

## Slide 2: Outline
Introduction
Study Scope
Next Step

## Slide 3: Introduction
Governing Standards
  NERC Standard TPL-001-4 (Transmission System Planning Performance Requirements)
Purpose of Short Circuit Analysis
  Determine the magnitude of short circuit currents in the future systems within the near-term planning horizon
  Identify circuit breakers that cannot interrupt short circuit currents
  Develop corrective action plans

## Slide 4: Study Scope
Study cases
  ERCOT will conduct short circuit analysis using the 2015 RTP cases developed for the near-term planning horizon, i.e., 2018 and 2020 summer peak cases.
Methodology and Assumptions
  Fault types to be tested at all BES buses (typically, 100 kV and above) including point of interconnection (POI)
    3-phase to ground fault
    Single-line to ground fault
  Transmission solutions developed in the 2015 RTP final cases including reliability and economic projects will be considered in the study
  All generators in each case will be modeled in-service, except those determined in the 2015 RTP scope (e.g. mothballed units as documented in the CDR report)

## Slide 5: Study Scope
  Sequence impedances of facilities are needed to perform the short circuit analysis
    Transmission
      Positive sequence data will be based on the RTP cases. Negative sequence data are identical to Positive sequence data
      For zero sequence impedances, use the database of SPWG.
        If zero sequence impedance of a transmission line is not available, ERCOT will use a default value (typically, 3 times greater than positive sequence impedance)
        If zero sequence impedance of a transformer is not available, ERCOT will either use the data of similar transformer in the system, or contact TPs to obtain sequence impedances

## Slide 6: Study Scope
    Generation
      If the generator exists in both RTP and SPWG, sequence data from SPWG will be used
      If the generator exists in RTP but NOT in SPWG, ERCOT will use either RARF database or data of a generator with the similar size and type
    Load level will be consistent with RTP cases
  Tools to be used:
    PSS/E or Power World software
  Consistent with SPWG methodology, the following options will be used to perform fault analysis.
    Flat, CL (Classical flat start)
    Shunt Elements: + Sequence 0
    Tap ratios set to 1.0
    Line charging set to 0

## Slide 7: Study Scope
Deliverables
  Results of the three-phase and single-line to ground fault current along with source impedance associated with each fault
  Request TPs and GOs to review the results and to provide a list of over-dutied devices and corrective action plans
High level schedule
  ERCOT plans to post study results on MIS around mid August 2015
  ERCOT plans to request TPs and GOs to provide a list of over-dutied devices and corrective action plans by mid September 2015

## Slide 8: Next Step
Seek comments and feedback from stakeholders regarding the study scope
Finalize the study scope for 2015 RTP