| NOGRR Number | 142 | NOGRR Title | Phasor Measurement |
| --- | --- | --- | --- |

| Date | May 21, 2015 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Brian Manning |
| E-mail Address | Brian.manning@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-3937 |
| Cell Number |  |
| Market Segment | Not applicable. |

Comments

ERCOT submits the clarifying revisions in Section 6.1.3.4,  Data Retention and Reporting Requirements, to standardize references to the NERC Reliability Standards.

Revised Cover Page Language

None proposed at this time.

Revised Proposed Guide Language

- 6.1.3	Phasor Measurement Recording Equipment

Phasor measurement recording equipment includes digital fault recorders, certain protective relays and/or meters with phasor measurement recording capability that meet the requirements in Sections 6.1.3.1, Recording Requirements and 6.1.3.3, Data Recording and Redundancy Requirements.  Phasor measurement recording equipment required by these Operating Guides shall be time synchronized with a Global Positioning System-based clock, or ERCOT-approved alternative, with sub-cycle (<1 microsecond) timing accuracy and performance.

- 6.1.3.1	Recording Requirements

Recorded electrical quantities shall be:

- Provided in Institute of Electrical and Electronic Engineers (IEEE) C37.118.1-2011, IEEE Standard for Synchrophasor format;

- A minimum output recording rate of 30 times per second;

- A minimum input sampling rate of 960 samples per second;

- Transmitted to an ERCOT phasor data concentrator via a communication link or stored locally per retention requirements in Section 6.1.3.4, Data Retention and Reporting Requirements.

- 6.1.3.2	Location Requirements

The Facility owner(s), whether a Transmission Service Provider (TSP) or new Generation Entity, shall install phasor measurement recording equipment at the following Facilities.  The installation shall occur not later than 18 months after a written notification from ERCOT to the Facility owner.

(a)	Flexible AC Transmission System (FACTS) devices configured to actively control steady-state voltage or power transfer capability, operated at or above 100kV, and energized after July 1, 2015;

(b)	One Transmission Facility identified by ERCOT associated with each published Generic Transmission Constraint as deemed necessary by ERCOT; and

(c)	New generating Facilities over 20 MVA aggregated at a single site placed into service after January 1, 2017;

- 6.1.3.3	Data Recording and Redundancy Requirements

Recorded electrical quantities shall be sufficient to determine the following:

- For locations meeting paragraphs (a or b) of Section 6.1.3.2, Location Requirements:

- Phase-to-neutral voltage magnitude/angle data for each phase from at least two distinct transmission level element measurements;

- Single phase current magnitude/angle data for each phase from at least two distinct transmission level lines; and

- Frequency and df/dt data for at least two transmission level element measurements;

- For locations meeting paragraph (c) of Section 6.1.3.2:

- Phase-to-neutral voltage magnitude/angle data for each phase from at least one generator-interconnected bus measurement;

- Single phase current magnitude/angle data for each phase from each interconnected generator over 20 MVA; and

- Frequency and df/dt data for at least one generator-interconnected bus measurement.

6.1.3.4	Data Retention and Reporting Requirements

The minimum recorded electrical quantities shall be retained per the following guidelines:

- Rolling ten calendar day window for all data stored locally and not transmitted to an ERCOT phasor data concentrator;

- Minimum three year data retention by the generating Facility owner for event data utilized for model validation in accordance with NERC Reliability Standards  Standard MO;

- Minimum three year data retention by the generating or Transmission Facility owner for event data provided to ERCOT via written request that is recorded in the context of an ERCOT-initiated disturbance analysis or event review.