| NPRR Number | 710 | NPRR Title | Removal of ORDC Phase 2 Language and Modification to HASL Calculation |
| --- | --- | --- | --- |
| Date Posted |  | May 27, 2015 |  |
| Requested Resolution |  | Normal |  |
| Nodal Protocol Sections Requiring Revision |  | 2.1, Definitions 3.9, Current Operating Plan (COP) 6.5.5.2, Operational Data Requirements 6.5.7.2, Resource Limit Calculator 6.7.4, Real-Time Ancillary Service Imbalance Payment or Charge 8.1.1, QSE Ancillary Service and Reserves Performance Standards 8.1.1.1, Ancillary Service and Reserves Qualification and Testing 8.1.1.2, General Capacity Testing Requirements 8.1.1.2.1, Ancillary Service and On-Line and Off-Line Reserve Technical Requirements and Qualification Criteria and Test Methods 8.1.1.2.1.6, OFF10 Reserve Qualification (deleted) 8.1.1.2.1.7, OFF30 Reserve Qualification (deleted) 8.1.1.4.2, Responsive Reserve Service Energy Deployment Criteria 8.1.1.4.4, OFF10 Reserve Energy Deployment Criteria (deleted) 8.1.1.4.5, OFF30 Reserve Energy Deployment Criteria (deleted) |  |
| Other Binding Documents Requiring Revision or Related Revision Requests |  | Companion revisions to the Other Binding Document “Methodology for Implementing Operating Reserve Demand Curve” are attached to this Nodal Protocol Revision Request (NPRR) as Attachment 1. |  |
| Revision Description |  | This NPRR removes Operating Reserve Demand Curve (ORDC) Phase 2; changes the High Ancillary Service Limit (HASL) calculation to remove Non-Frequency Responsive Capacity (NFRC) included in a Generation Resource’s High Sustained Limit (HSL), thereby creating the opportunity for an ORDC payment for the NFRC capacity through Ancillary Service imbalance Settlement; and clarifies the HASL definition between use in the Resource limit calculator, Reliability Unit Commitment (RUC) optimization, and the capacity shortfall ratio share. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |

| Business Case |  |  |
| --- | --- | --- |
| Qualitative Benefits | Revised HASL calculation to include NFRC in a Generation Resource’s HSL gives the Qualified Scheduling Entity (QSE) representing that Resource the ability to receive an ORDC payment for the NFRC capacity through the Ancillary Service imbalance Settlement. |  |
| Quantitative Benefits | Avoidance of project and FTE costs related to the outstanding ORDC Phase 2 work. |  |
| Impact to Market Segments |  |  |
| Credit Implications | No. |  |
| Other |  |  |

| Sponsor |  |
| --- | --- |
| Name | Resmi Surendran / David Thompson |
| E-mail Address | Resmi.Surendran@ercot.com / David.Thompson@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-3033 / 512-248-4519 |
| Cell Number |  |
| Market Segment | Not applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Cory Phillips |
| E-Mail Address | cory.phillips@ercot.com |
| Phone Number | 512-248-6464 |

Comments

Please also note that the following NPRRs also propose revisions to the following Sections:

- NPRR190, Clarification of Resource Definitions and Resource Registration of Self-Serve Generators for Reliability Purposes

  - Section 6.5.5.2

- NPRR650, Clarification of Real-Time Telemetry for Split Generation Resources

  - Section 6.5.5.2

- NPRR667, Ancillary Service Redesign

  - Section 6.5.5.2

  - Section 6.7.4

  - Section 8.1.1.1

  - Section 8.1.1.2

  - Section 8.1.1.4.2

- NPRR687, Required Telemetry for Operational Awareness and PDCWG Analysis

  - Section 6.5.5.2

- NPRR691, Alignment of Protocols with NERC Reliability Standard,  BAL-001-TRE-1

  - Section 8.1.1.4.2

- NPRR694, Required Telemetry for Operational Awareness and PDCWG Analysis

  - Section 6.5.5.2

- NPRR698, Clarifications to NPRR595, RRS Load Resource Treatment In ORDC

  - Section 6.5.5.2

  - Section 6.7.4

  - Section 8.1.1.1

  - Section 8.1.1.2

  - Section 8.1.1.2.1.6

  - Section 8.1.1.4.2

  - Section 8.1.1.4.4

Proposed Protocol Language Revision

2.1	DEFINITIONS

- High Ancillary Service Limit (HASL)

A dynamically calculated MW upper limit on a Resource to reserve the part of the Resource’s capacity committed for Ancillary Service, calculated as described in Section 6.5.7.2, Resource Limit Calculator.  HASL is also included in Section 5.7.4.1.1 ,Capacity Shortfall Ratio Share, and in the RUC optimization but is not adjusted for Non-Frequency Responsive Capacity (NFRC) as in Section 6.5.7.2.

3.9	Current Operating Plan (COP)

(1)	Each Qualified Scheduling Entity (QSE) that represents a Resource must submit a Current Operating Plan (COP) under this Section.

(2)	ERCOT shall use the information provided in the COP to calculate the High Ancillary Service Limit (HASL) and Low Ancillary Service Limit (LASL) for each Resource for the Reliability Unit Commitment (RUC) processes.

(3)	ERCOT shall monitor the accuracy of each QSE’s COP as outlined in Section 8, Performance Monitoring.

(4)	A QSE must notify ERCOT that it plans to have a Resource On-Line by means of the COP using the Resource Status codes listed in paragraph (5)(b)(i) of Section 3.9.1, Current Operating Plan (COP) Criteria.  The QSE must show the Resource as On-Line with a Status of ONRUC, indicating a RUC process committed the Resource for all RUC-Committed Intervals.  A QSE may only use a RUC-committed Resource during that Resource’s RUC-Committed Interval to meet the QSE’s Ancillary Service Supply Responsibility if the Resource has been committed by the RUC process to provide Ancillary Service.

(5)	To reflect changes to a Resource’s capability, each QSE shall report by exception, changes to the COP for all hours after the Operating Period through the rest of the Operating Day.

(6)	When a QSE updates its COP to show changes in Resource status, the QSE shall update for each On-Line Resource, either an Energy Offer Curve under Section 4.4.9, Energy Offers and Bids, or Output Schedule under Section 6.4.2, Output Schedules.

(7)	Each QSE, including QSEs representing Reliability Must-Run (RMR) Units, or Black Start Resources, shall submit a revised COP reflecting changes in Resource availability as soon as reasonably practicable, but in no event later than 60 minutes after the event that caused the change.

(8)	Each QSE representing a Qualifying Facility (QF) must submit a Low Sustained Limit (LSL) that represents the minimum energy available, in MW, from the unit for economic dispatch based on the minimum stable steam delivery to the thermal host plus a justifiable reliability margin that accounts for changes in ambient conditions.

- 6.5.5.2	Operational Data Requirements

(1)	ERCOT shall use Operating Period data to monitor and control the reliability of the ERCOT Transmission Grid and shall use it in network analysis software to predict the short-term reliability of the ERCOT Transmission Grid.  Each TSP, at its own expense, may obtain that Operating Period data from ERCOT or directly from QSEs.

(2)	A QSE representing a Generation Resource connected to Transmission Facilities or distribution facilities shall provide the following Real-Time telemetry data to ERCOT for each Generation Resource.  ERCOT shall make that data available, in accordance with ERCOT Protocols, NERC Reliability Standards, and Governmental Authority requirements, to requesting TSPs and DSPs operating within ERCOT.  Such data must be provided to the requesting TSP or DSP at the requesting TSP’s or DSP’s expense, including:

(a)	Net real power (in MW) as measured by installed power metering or as calculated in accordance with the Operating Guides based on metered gross real power and conversion constants determined by the Resource Entity and provided to ERCOT through the Resource Registration process.  Net real power represents the actual generation of a Resource for all real power dispatch purposes, including use in Security-Constrained Economic Dispatch (SCED), determination of the High Ancillary Service Limit (HASL), High Dispatch Limit (HDL), Low Dispatch Limit (LDL) and Low Ancillary Service Limit (LASL), and is consistent with telemetered HSL, LSL and Non-Frequency Responsive Capacity (NFRC);

(b)	Gross real power (in MW) as measured by installed power metering or as calculated in accordance with the Operating Guides based on metered real power, which may include Supervisory Control and Data Acquisition (SCADA) metering, and conversions constants determined by the Resource Entity and provided to ERCOT through the Resource Registration process;

(c)	Gross Reactive Power (in Megavolt-Amperes reactive (MVAr));

(d)	Net Reactive Power (in MVAr);

(e)	Power to standby transformers serving plant auxiliary Load;

(f)	Status of switching devices in the plant switchyard not monitored by the TSP or DSP affecting flows on the ERCOT Transmission Grid;

(g)	Any data mutually agreed to by ERCOT and the QSE to adequately manage system reliability;

(h)	Generation Resource breaker and switch status;

(i)	HSL (Combined Cycle Generation Resources) shall:

(i)	Submit the HSL of the current operating configuration; and

(ii)	When providing RRS, update the HSL as needed, to be consistent with Resource performance limitations of RRS provision;

(j)	NFRC currently available (unloaded) and included in the HSL of the Combined Cycle Generation Resource’s current configuration;

(k)	High Emergency Limit (HEL), under Section 6.5.9.2, Failure of the SCED Process;

(l)	Low Emergency Limit (LEL), under Section 6.5.9.2;

(m)	LSL;

(n)	Configuration identification for Combined Cycle Generation Resources;

(o)	Ancillary Service Schedule for each quantity of RRS and Non-Spin which is equal to the Ancillary Service Resource Responsibility minus the amount of Ancillary Service deployment;

(p)	Ancillary Service Resource Responsibility for each quantity of Regulation Up (Reg-Up), Regulation Down (Reg-Down), RRS and Non-Spin.  The sum of Ancillary Service Resource Responsibility for all Resources in a QSE is equal to the Ancillary Service Supply Responsibility for that QSE;

(q)	Reg-Up and Reg-Down Services participation factors represent how a QSE is planning to deploy the Ancillary Service energy on a percentage basis to specific qualified Resource(s).  The Reg-Up and Reg-Down Services participation factors for a Resource providing Fast Responding Regulation Up Service (FRRS-Up) or Fast Responding Regulation Down Service (FRRS-Down) shall be zero; and

(r)	The designated Master QSE of a Generation Resource that has been split to function as two or more Split Generation Resources shall provide Real-Time telemetry for items (a), (b), (c), (d), (e), (g), and (h) above, PSS and AVR status for the total Generation Resource in addition to the Split Generation Resource the Master QSE represents.

(3)	For each Wind-powered Generation Resource (WGR), the QSE shall set the HSL equal to the current net output capability of the facility.  The net output capability should consider the net real power of the WGR, turbine availability, weather conditions, and whether the WGR net output is being affected by compliance with a SCED Dispatch Instruction.

[NPRR588: Replace paragraph (3) above with the following upon system implementation:] (3) For each Intermittent Renewable Resource (IRR), the QSE shall set the HSL equal to the current net output capability of the facility. The net output capability should consider the net real power of the IRR generation equipment, IRR generation equipment availability, weather conditions, and whether the IRR net output is being affected by compliance with a SCED Dispatch Instruction.

(4)	For each Aggregate Generation Resource (AGR), the QSE shall telemeter the number of its generators online.

(5)	A QSE representing a Load Resource connected to Transmission Facilities or distribution facilities shall provide the following Real-Time data to ERCOT for each Load Resource and ERCOT shall make the data available, in accordance with ERCOT Protocols, NERC standards and policies, and Governmental Authority requirements, to the Load Resource’s host TSP or DSP at the TSP’s or DSP’s expense.  The Load Resource’s net real power consumption, Low Power Consumption (LPC) and Maximum Power Consumption (MPC) shall be telemetered to ERCOT using a positive (+) sign convention:

(a)	Load Resource net real power consumption (in MW);

(b)	Any data mutually agreed to by ERCOT and the QSE to adequately manage system reliability;

(c)	Load Resource breaker status;

(d)	LPC (in MW);

(e)	MPC (in MW);

(f)	Ancillary Service Schedule (in MW) for each quantity of RRS and Non-Spin, which is equal to the Ancillary Service Resource Responsibility minus the amount of Ancillary Service deployment;

(g)	Ancillary Service Resource Responsibility (in MW) for each quantity of Reg-Up and Reg-Down for Controllable Load Resources, and RRS and Non-Spin for all Load Resources;

(h)	The status of the high-set under-frequency relay, if required for qualification;

(i)	For a Controllable Load Resource providing Non-Spin, the Scheduled Power Consumption that represents zero Ancillary Service deployments;

(j)	For a single-site Controllable Load Resource with registered maximum Demand response capacity of ten MW or greater, net Reactive Power (in MVAr);

(k)	Resource Status (Resource Status shall be ONRL if high-set under-frequency relay is active);

(l)	Reg-Up and Reg-Down services participation factor, which represents how a QSE is planning to deploy the Ancillary Service energy on a percentage basis to specific qualified Resource(s).  The Reg-Up and Reg-Down services participation factors for a Resource providing FRRS-Up or FRRS-Down shall be zero; and

(m)	For a Controllable Load Resource providing Non-Spin, the “Scheduled Power Consumption Plus Two Hours,” representing the QSE’s forecast of the Controllable Load Resource’s instantaneous power consumption for a point two hours in the future.

(6)	A QSE with Resources used in SCED shall provide communications equipment to receive ERCOT-telemetered control deployments.

(7)	A QSE providing any Regulation Service shall provide telemetry indicating the appropriate status of Resources providing Reg-Up or Reg-Down, including status indicating whether the Resource is temporarily blocked from receiving Reg-Up and/or Reg-Down deployments from the QSE.  This temporary blocking will be indicated by the enabling of the Raise Block Status and/or Lower Block Status telemetry points.

(a)	Raise Block Status and Lower Block Status are telemetry points used in transient unit conditions to communicate to ERCOT that a Resource’s ability to adjust its output has been unexpectedly impaired.

(b)	When one or both of the telemetry points are enabled for a Resource, ERCOT will cease using the regulation capacity assigned to that Resource for Ancillary Service deployment.

(c)	This hiatus of deployment will not excuse the Resource’s obligation to provide the Ancillary Services for which it has been committed.

(d)	These telemetry points shall only be utilized during unforeseen transient unit conditions such as plant equipment failures.  Raise Block Status and Lower Block Status shall only be enabled until the Resource operator has time to update the Resource limits and Ancillary Service telemetry to reflect the problem.

(e)	The Resource limits and Ancillary Service telemetry shall be updated as soon as practicable.  Raise Block Status and Lower Block Status will then be disabled.

(8)	Real-Time data for reliability purposes must be accurate to within three percent.  This telemetry may be provided from relaying accuracy instrumentation transformers.

(9)	Each QSE shall report the current configuration of combined-cycle Resources that it represents to ERCOT.  The telemetered Resource Status for a Combined Cycle Generation Resource may only be assigned a Resource Status of OFFNS if no generation units within that Combined Cycle Generation Resource are On-Line.

(10)	A QSE representing Combined Cycle Generation Resources shall provide ERCOT with the possible operating configurations for each power block with accompanying limits.  Combined Cycle Train power augmentation methods may be included as part of one or more of the registered Combined Cycle Generation Resource configurations.  Power augmentation methods may include:

(a)	Combustion turbine inlet air cooling methods;

(b)	Duct firing;

(c)	Other ways of temporarily increasing the output of Combined Cycle Generation Resources; and

(d)	For Qualifying Facilities (QFs), an LSL that represents the minimum energy available for Dispatch by SCED, in MW, from the Combined Cycle Generation Resource based on the minimum stable steam delivery to the thermal host plus a justifiable reliability margin that accounts for changes in ambient conditions.

- 6.5.7.2	Resource Limit Calculator

(1)	ERCOT shall calculate the HASL, LASL, SURAMP, SDRAMP, HDL and LDL within four seconds after a change of the Resource-specific attributes provided as part of the QSE’s SCADA telemetry under Section 6.5.5.2, Operational Data Requirements.  The formulas described below define which Resource-specific attributes must be used to calculate each Resource limit.  The Resource limits are used as inputs into both the SCED process and the Ancillary Service Capacity Monitor as described in Section 6.5.7.6, Load Frequency Control.  These Resource limits help ensure that the deployments produced by the SCED and Load Frequency Control (LFC) processes will respect the commitment of a Resource to provide Ancillary Services as well as individual Resource physical limitations.

(2)	The figures below illustrate how the Resource Limit Calculator determines the Resource limits for Generation and Load Resources:

Generation Resources:

LSL

HSL

Time

LSL

-

LASL

-

HASL

-

Generation

Increase

Generation

Decrease

Services

Provided: Reg

Down

Provided: Reg Up,

Responsive, Non-Spin

Current

Telemetry

HDL

LDL

Ramp

Rate

5 Minutes

Generation

Quantity

Offer Curve Generation

LSL

HSL

-

-

-

Generation

Increase

Generation

Decrease

Ramp

Rate

5 Minutes

-

0

-

-

Generation

Increase

Generation

Decrease

Ramp

Rate

5 Minutes

Ancillary

Load Resources:

Time

LSL = LPC -

LASL  -

HASL  -

Ancillary Services Provided: Reg-Down

Current Load

Telemetry

HDL

LDL

5-30 Minutes

Load

Quantity

Bid Curve Load

LSL/LPC

HSL/MPC

0

Increasing

Consumption

Decreasing

Consumption

Ramp

Rate

Ancillary Services Provided: Reg-Up, RRS, Non-Spin

HSL = MPC -

Normal Load

Fluctuation

(3)	For Generation Resources, HASL is calculated as follows:

HASL	=	Max (LASL, (HSLTELEM – (RRSTELEM + RUSTELEM + NSRSTELEM +NFRCTELEM)))

| Variable | Description |
| --- | --- |
| HASL | High Ancillary Service Limit. |
| HSLTELEM | High Sustained Limit provided via telemetry – per Section 6.5.5.2. |
| LASL | Low Ancillary Service Limit. |
| RRSTELEM | Responsive Reserve Ancillary Service Schedule provided by telemetry. |
| RUSTELEM | Reg-Up Ancillary Service Resource Responsibility designation provided by telemetry. |
| NSRSTELEM | Non-Spin Ancillary Service Schedule provided via telemetry. |
| NFRCTELEM | NFRC currently available (unloaded) and included in the HSL of the Generation Resource with non-zero Responsive Reserve Ancillary Service Service Schedule telemetry. |

(4)	For Generation Resources, LASL is calculated as follows:

LASL	=	LSLTELEM + RDSTELEM

| Variable | Description |
| --- | --- |
| LASL | Low Ancillary Service Limit. |
| LSLTELEM | Low Sustained Limit provided via telemetry. |
| RDSTELEM | Reg-Down Ancillary Service Resource Responsibility designation provided by telemetry. |

(5)	For each Generation Resource, the SURAMP is calculated as follows:

SURAMP	=	RAMPRATE – (RUSTELEM * REGP / 5)

| Variable | Description |
| --- | --- |
| SURAMP | SCED Up Ramp Rate. |
| RAMPRATE | Normal Ramp Rate up, as telemetered by the QSE, when RRS is not deployed or when the subject Resource is not providing RRS. Emergency Ramp Rate up, as telemetered by the QSE, for Resources deploying RRS. |
| RUSTELEM | Reg-Up Ancillary Service Resource Responsibility designation provided by telemetry. |
| REGP | Percentage of Regulation Service for which ramp rate will be reserved in Real-Time. The value will be between one and zero. Market Participants will be notified of the change in this value. |

(6)	For each Generation Resource, the SDRAMP is calculated as follows:

SDRAMP	=	NORMRAMP – (RDSTELEM * REGP / 5)

| Variable | Description |
| --- | --- |
| SDRAMP | SCED Down Ramp Rate. |
| NORMRAMP | Normal Ramp Rate down, as telemetered by the QSE. |
| RDSTELEM | Reg-Down Ancillary Service Resource Responsibility designation by Resource provided via telemetry. |
| REGP | Percentage of Regulation Service for which ramp rate will be reserved in Real-Time. The value will be between one and zero. Market Participants will be notified of the change in this value. |

(7)	For Generation Resources, HDL is calculated as follows:

(a)	If the telemetered Resource Status is SHUTDOWN, then

HDL	=	POWERTELEM – (SDRAMP * 5)

(b)	If the telemetered Resource Status is any status code specified in item (5)(b)(i) of Section 3.9.1, Current Operating Plan (COP) Criteria, other than SHUTDOWN, then

HDL	=	Min (POWERTELEM + (SURAMP * 5), HASL)

| Variable | Description |
| --- | --- |
| HDL | High Dispatch Limit. |
| POWERTELEM | Gross or net real power provided via telemetry. |
| SURAMP | SCED Up Ramp Rate. |
| SDRAMP | SCED Down Ramp Rate. |
| HASL | High Ancillary Service Limit – definition provided in Section 2, Definitions and Acronyms. |

(8)	For Generation Resources, LDL is calculated as follows:

(a)	If the telemetered Resource Status is STARTUP, then

LDL	=	POWERTELEM + (SURAMP * 5)

(b)	If the telemetered Resource Status is any status code specified in item (5)(b)(i) of Section 3.9.1 other than STARTUP, then

LDL	=	Max (POWERTELEM - (SDRAMP * 5), LASL)

| Variable | Description |
| --- | --- |
| LDL | Low Dispatch Limit. |
| POWERTELEM | Gross or net real power provided via telemetry. |
| SDRAMP | SCED Down Ramp Rate. |
| LASL | Low Ancillary Service Limit – definition provided in Section 2. |

(9)	For Load Resources, HASL is calculated as follows:

HASL	=	Max (LPCTELEM, (MPCTELEM – RDSTELEM))

| Variable | Description |
| --- | --- |
| HASL | High Ancillary Service Limit. |
| LPCTELEM | Low Power Consumption provided via telemetry. |
| MPCTELEM | Maximum Power Consumption provided via telemetry. |
| RDSTELEM | Reg-Down Ancillary Service Resource Responsibility designation provided by telemetry. |

(10)	For Load Resources, LASL is calculated as follows:

LASL	=	Min (HASL, (LPCTELEM + (RRSTELEM + RUSTELEM + NSRSTELEM)))

| Variable | Description |
| --- | --- |
| LASL | Low Ancillary Service Limit. |
| HASL | High Ancillary Service Limit. |
| LPCTELEM | Low Power Consumption provided via telemetry. |
| RRSTELEM | Responsive Reserve Ancillary Service Schedule provided by telemetry. |
| RUSTELEM | Reg-Up Ancillary Service Resource Responsibility designation provided by telemetry. |
| NSRSTELEM | Non-Spin Ancillary Service Schedule provided via telemetry. |

(11)	For each Load Resource, the SURAMP is calculated as follows:

SURAMP	=	RAMPRATE – (RUSTELEM * REGP / 5)

| Variable | Description |
| --- | --- |
| SURAMP | SCED Up Ramp Rate. |
| RAMPRATE | Normal Ramp Rate up, as telemetered by the QSE, when RRS is not deployed or when the subject Load Resource is not providing RRS. Emergency Ramp Rate up, as telemetered by the QSE, for Load Resources deploying RRS. |
| RUSTELEM | Reg-Up Ancillary Service Resource Responsibility designation provided by telemetry. |
| REGP | Percentage of Regulation Service for which ramp rate will be reserved in Real-Time. The value will be between one and zero. Market Participants will be notified of the change in this value. |

(12)	For each Load Resource, the SDRAMP is calculated as follows:

SDRAMP	=	NORMRAMP – (RDSTELEM * REGP / 5)

| Variable | Description |
| --- | --- |
| SDRAMP | SCED Down Ramp Rate. |
| NORMRAMP | Normal Ramp Rate down, as telemetered by the QSE. |
| RDSTELEM | Reg-Down Ancillary Service Resource Responsibility designation by Resource provided via telemetry. |
| REGP | Percentage of Regulation Service for which ramp rate will be reserved in Real-Time. The value will be between one and zero. Market Participants will be notified of the change in this value. |

(13)	For Load Resources, HDL is calculated as follows:

HDL	=	Min (POWERTELEM + (SDRAMP * 5), HASL)

| Variable | Description |
| --- | --- |
| HDL | High Dispatch Limit. |
| POWERTELEM | Net real power flow provided via telemetry. |
| SDRAMP | SCED Down Ramp Rate. |
| HASL | High Ancillary Service Limit – definition provided in Section 2. |

(14)	For Load Resources, LDL is calculated as follows:

LDL	=	Max (POWERTELEM - (SURAMP * 5), LASL)

| Variable | Description |
| --- | --- |
| LDL | Low Dispatch Limit. |
| POWERTELEM | Net real power flow provided via telemetry. |
| SURAMP | SCED Up Ramp Rate. |
| LASL | Low Ancillary Service Limit – definition provided in Section 2. |

- 6.7.4	Real-Time Ancillary Service Imbalance Payment or Charge

(1)	Based on the Real-Time On-Line Reserve Price Adders and a Real-Time Off-Line Reserve Price Adders, ERCOT shall calculate Ancillary Service imbalance Settlement, which will make Resources indifferent to the utilization of their capacity for energy or Ancillary Service reserves, as set forth in this Section.

[NPRR626: Replace paragraph (1) above upon system implementation:] (1) Based on the Real-Time On-Line Reliability Deployment Price Adders, Real-Time On-Line Reserve Price Adders and a Real-Time Off-Line Reserve Price Adders, ERCOT shall calculate Ancillary Service imbalance Settlement, which will make Resources indifferent to the utilization of their capacity for energy or Ancillary Service reserves, as set forth in this Section.

(2)	The payment or charge to each QSE for Ancillary Service imbalance is calculated based on the price calculation set forth in paragraph (11) of Section 6.5.7.3, Security Constrained Economic Dispatch, and applied to the following amounts for each QSE:

(a)	The amount of Real-Time Metered Generation from all Generation Resources, represented by the QSE for the 15-minute Settlement Interval;

(b)	The amount of On-Line capacity based on the telemetered High Sustained Limit (HSL) for all On-Line Generation Resources, the Ancillary Service Schedule for RRS from Load Resources controlled by high-set under-frequency relay, and the capacity from Controllable Load Resources available to Security-Constrained Economic Dispatch (SCED);

(c)	The amount of Ancillary Service Resource Responsibility for Reg-Up, RRS and Non-Spin for all Generation and Load Resources represented by the QSE for the 15-minute Settlement Interval.

(3)	Intermittent Renewable Resources (IRRs) with the exception of Wind-powered Generation Resources (WGRs), Resources with a telemetered ONTEST, STARTUP (except Resources with Non-Spin Ancillary Service Resource Responsibility greater than zero), or SHUTDOWN Resource Status, Resources with a telemetered net real power (in MW) less than 95% of their telemetered Low Sustained Limit (LSL), and nuclear Resources will be excluded from the amounts calculated pursuant to paragraphs (2)(a) and (b) above.

[NPRR645: Replace paragraph (3) above with the following upon system implementation:] (3) Resources meeting one or more of the following conditions will be excluded from the amounts calculated pursuant to paragraphs (2)(a) and (b) above: (a) Intermittent Renewable Resources (IRRs) excluding Wind-powered Generation Resources (WGRs); (b) Nuclear Resources; (c) Resources with a telemetered ONTEST, STARTUP, or SHUTDOWN Resource Status excluding Resources telemetering both STARTUP Resource Status and greater than zero Non-Spin Ancillary Service Responsibility; or (d) Resources with a telemetered net real power (in MW) less than 95% of their telemetered Low Sustained Limit (LSL) excluding Resources telemetering both STARTUP Resource Status and greater than zero Non-Spin Ancillary Service Responsibility.

(4)	Reliability Must-Run (RMR) Units and Reliability Unit Commitment (RUC) Resources On-Line during the hour due to an ERCOT instruction, except RUC Resources that were issued a RUC Dispatch Instruction to provide Ancillary Services pursuant to paragraph (10) of Section 5.5.2, Reliability Unit Commitment (RUC) Process, and that the QSE subsequently self-committed pursuant to paragraph (11) of Section 5.5.2, will be excluded from the amounts calculated for the 15-minute Settlement Interval pursuant to paragraphs (2)(a), (b) and (c) above.

(5)	The Real-Time Off-Line Reserve Capacity for the QSE (RTOFFCAP) shall be administratively set to zero when the SCED snapshot of the Physical Responsive Capability (PRC) is less than or equal to the PRC MW at which Energy Emergency Alert (EEA) Level 1 is initiated.

[NPRR645: Insert paragraph (6) below upon system implementation and renumber accordingly:] (6) Resources that have a Under Generation Volume (UGEN) greater than zero, and are not-exempt from a Base Point Deviation Charge, as set forth in Section 6.6.5, Base Point Deviation Charge, or are not already excluded in paragraphs (3) or (4) above, for the 15-minute Settlement Interval will have the UGEN amounts removed from the amounts calculated pursuant to paragraphs (2)(a) and (b) above

(6)	The payment or charge to each QSE for the Ancillary Service Imbalance for a given 15 minute Settlement Interval is calculated as follows:

RTASIAMT q	=		(-1) * [(RTASOLIMB q * RTRSVPOR) + (RTASOFFIMB q * RTRSVPOFF)]

[NPRR626: Insert the following equation RTRDASIAMT q below upon system implementation:] RTRDASIAMT q= (-1) * (RTASOLIMB q * RTRDP)

Where:

RTASOLIMB q=		RTOLCAP q – [((SYS_GEN_DISCFACTOR * RTASRESP q ) * ¼) – RTASOFF q – RTRUCNBBRESP q – RTCLRNSRESP q – RTRMRRESP q]

Where:

RTASOFF q =			SYS_GEN_DISCFACTOR * RTASOFFR q, r, p

RTRUCNBBRESP q  =	SYS_GEN_DISCFACTOR *  RTRUCASA q, r *  ¼

RTCLRNSRESP q =		SYS_GEN_DISCFACTOR *  HNSADJ q, r, p *  ¼

RTRMRRESP q =	SYS_GEN_DISCFACTOR * (HRRADJ q, r, p + HRUADJ q, r, p + HNSADJ q, r, p) *  ¼

RTOLCAP q =	(RTOLHSL q – RTMGQ q) + RTCLRCAP q + RTNCLRRRS q

[NPRR645: Replace the above equation RTOLCAP q with the following upon system implementation:] RTOLCAP q = (RTOLHSL q – RTMGQ q – SYS_GEN_DISCFACTOR * (UGENA q, r, p)) + RTCLRCAP q + RTNCLRRRS q

Where:

RTNCLRRRS q =	SYS_GEN_DISCFACTOR *  RTNCLRRRSR q, r, p

And, adjusted pursuant to paragraphs (3) and (4) above:

RTOLHSL q =		SYS_GEN_DISCFACTOR * RTOLHSLR q, r, p

RTMGQ q =		SYS_GEN_DISCFACTOR * RTMG q, r, p

[NPRR645: Replace the above language with the following upon system implementation:] Where: RTNCLRRRS q = SYS_GEN_DISCFACTOR * RTNCLRRRSR q, r, p RTOLHSL q = SYS_GEN_DISCFACTOR * RTOLHSLRA q, r, p RTMGQ q = SYS_GEN_DISCFACTOR * RTMGA q, r, p If RTMGA q, r, p > RTOLHSLRA q, r, p Then RTMGA q, r, p = RTOLHSLRA q, r, p

RTCLRCAP q=	RTCLRNPF q – RTCLRLSL q – RTCLRNS q + RTCLRREG q

Where:

RTCLRNPF q=		SYS_GEN_DISCFACTOR * RTCLRNPFR q, r, p

RTCLRLSL q =		SYS_GEN_DISCFACTOR * RTCLRLSLR q, r, p

RTCLRNS q =		SYS_GEN_DISCFACTOR *  RTCLRNSR q, r, p

RTCLRREG q =	SYS_GEN_DISCFACTOR *  RTCLRREGR q, r, p

RTRSVPOR=	(RNWF  y * RTORPA y)

RTASOFFIMB q =	RTOFFCAP q – (RTASOFF q + (RTCLRNSRESP q)

RTOFFCAP q =	(SYS_GEN_DISCFACTOR * RTCST30HSL q) + (SYS_GEN_DISCFACTOR * RTOFFNSHSL q)+ RTCLRNS q

RTRSVPOFF=	(RNWF  y * RTOFFPA y)

[NPRR626: Insert the following equation RTRDP below upon system implementation:] RTRDP = (RNWF y * RTORDPA y)

RNWF y=	TLMP y / TLMP y

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTASIAMT q | $ | Real-Time Ancillary Service Imbalance Amount—The total payment or charge to QSE q for the Real-Time Ancillary Service imbalance for each 15-minute Settlement Interval. |
| [NPRR626: Replace the variable above RTASIAMT q with the following upon system implementation:] RTASIAMT q; $; Real-Time Ancillary Service Imbalance Amount—The total payment or charge to QSE q for the Real-Time Ancillary Service imbalance associated with ORDC for each 15-minute Settlement Interval.. |
| [NPRR626: Insert the following variable RTRDASIAMT q below upon system implementation:] RTRDASIAMT q; $; Real-Time Reliability Deployment Ancillary Service Imbalance Amount—The total payment or charge to QSE q for the Real-Time Ancillary Service imbalance associated with Reliability Deployments for each 15-minute Settlement Interval.. |
| RTASOLIMB q | MWh | Real Time Ancillary Service On-Line Reserve Imbalance for the QSE The Real-Time Ancillary Service On-Line reserve imbalance for the QSE q, for each 15-minute Settlement Interval. |
| RTORPA y | $/MWh | Real-Time On-Line Reserve Price Adder per intervalThe Real-Time Price Adder for On-Line Reserves for the SCED interval y. |
| RTOFFPA y | $/MWh | Real-Time Off-Line Reserve Price Adder per intervalThe Real-Time Price Adder for Off-Line Reserves for the SCED interval y. |
| TLMP y | second | Duration of SCED interval per intervalThe duration of the SCED interval y. |
| [NPRR626: Insert the following variables RTRDP and RTORDPA y below upon system implementation:] RTRDP; $/MWh; Real-Time On-Line Reliability Deployment PriceThe Real-Time price for the 15-minute Settlement Interval, reflecting the impact of reliability deployments on energy prices that is calculated from the Real-time On-Line Reliability Deployment Price Adder.. RTORDPA y; $/MWh; Real-Time On-Line Reliability Deployment Price AdderThe Real-Time Price Adder that captures the impact of reliability deployments on energy prices for the SCED interval y.. |
| RNWF y | none | Resource Node Weighting Factor per intervalThe weight used in the Resource Node Settlement Point Price calculation for the portion of the SCED interval y within the 15-minute Settlement Interval. |
| RTRSVPOR | $/MWh | Real-Time Reserve Price for On-Line ReservesThe Real-Time Reserve Price for On-Line Reserves for the 15-minute Settlement Interval. |
| RTRSVPOFF | $/MWh | Real-Time Reserve Price for Off-Line ReservesThe Real-Time Reserve Price for Off-Line Reserves for the 15-minute Settlement Interval. |
| RTOLCAP q | MWh | Real-Time On-Line Reserve Capacity for the QSEThe Real-Time reserve capacity of On-Line Resources available for the QSE q, for the 15-minute Settlement Interval. |
| RTOLHSLR q, r, p | MWh | Real-Time On-Line High Sustained Limit for the ResourceThe Real-Time telemetered HSL for the Resource that is available to SCED, integrated over the 15-minute Settlement Interval. |
| [NPRR645: Replace the variable RTOLHSLR q, r, p above with the new variable RTOLHSLRA q, r, p below upon system implementation:] RTOLHSLRA q, r, p; MWh; Real-Time Adjusted On-Line High Sustained Limit for the ResourceThe Real-Time telemetered HSL for the Resource that is available to SCED, integrated over the 15-minute Settlement Interval, and adjusted pursuant to paragraphs (3) and (4) above... |
| RTOLHSL q | MWh | Real-Time On-Line High Sustained Limit for the QSEThe Real-Time telemetered HSL for all Generation Resources available to SCED, pursuant to paragraphs (3) and (4) above, integrated over the 15-minute Settlement Interval for the QSE q, discounted by the system-wide discount factor. |
| RTASRESP q | MW | Real-Time Ancillary Service Supply Responsibility for the QSEThe Real-Time Ancillary Service Supply Responsibility for Reg-Up, RRS and Non-Spin pursuant to Section 4.4.7.4, Ancillary Service Supply Responsibility, for all Generation and Load Resources discounted by the system-wide discount factor for the QSE q, for the 15-minute Settlement Interval. |
| upon system implementation:] |
| RTCLRCAP q | MWh | Real-Time Capacity from Controllable Load Resources for the QSE—The Real-Time capacity and Reg-Up minus Non-Spin available from all Controllable Load Resources available to SCED for the QSE q, integrated over the 15-minute Settlement Interval. |
| RTNCLRRRSR q | MWh | Real-Time Non-Controllable Load Resources Responsive Reserve Schedule for the QSE—The validated Real-Time RRS Ancillary Service Schedule from all Load Resources other than Controllable Load Resources available to SCED discounted by the system-wide discount factor for the QSE q, integrated over the 15-minute Settlement Interval. |
| RTNCLRRRS q | MWh | Real-Time Non-Controllable Load Resources Responsive Reserve Schedule for the QSE—The Real-Time RRS Ancillary Service Schedule from all Load Resources other than Controllable Load Resources available to SCED for the QSE q, integrated over the 15-minute Settlement Interval. |
| RTCLRNPFR q, r, p | MWh | Real-Time Net Power Flow from the Controllable Load Resource—The Real-Time net power flow from the Controllable Load Resource r available to SCED integrated over the 15-minute Settlement Interval discounted by the system-wide discount factor. |
| RTCLRNPF q | MWh | Real-Time Net Power Flow from Controllable Load Resources for the QSE—The Real-Time net power flow from all Controllable Load Resources available to SCED integrated over the 15-minute Settlement Interval for the QSE q. |
| RTCLRLSLR q, r, p | MWh | Real-Time Low Sustained Limit for the Controllable Load Resource—The Real-Time LSL from the Controllable Load Resource r available to SCED integrated over the 15-minute Settlement Interval discounted by the system-wide discount factor. |
| RTCLRLSL q | MWh | Real-Time Low Sustained Limit from Controllable Load Resources for the QSE—The Real-Time LSL from Controllable Load Resources available to SCED integrated over the 15-minute Settlement Interval for the QSE q. |
| RTCLRREG q | MWh | Real-Time Controllable Load Resources Regulation-Up Schedule for the QSE—The Real-Time Reg-Up Ancillary Service Schedule from all Controllable Load Resources with Primary Frequency Response for the QSE q, integrated over the 15-minute Settlement Interval. |
| RTCLRREGR q, r, p | MWh | Real-Time Controllable Load Resource Regulation-Up Schedule for the Resource—The validated Real-Time Reg-Up Ancillary Service Schedule for the Controllable Load Resource r with Primary Frequency Response discounted by the system-wide discount factor, integrated over the 15-minute Settlement Interval. |
| RTMG q, r, p | MWh | Real-Time Metered Generation per QSE per Settlement Point per Resource—The metered generation of Generation Resource r at Resource Node p represented by QSE q in Real-Time for the 15-minute Settlement Interval. Where for a Combined Cycle Train, the Resource r is the Combined Cycle Train. |
| [NPRR645: Replace the variable RTMG q, r, p above with the new variable RTMGA q, r, p below upon system implementation:] RTMGA q, r, p; MWh; Real-Time Adjusted Metered Generation per QSE per Settlement Point per Resource—The adjusted metered generation, pursuant to paragraphs (3) and (4) above, of Generation Resource r at Resource Node p represented by QSE q in Real-Time for the 15-minute Settlement Interval. Where for a Combined Cycle Train, the Resource r is the Combined Cycle Train... |
| RTMGQ q | MWh | Real-Time Metered Generation per QSE—The metered generation, discounted by the system-wide discount factor, of all generation Resources represented by QSE q in Real-Time for the 15-minute Settlement Interval, pursuant to paragraphs (3) and (4) above. |
| RTASOFFIMB q | MWh | Real-Time Ancillary Service Off-Line Reserve Imbalance for the QSEThe Real-Time Ancillary Service Off-Line reserve imbalance for the QSE q, for each 15-minute Settlement Interval. |
| RTOFFCAP q | MWh | Real-Time Off-Line Reserve Capacity for the QSEThe Real-Time reserve capacity of Off-Line Resources available for the QSE q, for the 15-minute Settlement Interval. |
| RTCST30HSL q | MWh | Real-Time Generation Resources with Cold Start Available in 30 MinutesThe Real-Time telemetered HSLs of Generation Resources that have telemetered an OFF Resource Status and can be started from a cold temperature state in 30 minutes and discounted by the system-wide discount factor for the QSE q, time-weighted over the 15-minute Settlement Interval. |
| below upon system implementation:] |
| RTOFFNSHSL q | MWh | Real-Time Generation Resources with Off-Line Non-Spin ScheduleThe Real-Time telemetered HSLs of Generation Resources that have telemetered an OFFNS Resource Status and discounted by the system-wide discount factor for the QSE q, time-weighted over the 15-minute Settlement Interval. |
| RTASOFFR q, r, p | MWh | Real-Time Ancillary Service Schedule for the Off-Line Generation ResourceThe validated Real-Time telemetered Ancillary Service Schedule for the Off-Line Generation Resource r discounted by the system-wide discount factor, integrated over the 15-minute Settlement Interval. |
| RTASOFF q | MWh | Real-Time Ancillary Service Schedule for Off-Line Generation Resources for the QSEThe Real-Time telemetered Ancillary Service Schedule for all Off-Line Generation Resources for the QSE q, integrated over the 15-minute Settlement Interval. |
| HRRADJ q, r, p | MW | Ancillary Service Resource Responsibility Capacity for Responsive Reserve at Adjustment Period—The Responsive Reserve Ancillary Service Resource Responsibility for the Resource r as seen in the last Current Operating Plan (COP) and Trades Snapshot at the end of the Adjustment Period, for the hour that includes the 15-minute Settlement Interval. |
| HRUADJ q, r, p | MW | Ancillary Service Resource Responsibility Capacity for Reg-Up at Adjustment Period—The Regulation Up Ancillary Service Resource Responsibility for the Resource r as seen in the last COP and Trades Snapshot at the end of the Adjustment Period, for the hour that includes the 15-minute Settlement Interval. |
| HNSADJ q, r, p | MW | Ancillary Service Resource Responsibility Capacity for Non-Spin at Adjustment Period—The Non-Spin Ancillary Service Resource Responsibility for the Resource r as seen in the last COP and Trades Snapshot at the end of the Adjustment Period, for the hour that includes the 15-minute Settlement Interval. |
| RTRUCNBBRESP q | MWh | Real-Time RUC Ancillary Service Supply Responsibility for the QSE in Non-Buy-Back hoursThe Real-Time Ancillary Service Supply Responsibility for Reg-Up, RRS and Non-Spin pursuant to the Ancillary Service awards, for the 15-minute Settlement Interval that falls within a RUC-Committed Hour, discounted by the system-wide discount factor for the QSE q. |
| RTRUCASA q, r | MW | Real-Time RUC Ancillary Service AwardsThe Real-Time Ancillary Service award to the RUC Resource r for Reg-Up, RRS and Non-Spin for the hour that includes the 15-minute Settlement Interval that falls within a RUC-Committed Hour for the QSE q. |
| RTCLRNSRESP q | MWh | Real-Time Controllable Load Resource Non-Spin Responsibility for the QSEThe Real Time Non-Spin Ancillary Service Supply Responsibility as set forth in the end of the Adjustment Period COP for all Controllable Load Resources available to SCED discounted by the system-wide discount factor for the QSE q, for the 15-minute Settlement Interval. |
| RTRMRRESP q | MWh | Real-Time Ancillary Service Supply Responsibility for RMR Units represented by the QSEThe Real-Time Ancillary Service Supply Responsibility as set forth in the end of the Adjustment Period COP for Reg-Up, RRS and Non-Spin for all RMR Units discounted by the system-wide discount factor for the QSE q, integrated over the 15-minute Settlement Interval. |
| RTCLRNSR q, r, p | MWh | Real-Time Non-Spin Schedule for the Controllable Load Resource The validated Real Time telemetered Non-Spin Ancillary Service Schedule for the Controllable Load Resource r, discounted by the system-wide discount factor, integrated over the 15-minute Settlement Interval. |
| RTCLRNS q | MWh | Real-Time Non-Spin Schedule for Controllable Load Resources for the QSEThe Real Time telemetered Non-Spin Ancillary Service Schedule for all Controllable Load Resources for the QSE q, integrated over the 15-minute Settlement Interval. |
| SYS_GEN_DISCFACTOR | none | System-Wide Discount Factor – The system-wide discount factor used to discount inputs used in the calculation of Real-Time Ancillary Services Imbalance payment or charge is calculated for each Season based on the average of the Reserve Discount Factors (RDFs) for that Season from the year prior. |
| [NPRR645: Insert the following variables UGEN q, r, p and UGENA q, r, p upon system implementation:] UGEN q, r, p; MWh; Under Generation Volumes per QSE per Settlement Point per Resource—The amount under-generated by the Generation Resource r represented by QSE q at Resource Node p for the 15-minute Settlement Interval.. UGENA q, r, p; MWh; Adjusted Under Generation Volumes per QSE per Settlement Point per Resource—The amount under-generated by the Generation Resource r represented by QSE q at Resource Node p for the 15-minute Settlement Interval adjusted pursuant to paragraph (6) above.. |
| r | none | A Generation or Load Resource. |
| y | none | A SCED interval in the 15-minute Settlement Interval. The summation is over the total number of SCED runs that cover the 15-minute Settlement Interval. |
| q | none | A QSE. |

(7) 	The payment to each QSE for the Ancillary Service reserves associated with RUC Resources that have received a RUC Dispatch to provide Ancillary Services in which the 15-minute Settlement Interval is part of a RUC Buy-Back Hour based on the RUC opt out provision set forth in paragraph (11) of Section 5.5.2 for a given 15-minute Settlement Interval is calculated as follows:

RTRUCRSVAMT q =	(-1) * (RTRUCRESP q * RTRSVPOR)

[NPRR626: Insert the following equation RTRDRUCRSVAMT q below upon system implementation:] RTRDRUCRSVAMT q = (-1) * (RTRUCRESP q * RTRDP)

Where:

RTRUCRESP q=  RTRUCASA q, r * ¼

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTRUCRSVAMT q | $ | Real-Time RUC Ancillary Service Reserve Amount—The total payment ¦to QSE q for the Real-Time RUC Ancillary Service Reserve payment for each 15-minute Settlement Interval. |
| [NPRR626: Replace the variable RTRUCRSVAMTq above with the following upon system implementation:] RTRUCRSVAMT q; $; Real-Time RUC Ancillary Service Reserve Amount—The total payment ¦to QSE q for the Real-Time RUC Ancillary Service Reserve payment associated with ORDC for each 15-minute Settlement Interval.. |
| [NPRR626: Insert the following variable RTRDRUCRSVAMT q below upon system implementation:] RTRDRUCRSVAMT q; $; Real-Time Reliability Deployment RUC Ancillary Service Reserve Amount—The total payment ¦to QSE q for the Real-Time RUC Ancillary Service Reserve payment associated with Reliability Deployments for each 15-minute Settlement Interval.. |
| RTRUCRESP q | MWh | Real-Time RUC Ancillary Service Supply Responsibility for the QSEThe Real-Time Ancillary Service Supply Responsibility pursuant to the Ancillary Service awards for Reg-Up, RRS and Non-Spin for all RUC Resources that have opted out per paragraph (11) of Section 5.5.2 discounted by the system-wide discount factor for the QSE q, for the 15-minute Settlement Interval. |
| RTRUCASA q, r | MW | Real-Time RUC Ancillary Service AwardsThe Real-Time Ancillary Service award to the RUC Resource r for Reg-Up, RRS and Non-Spin for the 15-minute Settlement Interval that falls within a RUC-Committed Hour for the QSE q. |
| RTRSVPOR | $/MWh | Real-Time Reserve Price for On-Line ReservesThe Real-Time Reserve Price for On-Line Reserves for the 15-minute Settlement Interval. |
| [NPRR626: Insert the following variable RTRDP below upon system implementation:] RTRDP; $/MWh; Real-Time On-Line Reliability Deployment Price The Real-Time price for the 15-minute Settlement Interval, reflecting the impact of reliability deployments on energy prices that is calculated from the Real-time On-Line Reliability Deployment Price Adder.. |
| q | none | A QSE. |

8.1.1	QSE Ancillary Service Performance Standards

Each QSE and its Resources that provide Ancillary Service must meet performance measures set out in these Protocols and the Operating Guides.  ERCOT shall develop a TAC- and ERCOT Board-approved Ancillary Service monitoring program to evaluate the performance of QSEs and Resources providing Ancillary Services prior to the Texas Nodal Market Implementation Date.  This program must include monitoring of capacity availability and energy deployments as described below and in Section 6.5.7.5, Ancillary Services Capacity Monitor.

- 8.1.1.1	Ancillary Service Qualification and Testing

(1)	Each QSE and the Resource providing Ancillary Service must meet qualification criteria to operate satisfactorily with ERCOT.  ERCOT shall use the Ancillary Service qualification and testing program that is approved by TAC and included in the Operating Guides.  Each QSE for the Resources that it represents may only provide Ancillary Services on those Resources for which it has met the qualification criteria.

(2)	General capacity testing must be used to verify a Resource’s Net Dependable Capability.  Qualification tests allow the Resource and QSE to demonstrate the minimum capabilities necessary to deploy an Ancillary Service.

(3)	A Resource may be provisionally qualified for a period of 90 days and may be eligible to participate as a Resource providing Ancillary Service.  Resources that have installed the appropriate equipment with verifiable testing data may be provisionally qualified as providers of Ancillary Service.

(4)	A Load Resource may be provisionally qualified for a period of 90 days to participate as a Resource providing Ancillary Service, if the Load Resource is metered with an Interval Data Recorder (IDR) to ERCOT’s reasonable satisfaction.  A Load Resource providing Ancillary Service in Real-Time must meet the following requirements:

(a)	Electric Service Identifier (ESI ID) registration of Load Resources providing Ancillary Service by the QSE; and

(b)	Load Resource telemetry is installed and tested between QSE and ERCOT.

(5)	Provisional qualification as described herein may be revoked by ERCOT at any time for any non-compliance with provisional qualification requirements.

(6)	For those Settlement Intervals during which a Generation Resource or Load Resource behind the Generation Resource Node is engaged in testing in accordance with this Section, the provisions of Section 6.6.5, Generation Resource Base-Point Deviation Charge, will not apply to the Resource being tested beginning with the Settlement Interval immediately preceding the Settlement Interval in which ERCOT issues a Dispatch Instruction that begins the test and continuing until the end of the Settlement Interval in which the test completes.  During the same Settlement Intervals for the testing period, the Generation Resource Energy Deployment Performance (GREDP) calculated in accordance with Section 8.1.1.4.1, Regulation Service and Generation Resource/Controllable Load Resource Energy Deployment Performance, will not apply.

(7)	ERCOT may reduce the amount a Resource may contribute toward Ancillary Service if it determines unsatisfactory performance of the Resource as defined in Section 8.1.1, QSE Ancillary Service Performance Standards.

(8)	To maintain qualification with ERCOT to provide RRS service, each Load Resource, excluding Controllable Load Resources, will be subject to a Load interruption test at a date and time determined by ERCOT and known only to ERCOT and the affected Transmission Service Provider (TSP), to verify the ability to respond to an ERCOT Dispatch Instruction.  To successfully pass this test, the Load Resource must deploy at least 95% of its Ancillary Service Resource Responsibility for RRS within ten minutes of the receipt of the ERCOT Dispatch Instruction by the Load Resource’s QSE.  If a Load Resource has responded to an actual ERCOT Dispatch Instruction with at least a 95% reduction in its Ancillary Service Resource Responsibility for RRS within ten minutes in the rolling 365-day period, ERCOT will use that response in lieu of a Load interruption test.  If a Load Resource has not responded to an ERCOT Dispatch Instruction with at least a 95% reduction in its Ancillary Service Resource Responsibility for RRS within ten minutes, either in a deployment event or a Load interruption test, in any rolling 365-day period, it is subject to a Load interruption test by ERCOT.  QSEs may request to have individual Load Resources aggregated for the purposes of Load interruption tests.  All performance evaluations will apply on an individual Resource basis.

[NPRR595: Replace paragraph (8) above with the following upon system implementation:] (8) To maintain qualification with ERCOT to provide RRS service, each Load Resource, excluding Controllable Load Resources, will be subject to a Load interruption test at a date and time determined by ERCOT and known only to ERCOT and the affected Transmission Service Provider (TSP), to verify the ability to respond to an ERCOT Dispatch Instruction. To successfully pass this test, within ten minutes of the receipt of the ERCOT Dispatch Instruction by the Load Resource’s QSE, the Load Resource’s response shall not be less than 95% of the requested MW deployment, nor more than 150% of the lesser of the following: (a) The Resource’s Responsibility for RRS, or (b) The requested MW deployment. The requested MW deployment will be the sum of the Resource’s Responsibility for RRS and the telemetered additional capacity between the net power consumption and the Low Power Consumption (LPC). If a Load Resource has responded to an actual ERCOT Dispatch Instruction in compliance with (a) and (b) above in the rolling 365-day period, ERCOT will use that response in lieu of a Load interruption test. If a Load Resource has not responded to an ERCOT Dispatch Instruction in compliance with (a) and (b) above, either in a deployment event or a Load interruption test, in any rolling 365-day period, it is subject to a Load interruption test by ERCOT. QSEs may request to have individual Load Resources aggregated for the purposes of Load interruption tests. All performance evaluations will apply on an individual Resource basis.

(9)	ERCOT may revoke the Ancillary Service qualification of any Load Resource, excluding Controllable Load Resources, for failure to comply with the required performance standards, based on the evaluation it performed under paragraph (c) of Section 8.1.1.4.2, Responsive Reserve Service Energy Deployment Criteria.  Specifically, if a Load Resource that is providing RRS fails to respond with at least 95% of its Ancillary Service Resource Responsibility for RRS within ten minutes of an ERCOT Dispatch Instruction, that response shall be considered a failure.  Two Load Resource performance failures, either in a deployment event or a Load interruption test, within any rolling 365-day period shall result in disqualification of that Load Resource.  After six months of disqualification, the Load Resource may reapply for qualification provided it submits a corrective action plan to ERCOT that identifies actions taken to correct performance deficiencies and the disqualified Load Resource successfully passes a new Load interruption test as specified in this Section 8.1.1.1.

- 8.1.1.2	General Capacity Testing Requirements

(1)	Within the first 15 days of each Season, each QSE shall provide ERCOT a Seasonal High Sustained Limit (HSL) for any Generation Resource with a capacity greater than ten MW that will be operated during that Season.  ERCOT shall provide an appropriate form for QSEs to submit their Seasonal HSL data.  The Seasonal HSL form shall take into account auxiliary Load and gross and net real power capability of the Generation Resource.  Each QSE shall update its COP and telemetry, as necessary, to reflect the HSL of each of its Generation Resources in a given operating interval as well as other operational limitations.  The HSL shown in the COP for a Generation Resource may not be ramp rate-limited while the Real-Time telemetered value of HSL for the Generation Resource may be ramp rate-limited by the QSE representing the Generation Resource in order for the Generation Resource to meet its HSL using the testing process described in paragraph (2) below.

(2)	To verify that the HSL reported by telemetry is achievable, ERCOT may, at its discretion, conduct an unannounced Generation Resource test.  At a time determined solely by ERCOT, ERCOT will issue a Verbal Dispatch Instruction (VDI) to the QSE to operate the designated Generation Resource at its HSL as shown in the QSE’s telemetry at the time the test is initiated.  The QSE shall immediately upon receiving the VDI release all Ancillary Service obligations carried by the unit to be tested and shall telemeter Resource Status as “ONTEST.”  The QSE shall not be required to start the designated Generation Resource if it is not already On-Line when ERCOT announces its intent to test the Resource.  If the designated Generation Resource is operating at its Low Sustained Limit (LSL) when ERCOT sends the VDI to begin the test, the QSE shall have up to 60 minutes to allow the Resource to reach 90% of its HSL as shown by telemetry and up to an additional 20 minutes for the Resource to reach the HSL shown by telemetry at the time the test is initiated.  This time requirement does not apply to nuclear-fueled Generation Resources.  If the designated Generation Resource is operating between its LSL and 50% of its HSL shown by telemetry when ERCOT begins the test, the QSE shall have 60 minutes for the Resource to reach its HSL.  If the Resource is operating at or above 50% of its HSL shown by telemetry when ERCOT begins the test, the QSE shall have 30 minutes for the Resource to reach its HSL.  Once the designated Generation Resource reaches its HSL, the QSE shall hold it at that output level for a minimum of 30 minutes.  The HSL for the designated Generation Resource shall be determined based on the Real-Time averaged MW telemetered by the Resource during the 30 minutes of constant output.  After each test, the QSE representing the Generation Resource will complete and submit the test form using the Net Dependable Capability and Reactive Capability (NDCRC) application located on the Market Information System (MIS) Secure Area within two Business Days.

(3)	ERCOT may test multiple Generation Resources within a single QSE within a single 24-hour period.  However, in no case shall ERCOT test more than two Generation Resources within one QSE simultaneously.  All Resources On-Line in a Combined-Cycle Configuration will be measured on an aggregate capacity basis.  All QSEs associated with a jointly owned unit will be tested simultaneously.  Hydro and wind generation will be excluded from unannounced generation capacity testing.  ERCOT shall not perform an unannounced Generation Resource test during a Watch or Energy Emergency Alert (EEA) event.  If an unannounced Generation Resource test is underway when a Watch or EEA event commences, ERCOT may cancel the test.

[NPRR588: Replace paragraph (3) above with the following upon system implementation:] (3) ERCOT may test multiple Generation Resources within a single QSE within a single 24-hour period. However, in no case shall ERCOT test more than two Generation Resources within one QSE simultaneously. All Resources On-Line in a Combined-Cycle Configuration will be measured on an aggregate capacity basis. All QSEs associated with a jointly owned unit will be tested simultaneously. Hydro, wind, and PhotoVoltaic (PV) generation will be excluded from unannounced generation capacity testing. ERCOT shall not perform an unannounced Generation Resource test during a Watch or Energy Emergency Alert (EEA) event. If an unannounced Generation Resource test is under way when a Watch or EEA event commences, ERCOT may cancel the test.

(4)	Should the designated Generation Resource fail to reach its HSL shown in its telemetry within the time frame set forth herein, the Real-Time averaged MW telemetered during the test shall be the basis for the new HSL for the designated Generation Resource for that Season.  The QSE shall have the opportunity to request another test as quickly as possible (at a time determined by ERCOT) and may retest up to two times per month.  The QSE may also demonstrate an increased value of HSL by operating the Generation Resource at an Output Schedule for at least 30 minutes.  In order to raise an output schedule above the Seasonal HSL, the QSE may set the Resource telemetered HSL equal to its output temporarily for the purposes of the demonstration tests.  After either a retest or a demonstration test, the MW capability of the Generation Resource based on the average of the MW production telemetered during the test shall be the basis for the new HSL for the designated Generation Resource for that Season.  Any requested retest must take place within three Business Days after the request for retest.

(5)	The telemetered value of HSL for the Generation Resource shall only be used for testing purposes as described in this Section or for system reliability calculations.

(6)	A Resource Entity owning a hydro unit operating in the synchronous condenser fast response mode to provide hydro RRS shall evaluate the maximum capability of the Resource each Season.

(7)	ERCOT shall maintain historical records of unannounced Generation Resource test results, using the information contained therein to adjust the Reserve Discount Factor (RDF) subject to the approval of the appropriate TAC subcommittee.  ERCOT shall report to the Reliability and Operations Subcommittee (ROS) annually or as requested by ROS the aggregated results of such unannounced testing (excluding retests), including, but not limited to, the number and total capacity of Resources tested, the percentage of Resources that met or exceeded their HSL reported by telemetry, the percentage that failed to meet their HSL reported by telemetry, and the total MW capacity shortfall of those Resources that failed to meet their HSL reported by telemetry.

(8)	QSEs who receive a VDI to operate the designated Generation Resource for an unannounced Generation Resource test may be considered for additional compensation under Section 6.6.9, Emergency Operations Settlement.  Any unannounced Generation Resource test VDI that ERCOT issues as a result of a QSE-requested retest will not be considered for additional compensation under Section 6.6.9.

(9)	All unannounced Generation Resource test VDIs will be considered as an instructed deviation for compliance purposes.

(10)	Before the start of each Season, a QSE shall provide ERCOT a list identifying each Controllable Load Resource that is expected to operate in a Season as a provider of Ancillary Service.  Prior to the beginning of each Season, QSEs shall identify the Controllable Load Resources to be tested during the Season and the specific week of the test if known.  Any Controllable Load Resource for which the QSE desires qualification to provide Ancillary Services shall have its Net Dependable Capability verified prior to providing Ancillary Services.

(11)	ERCOT shall verify the telemetry attributes of each qualified Load Resource as follows:

(a)	ERCOT shall annually verify the telemetry attributes of each Load Resource providing RRS using a high-set under-frequency relay.  In addition, once every two years, any Load Resource qualified to provide RRS Service using a high-set under-frequency relay shall test the correct operation of the under-frequency relay or the output from the solid-state switch, whichever applies.  However, if a Load Resource’s performance has been verified through response to an actual event, the data from the event can be used to meet the annual telemetry verification requirement for that year and the biennial relay-testing requirement.

(b)	ERCOT shall periodically validate the telemetry attributes of each Controllable Load Resource.  In the case of an Aggregate Load Resource, ERCOT will follow the validation procedures described in the document titled “Requirements for Aggregate Load Resource Participation in the ERCOT Markets.”  If a QSE fails to meet its telemetry validation requirements, ERCOT may suspend the QSE and/or the Controllable Load Resource from participation in the applicable services or markets.  If disqualified pursuant to this paragraph, a QSE or Controllable Load Resource may reestablish its qualification by submitting a corrective action plan to ERCOT that identifies actions taken to correct performance deficiencies and by successfully passing a new ERCOT telemetry validation test.

(12)	Telemetry values of a Load Resource may be adjusted to reflect Distribution Losses, based on the ERCOT-forecasted Distribution Loss Factors (DLFs).  Load Resources may be adjusted for Distribution Losses using the same distribution loss code as assigned to the ESI ID.

(13)	A specific Load Resource to be used for the first time to provide Regulation, RRS, Non-Spin or energy by following Security-Constrained Economic Dispatch (SCED) Base Points, must be tested to ERCOT’s reasonable satisfaction using actual Demand response as part of its qualification.  The test must take place at a time mutually selected by the QSE representing the Load Resource and ERCOT.  ERCOT shall make available its standard test document for Load Resource qualification required under this Section on the MIS Public Area.

(14)	Any changes to a Load Resource including changes to its capability to provide Ancillary Service requires updates by the Load Resource to the registration information detailing the change.  For Non-Opt-In Entities (NOIEs) representing specific Load Resources that are located behind the NOIE Settlement Metering points, the NOIE shall provide an alternative unique descriptor of the qualified Load Resource for ERCOT’s records.

(15)	Qualification of a Resource, including a Load Resource, remains valid for that Resource in the event of a change of QSE for the Resource, provided that the new QSE demonstrates to ERCOT’s reasonable satisfaction that the new QSE has adequate communications and control capability for the Resource.

(16)	For purposes of qualifying Quick Start Generation Resources (QSGRs), ERCOT shall issue a unit-specific VDI for the MW amount that the QSE is requesting to qualify its QSGR to provide.  The QSE shall telemeter an ONTEST Resource Status.  The QSGR will only be qualified to provide an amount not to exceed the observed output at the end of a ten-minute test period.

(17)	ERCOT may revoke the QSGR qualification of any QSGR for failure to comply with the following performance standard:

(a)	A QSGR, available for deployment by SCED, is deemed to have failed to start for the purpose of this performance measure if the QSGR fails to achieve at least 90% of the minimum ERCOT SCED Base Point, including zero Base Points, within ten minutes of the initial ERCOT SCED Base Point that dispatched the QSGR above zero MW output.

(b)	ERCOT may revoke a QSGR’s qualification if within a rolling 90-day period the number of QSGR failures to start, as determined by paragraph (a) above, exceeds the higher of three failures or 10% of the number of quick start mode startups made in response to SCED deployments.

(18)	If disqualified pursuant to paragraph (17) above, a QSGR may reestablish its QSGR qualification by submitting a corrective action plan to ERCOT that identifies actions taken to correct performance deficiencies and by successfully passing a new ERCOT QSGR test.

- 8.1.1.2.1	Ancillary Service Technical Requirements and Qualification Criteria and Test Methods

(1)	A QSE and the Resource that it represents must be qualified to provide Ancillary Services.  ERCOT shall develop and operate a qualification and testing program that meets the requirements of this Section for each Ancillary Service.  Prior to the Texas Nodal Market Implementation Date, a QSE and the Resources that it represents that are qualified to provide an Ancillary Service in accordance with an effective Protocol, are deemed to be qualified to provide Ancillary Services after the Texas Nodal Market Implementation Date, provided that the QSE and the Resource have been certified capable of providing an Ancillary Service by a responsible Market Participant, as determined by ERCOT.  Resources that are thus certified to provide Ancillary Services and that have a performance history determined in accordance with this Section, and that fail to meet the performance metrics described in this Section on the Texas Nodal Market Implementation Date, or thereafter, will be required to qualify in accordance with this Section before providing the Ancillary Service.

(2)	A QSE and the Resource that it represents must be qualified in accordance with this Section as an Ancillary Service and reserve provider and at ERCOT’s discretion will be required to re-qualify to provide Ancillary Service or reserve if acceptable performance as determined in accordance with this Section has not been maintained.

- 8.1.1.4.2	Responsive Reserve Service Energy Deployment Criteria

(1)	Each QSE providing RRS shall so indicate by appropriate entries in the Resource’s Ancillary Service Schedule and the Ancillary Service Resource Responsibility providing that service.  ERCOT shall adjust the Generation Resource’s Base Point for any requested RRS energy in the next cycle of SCED as specified in Section 6.5.7.6.2.2, Deployment of Responsive Reserve Service.  For Controllable Load Resources, the QSE shall control its Resources to operate to the Resource’s Scheduled Power Consumption minus any Ancillary Service deployments.  Control performance during periods in which ERCOT has deployed RRS shall be based on the requirements below and failure to meet any one of these requirements shall be reported to Texas RE as non-compliance:

(a)	Within one minute following a deployment instruction, the QSE must update the telemetered Ancillary Service Schedule for RRS for Generation Resources and Load Resources to reflect the deployment amount.  The difference between the sum of the QSE’s Resource RRS schedules and the sum of the QSE’s Resource RRS responsibilities must be equal to the QSE’s total RRS deployment instruction, excluding the deployment to Load Resources which are not Controllable Load Resources.

(b)	For QSEs with Load Resources, excluding Controllable Load Resources, ten minutes following deployment instruction, the sum of the QSE’s Load Resource response shall not be less than 95%, nor more than 150% of the requested MW deployment and be maintained until recalled or the Resource’s obligation to provide RRS expires.

[NPRR595: Replace paragraph (b) above with the following upon system implementation:] (b) For QSEs with Load Resources, excluding Controllable Load Resources, ten minutes following deployment instruction the sum of the QSE’s Load Resource response shall not be less than 95% of the requested MW deployment, nor more than 150% of the lesser of the following: - The QSE’s Responsibility for RRS from non-Controllable Load Resources; or - The requested MW deployment. The QSE’s portfolio shall maintain this response until recalled or the Resource’s obligation to provide RRS expires. The combination of the QSE’s RRS responsibility and additional available capacity shall not exceed 150% of the sum of the QSE’s Ancillary Service Resource Responsibility for RRS from non-Controllable Load Resources. Any additional available capacity from Load Resources other than Controllable Load Resources shall be deployed concurrently with RRS Service.

(c)	For Load Resources, excluding Controllable Load Resources, associated with a QSE that does not successfully deploy as defined under this Section, ERCOT shall evaluate, identify and investigate each Load Resource that contributed to such failure, in order to determine failure under paragraph (9) of Section 8.1.1.1, Ancillary Service and Reserves Qualification and Testing.

(d)	A Load Resource providing RRS excluding Controllable Load Resources must return to at least 95% of its Ancillary Service Resource Responsibility for RRS within three hours following a recall instruction unless replaced by another Resource as described below.  However, the Load Resource should attempt to return to at least 95% of its Ancillary Service Resource Responsibility for RRS as soon as practical considering process constraints.  For a Load Resource that is not a Controllable Load Resource that is unable to return to its Ancillary Service Resource Responsibility within three hours of recall instruction, its QSE may replace the quantity of deficient RRS capacity within that same three hours using other Generation Resources or other Load Resources not previously committed to provide RRS.

(e)	During periods when the Load level of a Load Resource (excluding Controllable Load Resources) has been affected by a Dispatch Instruction from ERCOT, the performance of a Load Resource in response to a Dispatch Instruction must be determined by subtracting the Load Resource’s actual Load response from its Baseline.  “Baseline” capacity is calculated by measuring the average of the real power consumption for five minutes before the Dispatch Instruction if the Load level of a Load Resource had not been affected by a Dispatch Instruction from ERCOT.  The actual Load response is the average of the real power consumption data being telemetered to ERCOT during the Settlement Interval indicated in the Dispatch Instruction.

(2)	For all Measurable Events, ERCOT shall use the recorded data for each two-second scan rate value of real power output for each Generation Resource, Controllable Load Resource.  ERCOT shall use the recorded MW data beginning one minute before the start of the frequency excursion event until ten minutes after the start of the frequency excursion event.  Satisfactory performance must be measured by comparing actual Primary Frequency Response to the expected Primary Frequency Response as required in the Operating Guides.

(3)	ERCOT shall monitor the Primary Frequency Response that is delivered during Measurable Events of Generation Resources and Controllable Load Resources, relay response for Loads and hydro RRS at the frequency specified in paragraph (3)(b) of Section 3.18, Resource Limits in Providing Ancillary Service.  Primary Frequency Response performance must be analyzed by TAC and a performance metric must be provided in the Operating Guides.