## Slide 1: Regulation Bias Analysis post SCR-773
PDCWG Meeting 09/10/2014

## Slide 2: Discussion Points
Current GTBD Parameters
Metric to measure Regulation bias and performance
Regulation Deployed comparison (June to August)
Total Regulation (net) Deployed comparison
Regulation Deployed 15-minute interval comparison by each hour for 2012, 2013 and 2014 months
Regulation Exhaustion Rate
Regulation bias for consecutive 5-min interval
Summary

## Slide 3: Metric to measure SCR-773 performance
Trend and monitor the regulation deployed by hour
Set target of 50 MW for total regulation deployed by hour for peak hours (HE 14 to HE 18)
Set target of 85% for the number of intervals where regulation deployment was both up and down (zero crossing) for peak hours (HE 14 to HE 18)
Track the Regulation exhaustion rate for all hours (not to exceed <1.2% )
Using a 50MW filter, target 15 occurrences or less per month for regulation bias of six or more consecutive 5 minute intervals for peak hours (HE 14 to HE 18).

## Slide 4: Current GTBD Parameters

## Slide 5: Regulation Deployed Comparisons
Metric 1
Trend and monitor the regulation deployed by hour

## Slide 6: Regulation Deployed comparison - Table

## Slide 7: Hourly Regulation-Up Deployed Monthly comparison - Chart

## Slide 8: Hourly Regulation-Up Deployed Monthly comparison - Chart

## Slide 9: Hourly Regulation-Up Deployed Monthly comparison - Chart

## Slide 10: Hourly Regulation-Down Deployed Monthly comparison - Chart

## Slide 11: Hourly Regulation-Down Deployed Monthly comparison - Chart

## Slide 12: Hourly Regulation-Down Deployed Monthly comparison - Chart

## Slide 13: Total Regulation Deployed Comparisons
Metric 2
Set target of 50 MW for total regulation deployed by hour for peak hours (HE 14 to HE 18)

## Slide 14: Hourly Total-Regulation Deployed Monthly comparison - Chart
Shut-Down Period

## Slide 15: Hourly Total-Regulation Deployed Monthly comparison - Chart
Shut-Down Period
Peak Hours

## Slide 16: Hourly Total-Regulation Deployed Monthly comparison - Chart
Start-Up Hours
Peak Hours

## Slide 17: 15-Minute intervals where both Reg-Up/Down were deployed
Metric 3
Set target of 85% for the number of intervals where regulation deployment was both up and down (zero crossing) for peak hours (HE 14 to HE 18)

## Slide 18: Regulation Deployed 15-Minute Interval Comparison – by hours

## Slide 19: Regulation Exhaustion Rate
Metric 4
Track the Regulation exhaustion rate for all hours (not to exceed <1.2% )

## Slide 20: Regulation-Up Exhaustion Rate – by hours
0.57% | 1.84% | 1.04%

## Slide 21: Regulation-Up Exhaustion Rate – by hours

## Slide 22: Regulation-Up Exhaustion Rate – by hours
1.09% | 0.64% | 1.89%

## Slide 23: Regulation-Down Exhaustion Rate – by hours
1.12% | 1.51% | 0.74%

## Slide 24: Regulation-Down Exhaustion Rate – by hours
0.71% | 0.45% | 0.54%

## Slide 25: Regulation-Down Exhaustion Rate – by hours
0.71% | 0.63% | 0.56%

## Slide 26: Stats on Reg-Up Bias for consecutive 5-min intervals
Metric 5
Using a 50MW filter, target 15 occurrences or less per month for regulation bias of six or more consecutive 5 minute intervals for peak hours (HE 14 to HE 18*).

## Slide 27: Reg-Up Bias for six Consecutive 5 min intervals (50 MW filter)

## Slide 28: Reg-Up Bias for six Consecutive 5 min intervals (50 MW filter)

## Slide 29: Reg-Up Bias for six Consecutive 5 min intervals (50 MW filter)

## Slide 30: Questions??

## Slide 31: Appendix

## Slide 32
Regulation-Up Deployed by hours

## Slide 33
Regulation-Up Deployed by hours

## Slide 34
Regulation-Up Deployed by hours

## Slide 35
Regulation-Down Deployed by hours

## Slide 36
Regulation-Down Deployed by hours

## Slide 37
Regulation-Down Deployed by hours