| NOGRR Number |  | NOGRR Title | Reactive Power Testing Requirements |
| --- | --- | --- | --- |
| Date Posted |  |
| Requested Resolution | Normal |
| Nodal Operating Guide Sections Requiring Revision | 3.3.2 Unit Reactive Capability Requirements 3.5 ERCOT Implementation |
| Other Binding Documents Requiring Revision or Related Revision Requests | None |
| Revision Description | This Nodal Operating Guide Revision Request (NOGRR) revises the language in Section 3.3.2, Unit Reactive Capability Requirements to harmonize the ERCOT reactive testing requirements with the recently approved NERC Standard MOD-025-1 for reactive testing. |
| Reason for Revision | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |

| Business Case |
| --- |
| Qualitative Benefits | Will eliminate the need for duplicative testing by Generation Resources and IRRs to comply with both ERCOT and NERC requirements. |
| Quantitative Benefits | Duplicative testing could result in significant costs to Resource Entities due to the need for operating in “out of the market” conditions to complete testing. |
| Impact to Market Segments | Impact to all Resource Entities and QSEs which represent Generation Resources and Intermittent Renewable Resources. Will avoid confusion related to training operations staff to perform multiple testing procedures. |
| Other |  |

| Sponsor |
| --- |
| Name | Sherry K. Looney |
| E-mail Address | Sherry.looney@luminant.com |
| Company | Luminant Energy Company LLC |
| Phone Number | 214-875-9278 |
| Cell Number | 469-688-7607 |
| Market Segment | Independently Owned Utility |

| Market Rules Staff Contact |
| --- |
| Name |  |
| E-Mail Address |  |
| Phone Number |  |

Proposed Guide Language Revision

3.3.2	Generator Reactive Capability Requirements

3.3.2.1	Corrected Generator Reactive Limits (CGRL)

The generator reactive capability values for each generator on the ERCOT System shall be submitted to ERCOT through the Market Information System (MIS) Certified Area as part of the resource registration process.  The generator reactive capability diagram normally uses the manufacturer’s capability curve (normally referred to as the “D-Curve”) as a base, and is then modified to include and must contain the most limiting elements for the leading and lagging reactive output at the generator terminals.  The limiting factors such as under-excitation limiters, over-excitation limiters, ambient temperature limitations across the MW range of the generator at its terminals or any other factor that limits the reactive output of the generator and is verifiable through engineering calculations or testing may be produced on the modified reactive capability diagram.  The modified reactive capability diagram establishes the Corrected Generator Reactive Limits (CGRL) at the generator terminals that ERCOT Planning and ERCOT Operations will use for their studies. ERCOT Operations, after reviewing and validating the updated CGRL , will forward copies to the Steady State Working Group (SSWG).  The SSWG members shall have ten Business Days to provide ERCOT Operations any comments regarding updated CGRLs.  If appropriate, the SSWG shall use the updated CGRL in modeling such capability in the ERCOT transmission planning cases.  If ERCOT finds the submitted CGRL does not meet the requirements of Section 3.3.2.2, , ERCOT will follow Section 3.5, ERCOT Implementation.

3.3.2.2	Reactive Testing Requirements

(1)	Reactive testing may be performed as either “Coordinated”, or “Non-Coordinated”, the difference being the amount of notification provided to ERCOT and the TO, and level of their involvement in testing.

(a)	Coordinated Testing

(i)	Coordinated testing is the preferred method for new or larger-capacity units, as it provides a greater amount of coordination with ERCOT and the TO, allowing testing impacts and any potential adjustments to local voltage levels to be studied in advance.

(ii)	The QSE representing the resource requesting a Coordinated test must submit a test request to ERCOT and the TO via their QSE, by no later than 15:00, one day prior to the proposed test date.  ERCOT and the TO then have until 15:00 of the day prior to the proposed test date to either approve or disapprove the test request.

(iii)	Both ERCOT and the TO have the right to deny or cancel a test at any time, if they feel that system reliability may be adversely impacted by the test.

(iv)	The test requests should contain the proposed time and date of the test, type of test (leading or lagging), expected unit MW and MVAR output during the test, and a copy of the CGRL diagram.

(b)	Non-Coordinated Testing

(i)	The QSE representing the resource requesting a Non-Coordinated test must inform ERCOT and the TO at least two hours prior to the proposed start of the test.

(ii)	Both ERCOT and the TO have the right to deny or cancel a test at any time, if they feel that system reliability may be adversely impacted by the test.

(2)	Lagging Reactive Testing

(a)	It is recommended, but not required, that lagging reactive tests be performed when system voltage is low in the normal range, such as during high load periods.

(b)	Laggings tests should meet the following performance criteria:

(i)	Lagging Test 1:  Test at >95% of the Resource’s seasonal HSL (normal expected maximum real power) for at least 1 minute.  IRRs shall test at >60%.  Testing acceptance is if the generator achieved >90% of the generator’s CGRL.

(ii)	Lagging Test 2:  Test at >95% of the Resource’s seasonal HSL (normal expected maximum real power) for at least 1 hour.  IRRs shall test with at least 90% of inverters on-line.  Testing acceptance is if the generator achieved >50% of the generator’s CGRL.

(iii)	Lagging Test 3:  Test at the generators normally expected minimum real power output during light load conditions for at least 1 minute.  Testing acceptance is if the generator achieved >50% of the generator’s CGRL.  IRR and Nuclear units are exempt from this test.

(iv)	Following one successful performance of each of Tests 1, 2 and 3, observed operational data within 2 years of the verification date may be used to fulfill testing requirements, provided that test conditions and acceptance criteria are met.

(3)	Leading Reactive Testing

(a)	Leading tests should meet the following performance criteria:

(i)	Leading Test 1:  Test at the generators normally expected maximum real power output during light load conditions, for at least 1 minute.  Testing acceptance is if the generator achieved >90% of the units CGRL.

(ii)	Leading Test 2:  Test at the generators normally expected minimum real power output during light load conditions for at least 1 minute.  Testing acceptance is if the generator achieved >50% of the generator’s CGRL.  IRR and Nuclear generators are exempt from this test.

(iii)	Following one successful performance of each of Tests 1 and 2, observed operational data within 2 years of the verification date may be used to fulfill testing requirements, provided that test conditions and acceptance criteria are met.

(4)	The Resource Entity shall measure the tested reactive capability of the Generation Resource at those points identified in the test entry screen of the Net Demonstrated Capability Reactive Capability (“NDCRC”) application.  Test results shall be submitted via the NDCRC application in the MIS Certified Area.  All required fields in the application shall be completed.

(5)	The QSE representing a Generation Resource shall be responsible for scheduling reactive verification tests in accordance with the conditions outlined above.  If ERCOT does not issue a specific request for a Generation Resource reactive capability verfication, the Generation Resource shall complete a reactive verification test at least every five years.

(6)	The CGRL should be available in the Resource Entities control room, where the tests are conducted and at the QSE’s Real-Time/generation dispatch desk.  During any test, the Generation Resource must maintain its generator cooling system at normal operating conditions

(7)	The Resource Entity representing a Generation Resource shall be responsible for the timely and accurate reporting of test results to ERCOT and the QSE representing the Resource.  The Resource Entity representing a Generation Resource shall be responsible for the timely submittal to ERCOT of an updated CGRL reflecting any known changes in the reactive output of the Generation Resource.

3.5	ERCOT Implementation

(1)	Reactive test results shall be reviewed by ERCOT to determine the accuracy and consistency of the test data provided, and to determine the appropriateness of generator loading and system conditions during the test.  ERCOT shall have the right to order a re-test of the generator, if it determines there are significant discrepancies with the test data.

(2)	Reactive test results shall be reviewed by ERCOT to determine if the test met the acceptance criteria of Section 3.3.2.2.    If the test fails to meet the acceptance criteria of Section 3.3.2.2,  ERCOT shall have the right to either order the Resource Entity to produce a new CGRL, or to order a re-test of the generator.

(3)	If generator reactive capability appears to be limited to less than 90% of the CGRL by unit controls or relays, ERCOT shall contact the Resource Entity and attempt to resolve the limitation.  ERCOT shall have the right to order the Resource Entity to produce a new CGRL that reflects current operating limits.

(4)	CGRL data validated by test, or any new CGRL produced by a Resource Entity in response to new operating limits, shall be implemented by ERCOT in its operational model within four weeks of receipt and resolution of the data.  ERCOT will provide such data to TSPs as Network Models after validation by ERCOT.

(5)	If any test fails to meet the acceptance criteria of 3.3.2.2, then observed operational data may not be used for subsequent testing until actual performance testing has met the acceptance criteria.