## Slide 1: Voltage Reduction in ERCOT Feasibility Report to ROS
Voltage Reduction Task Force

## Slide 2: Background
Coordinated Testing
  VRTF Report to ROS
  VRTF Test Protocol
  VRTF Testing Q&A
Assessment of Feasibility
    VRTF Frequently Asked Questions
    VRTF ERCOT Applicability and Cost Survey

## Slide 3: Study Questionnaire
Participation
  Full response from 10 entities
  Partial response from 2 entities
  No Response from 3 entities
Gathered data
  Entity-specific approach to voltage reduction
  Applicability without investment
  Applicability with investment (optional multiple scenarios)
  Cost of investment (per scenario)

## Slide 4: Study Questionnaire
Unification of data to represent typical level of investment
  Contact survey participants to provide applicability and cost associated with implementing a voltage reduction program simply using CVR controllers and SCADA communication

## Slide 5: Qualifying the Data
71-76% of ERCOT demand represented
Results based on full responses only
Summary data represents the average value of participants’ responses, weighted by relative size of load
If a range of applicability was given, the lower value was used
If a range of cost was given, the larger cost was used

## Slide 6: Study Summary
Applicability
  Voltage reduction feasible for 13% of participants' demand (10% of ERCOT) without investment
  Voltage reduction feasible for 64% of participants’ demand (46-49% of ERCOT) with investment
  Applicability is limited by lack of LTCs, sensitive customer load, and distribution system limitations

## Slide 7: Study Summary
Benefit and Cost
  Assuming a 2% reduction in demand (depends on voltage reduction; greater than 2% is possible) at VR eligible locations for the 75% of demand represented by the survey:
    520-650 MW reduction over system peak
    This equates to1.3% of participants’ total demand, which is 0.9-1.0% of ERCOT’s total demand
    740-850 MW possible with 100% participation, which would be 1.3% of ERCOT’s total demand
  Estimated average cost per MW over summer peak = $85,800 for survey participants

## Slide 8: Observations
Participants report larger applicability and larger demand reduction possible with additional investment
Entities who have implemented VVO programs reported reduced efforts for implementing a voltage reduction program