| PGRR Number | 042 | PGRR Title | Regional Transmission Plan Model Reserve Requirement and Load-Generation Imbalance Methodology |
| --- | --- | --- | --- |

| Date | July 20, 2015 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Timothy Cook |
| E-mail Address | tcook@crosstexas.com |
| Company | Cross Texas Transmission, LCC (CTT) |
| Phone Number | (636) 534-3250 |
| Cell Number |  |
| Market Segment | Investor Owned Utility (IOU) |

Comments

CTT supports efforts to increase transparency and refine processes used to develop the ERCOT Regional Transmission Plan. However, CTT is concerned that the most recent draft from ERCOT, dated July 2, 2015, may result in unintended consequences of limiting a transmission planner’s ability to perform local and regional transmission planning analysis.  In these comments CTT will limit its focus to three provisions contained in the 7/2/15 ERCOT comments: paragraphs (3)(i) and (3)(ii)(A) of Section 3.1.3, Project Evaluation, and paragraph (7) of Section 3.1.4.1.1, Regional Transmission Plan Cases.

A.       New paragraph (3) of Section 3.1.3 sets forth a methodology for ERCOT to conduct its independent review of Tier 1 and Tier 2 reliability-driven transmission projects, and specifically how ERCOT can account for load/generation imbalances in those studies. New paragraph (3)(i) of Section 3.1.3 proposes that,

(i)  ERCOT shall not decrease the Load from the forecasted level in any of the Weather Zones in which a transmission circuit with an identified reliability criteria violation is located.

This subsection has two fundamental flaws.  First, the subsection presumes ERCOT has identified one or more reliability criteria violations before the study is performed despite the fact that the study is designed to identify such violations.  It is simply impossible to know which circuit or circuits will demonstrate a reliability criteria violation until the study itself is done.  In other words, this subsection would require the transmission planners to know the results of the study before it is performed.  The second flaw is that the requirement established by this subsection does not work for an intertie line, which is exactly what the section is designed to address. In the case of an intertie line, with one terminal in each of two Weather Zones, the identified reliability criteria violation occurs in both Weather Zones. Therefore as written, ERCOT would not be able to decrease Load in either Weather Zone, which could mask reasonably expected reliability violations for lines located in two zones and other violations of lines that reside wholly within one zone.

These flaws are fatal to this subsection and it should therefore be stricken from the proposal.  The very next proposed subsection, paragraph (3)(ii) of Section 3.1.3, also provides more specific guidance and limits on how load and generation may be adjusted.  These specific parameters, in addition to the identified problems, render paragraph (3)(i) of Section 3.1.3 unnecessary.

B.       Newly proposed subsection, paragraph (3)(ii)(A) of Section 3.1.3 describes how load scaling may be conducted, and, if adopted, would read as follows:

(ii)	ERCOT may utilize any of the following to satisfy Load/generation imbalances:

(A)   Reduce Load in the study case outside of the Weather Zones in which the reliability criteria violation of a transmission circuit is located.  The Load scaling in any single Weather Zone shall never reduce the Load in the scaled Weather Zone below its average percentage of peak Load during the top ten hourly peak Load conditions for the past three years of the study Weather Zone.

The first sentence of subpart (A) suffers from the same flaws identified above in paragraph (3)(i) of Section 3.1.3 and should be modified to correct those flaws.  The intent of the second sentence makes sense, that is, the load scaling should be reflective of actual past load conditions.  The subsection proposes to accomplish this goal by taking into account an average of peak Load conditions in the study Weather Zone over ten peak hours over the past three years.  But one problem with the proposed implementation is that an unintended consequence of averaging may be to make the study case less reflective of conditions that may contribute to a reliability concern.  For example, the top ten hourly peak Load conditions for the Weather Zone may not be the ten worst case hours for the condition.  Additionally, if weather in two of the past three years was relatively mild then very hot conditions in the weather zone in the third year would be diluted by averaging.  By design, system reliability analyses are purposed to evaluate performance utilizing boundary operating criteria, based on historical observations or deterministic projections.  These industry-standard techniques allow planners to evaluate a spectrum of stressful yet potential operating conditions.  This methodology promotes high reliability, an unassailable tenet of transmission planning.  Conversely, averages, by their very nature, discount stressful criteria.  The result is a moderated solution, which thereby compromises reliability.

For these principal reasons, if ERCOT decides to proceed with revisions to these provisions of the Planning Guide, CTT requests that the following be adopted in place of the proposed revisions.  (These changes are redlined against the provision quoted above, which incorporates ERCOT’s comments):

(A)  Reduce Load in the study case outside of the Weather Zones in which the reliability criteria violation of a transmission circuit study area is located.  The Load scaling in any single Weather Zone shall never not reduce the Load in the scaled Weather Zone below its smallest average percentage of peak total hourly Load during the top ten hourly peak Load conditions for during the past three years of the study Weather Zone.

C.       CTT also believes there may be unintended consequences using only the ERCOT 90th percentile forecast for the Regional Transmission Plan.  It is important to recognize the knowledge and expertise of the TSPs with regard to forecasting load connected to their respective systems.  ERCOT simply does not possess this knowledge, which provides the TSPs with additional and different insights.  ERCOT’s focus is regional and it has no insight concerning individual TSP load levels. The current “higher of” method used for the study area accounts for this difference in perspective and knowledge and, additionally, given the uncertainty inherent in forecasting, ensures that the ERCOT system is properly and fully stressed for the planning study purpose. CTT contends that using a different load forecast for the Regional Transmission Plan versus the load forecast used for project evaluation (Independent Review) may well result in masking reliability problems. This may further lead to situations where needed solutions cannot be identified within reasonable approval and construction timeframes. To address this inadequacy CTT proposes the following changes to paragraph (7) of Section 3.1.4.1.1.

(7)	The Load utilized in the Regional Transmission Plan reliability base cases shall be organized and evaluated by Weather Zone.  ERCOT shall use the higher of the SSWG Load in each Weather Zone or the ERCOT’s 90th percentile peak Load forecast by Weather Zone, plus self-serve Load, for the study year.each Weather Zone’s 90th percentile peak Load forecast, plus self-serve Load, for the study year.  ERCOT may adjust this Load forecast to reflect specific, publicly known Load additions or subtractions that ERCOT reasonably anticipates.

Revised Cover Page Language

| Planning Guide Sections Requiring Revision | 3.1.1.2, Regional Transmission Plan 3.1.3, Project Evaluation 3.1.3.1, Definitions of Reliability-Driven and Economic-Driven Projects 3.1.4.1, Development of Regional Transmission Plan 3.1.4.1.1, Regional Transmission Plan Cases (new) 3.1.4.2, Use of Regional Transmission Plan |
| --- | --- |

Revised Proposed Guide Language

- 3.1.1.2	Regional Transmission Plan

(1)	The Regional Transmission Plan is developed annually by ERCOT, in coordination with the RPG and Transmission Service Providers (TSPs).  The Regional Transmission Plan addresses regional and ERCOT-wide reliability and economic transmission needs and the planned improvements to meet those needs for the upcoming six years starting with the SSWG base cases.  These planned improvements include projects previously approved by the ERCOT Board, projects previously reviewed by the RPG, new projects that will be refined at the appropriate time by TSPs in order to complete RPG review, and the local projects currently planned by TSPs.  Combined, these projects represent ERCOT’s plan which addresses the reliability and efficiency of the ERCOT System in order to meet North American Electric Reliability Corporation (NERC) Reliability Standards, the Protocols, Operating Guides and this Planning Guide.  Projects that are included in the Regional Transmission Plan are not considered to have been endorsed by ERCOT until they have undergone the appropriate level of RPG Project Review as outlined in Protocol Section 3.11.4, Regional Planning Group Project Review Process, if required.  The process used by ERCOT to develop the Regional Transmission Plan is outlined in Section 3.1.4, Regional Transmission Plan Development Process.

(2)	ERCOT shall post the Regional Transmission Plan to the Market Information System (MIS) Secure Area by December 31 of each year.

(3)	ERCOT shall include in the Regional Transmission Plan report a list of Transmission Facilities that are loaded above 95% of their applicable Ratings for the following conditions:

(a)	Normal system conditions; or

(b)	Following the contingency loss of a single generating unit, transmission circuit, transformer, or common tower outage.

- 3.1.3	Project Evaluation

(1)	ERCOT and the RPG shall evaluate proposed transmission projects using a variety of tools and techniques to ensure that the system is able to meet applicable reliability criteria in a cost-effective manner.  For most proposed projects, several alternatives will be identified to meet the reliability criteria or other performance improvement objectives that the proposed project is designed to meet.  The project alternative with the expected lowest cost over the life of the project is generally recommended, subject to consideration of the expected long-term system needs in the area (as identified in the LTSA), and consideration of the relative operational impacts of the alternatives.

(2)	In some cases, one alternative may be to dispatch the system in such a way that all reliability requirements are met, even without the proposed transmission project or any transmission alternative, resulting in a less efficient dispatch than what would be required to meet the reliability requirements if the proposed project was in place.  Consideration of the merits of this alternative relative to the proposed transmission project is more complex.  To facilitate the discussion and consideration of these alternatives, ERCOT has adopted certain definitions and practices, described in paragraph (4) of Protocol Section 3.11.2, Planning Criteria, and Sections 3.1.3.1, Definitions of Reliability-Driven and Economic-Driven Projects, and 3.1.3.2, Reliability-Driven Project Evaluation below.

(3)	In its independent review of reliability-driven projects classified as Tier 1 or 2 pursuant to Protocol Section 3.11.4, Regional Planning Group Project Review Process, ERCOT shall utilize the following procedures to satisfy Load/generation imbalances for projects intended to solve the reliability criteria violation of a transmission circuit that crosses at least one Weather Zone boundary:

(i)	ERCOT may utilize any of the following to satisfy Load/generation imbalances:

- Reduce Load in the study case outside of the study area.  The Load scaling in any single Weather Zone shall not reduce the Load in the scaled Weather Zone below its smallest percentage of total hourly Load during the past three years

- Increase the Dispatch level of each Wind-powered Generation Resource (WGR) outside the study Weather Zones up to the Seasonal Peak Average Wind Capacity as a Percent of Installed Capacity as defined in Protocol Section 3.2.6.2.2, Total Capacity Estimate.

- Increase the Dispatch level of each PhotoVoltaic Generation Resource (PVGR) outside the study Weather Zones up to the Solar Unit Capacity as defined in Protocol Section 3.2.6.2.2, Total Capacity Estimate.

- Increase the output from the Direct Current Ties (DC Ties) that are not in any of the study Weather Zones to their full Seasonal net max sustainable ratings for DC Tie Resources importing into the ERCOT Region.

- Add any or all Mothballed Generation Resources that have not yet announced their return to service during the study period and that are outside of any study Weather Zone.

- Add any or all proposed Generation Resources that are outside of any study Weather Zone and have signed Standard Generation Interconnection Agreements (SGIAs) but have not yet met the other requirements of Section 6.9, Addition of Proposed Generation Resources to the Planning Models.

(4) 	For informational purposes only, as part of its independent review of projects classified as Tier 1 or 2 pursuant to Protocol Section 3.11.4, Regional Planning Group Project Review Process, ERCOT shall perform a sensitivity analysis to evaluate the effect on a recommended transmission project of proposed Generation Resources in the area of the study that have signed SGIAs but were not included in the study cases.

- 3.1.3.1	Definitions of Reliability-Driven and Economic-Driven Projects

(1)	Proposed transmission projects are categorized for evaluation purposes into two types:

(a)	Reliability-driven projects; and

(b)	Economic-driven projects.

(2)	The differentiation between these two types of projects is based on whether a simultaneously-feasible, security-constrained generating unit commitment dispatch is expected to be available for all hours of the planning horizon that can resolve the system reliability issue that the proposed project is intended to resolve.  If it is not possible to simulate a dispatch of the Generation Resources such that all reliability criteria are met without the project, and the addition of the project allows the reliability criteria to be met, then the project is classified as a reliability-driven project.  If it is possible to simulate a dispatch of the Generation Resources in such a way that all reliability criteria are met without the project, but the project may allow the reliability criteria to be met at a lower total cost, then the project is classified as an economic-driven project.  When performing a simulation of the generating unit commitment and dispatch, only contingencies and limits that would be considered in the operations horizon shall be simulated.

- 3.1.4.1	Development of Regional Transmission Plan

(1)	The planning process begins with computer modeling studies of the generation and Transmission Facilities and substation Loads under normal conditions in the ERCOT System.  Contingency conditions along with changes in Load and generation that might be expected to occur in operation of the ERCOT Transmission Grid are also modeled.  To maintain adequate service and minimize interruptions during Outages, model simulations are used to identify adverse results based upon the planning criteria and to examine the effectiveness of various problem-solving alternatives.

(2)	The effectiveness of each alternative will be evaluated under a variety of possible operating environments because Loads and operating conditions cannot be predicted with certainty.  As a result, repeated simulations under different conditions are often required.  In addition, options considered for future installation may affect other alternatives so that several different combinations must be evaluated, thereby multiplying the number of simulations required.

(3)	Once feasible alternatives have been identified, the process is continued with a comparison of those alternatives.  To determine the most favorable, the short-range and long-range benefits of each alternative must be considered including operating flexibility and compatibility with future plans.

- 3.1.4.1.1	Regional Transmission Plan Cases

(1)	The starting base cases for the Regional Transmission Plan development are created by removing all Tier 1, 2 and 3 projects that have not undergone RPG Project Review from the most recent SSWG base cases to address the planning horizon.

(2)	ERCOT shall set all non-seasonal Mothballed Generation Resources to out of service in the Regional Transmission Plan reliability base cases. ERCOT shall add proposed Generation Resources that have met the criteria for inclusion according to Section 6.9, Addition of Proposed Generation Resources to the Regional Transmission Plan cases.

(3)	In the Regional Transmission Plan reliability base cases, ERCOT shall set the output from the DC Ties at the Seasonal net max sustainable ratings for DC Tie Resources as defined in Protocol Section 3.2.6.2.2, Total Capacity Estimate.

(4)	In the Regional Transmission Plan reliability base cases, ERCOT shall dispatch hydro Generation Resources up to the Hydro Unit Capacity as defined in Protocol Section 3.2.6.2.2, Total Capacity Estimate.

(5)	In the Regional Transmission Plan economic base cases, 8,760-hour profiles shall be used for hydro Generation Resources, WGRs, PVGRs and DC Ties.  ERCOT profiles shall be used for WGRs and PVGRs.  Average historical output for the past three years shall be used to create the hydro Generation Resource and DC Tie profiles.

(6)	ERCOT shall update the Regional Transmission Plan reliability and economic base cases to reflect any updates to the amount of Switchable Generation Resource capacity available to the ERCOT Region.

(7)	The Load utilized in the Regional Transmission Plan reliability base cases shall be organized and evaluated by Weather Zone.  ERCOT shall use the higher of the SSWG Load in each Weather Zone or the ERCOT’s 90th percentile peak Load forecast by Weather Zone, plus self-serve Load, for the study year.  ERCOT may adjust this Load forecast to reflect specific, publicly known Load additions or subtractions that ERCOT reasonably anticipates.

(8)	If the total generation capacity in a Regional Transmission Plan reliability base case is less than the peak Load in the case plus losses plus an operating reserve equal to the two largest units in the case, ERCOT shall group one or more Weather Zones into no fewer than four study regions and create a separate base case for each study region for the season and year being studied.

(a)	ERCOT shall not change Load or total generation capacity inside a study region.  ERCOT may redispatch dispatchable Generation Resources inside a study region as necessary.

(b)	ERCOT shall use the following procedures in the order listed below to balance the case:

(i)	ERCOT shall reduce Load outside of the study region such that the total load in the case is approximately equal to ERCOT’s 90th percentile system-wide coincident peak Load forecast plus self-serve Load.

(ii)	ERCOT may increase the Dispatch level of each WGR and PVGR outside the study region to a level that does not exceed the following maximums.

(A)	For a WGR, the maximum Dispatch level is the Seasonal Peak Average Wind Capacity as a Percent of Installed Capacity as defined in Protocol Section 3.2.6.2.2, Total Capacity Estimate.

(B)	For a PVGR, the maximum Dispatch level is the Solar Unit Capacity as defined in Protocol Section 3.2.6.2.2, Total Capacity Estimate.

(iii)	If the Load reductions in paragraph (8)(b)(i) are still not enough to balance the case, Load outside the study region may be reduced to a level sufficient to balance the case.

- 3.1.4.2	Use of Regional Transmission Plan

(1)	If a project submitted for RPG review is included in the Regional Transmission Plan, and no changes are identified which would affect the need for the proposed project through the 21-day comment period described in Section 3.1.5, Regional Planning Group Comment Process, then the Regional Transmission Plan may serve as the ERCOT Independent Review of the proposed project, if required.

(2)	Tier 1, 2, and 3 projects that are included in the Regional Transmission Plan should be submitted for RPG Project Review at an appropriate lead time.  Generally, this lead time should be sufficient to allow the review to be completed before the TSP reaches the decision point at which it must initiate the engineering and procurement in order to meet the required in-service date, but not farther in advance than is necessary.  In general, these lead times will be three to four months for Tier 3 projects and six to seven months for Tier 1 and 2 projects.

(3)	Tier 1, 2 and 3 projects that are included in the Regional Transmission Plan but do not reach this decision point before the development of the next year’s Regional Transmission Plan begins will be removed from the case used to develop the Regional Transmission Plan and will be re-evaluated as a part of the development of this subsequent Regional Transmission Plan.