| NPRR Number | 713 | NPRR Title | Reactive Power Testing Requirements |
| --- | --- | --- | --- |
| Date of Decision |  | July 16, 2015 |  |
| Action |  | Tabled |  |
| Timeline |  | Normal |  |
| Proposed Effective Date |  | To be determined. |  |
| Priority and Rank Assigned |  | To be determined. |  |
| Nodal Protocol Sections Requiring Revision |  | 8.1.1.2.1.4, Voltage Support Service Qualification |  |
| Related Documents Requiring Revision/Revision Requests |  | Nodal Operating Guide Revision Request (NOGRR) 147, Reactive Power Testing Requirements. |  |
| Revision Description |  | This Nodal Protocol Revision Request (NPRR) revises the language in Section 8.1.1.2.1.4 to reference the Reactive Power testing requirements in the Nodal Operating Guides and reflect the revisions to harmonize the Nodal Protocol requirements with recently approved North American Electric Reliability Corporation (NERC) Reliability Standards. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | Implementation of these changes will eliminate the need to have duplicative reactive test procedures for satisfying the regulatory requirements of the ERCOT Protocols, Nodal Operating Guides, and the NERC Reliability standards. These duplicative procedures would cause confusion in training and operating procedures for the plant personnel who perform the testing in the field. The change of the periodicity of testing from two to five years will decrease the probable number of hours when Generation Resources may be required to run uneconomically to comply with testing requirements.. |  |
| Credit Work Group Review |  | To be determined. |  |
| PRS Decision |  | On 7/16/15, PRS unanimously voted to table NPRR713 for one month and refer the issue to ROS. All Market Segments were present for the vote. |  |
| Summary of PRS Discussion |  | On 7/16/15, participants agreed that additional review at ROS could be beneficial and requested that ROS have a recommendation for review at next month’s PRS meeting. |  |

| Sponsor |  |
| --- | --- |
| Name | Sherry K. Looney |
| E-mail Address | Sherry.looney@luminant.com |
| Company | Luminant Energy Company, LLC |
| Phone Number | 214-875-9278 |
| Cell Number | 469-688-7607 |
| Market Segment | Investor Owned Utility (IOU) |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Brian Manning |
| E-Mail Address | Brian.manning@ercot.com |
| Phone Number | 512-248-3937 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| None. |  |

Market Rules Notes

None.

Proposed Protocol Language Revision

8.1.1.2.1.4	Voltage Support Service Qualification

(1)	The Resource Entity must verify and maintain its stated Reactive Power capability for each of its Generation Resources providing Voltage Support Service (VSS), as required by the Operating Guides.  Generation Resources providing VSS reactive capability limits shall be specified considering nominal substation voltage.

(2)	The Resource Entity shall conduct reactive capacity qualification tests to verify the maximum leading and lagging reactive capability of all Generation Resources required to provide VSS.  Reactive capability tests are performed during the resource commissioning process and at a minimum of once every five years or within 12 months following the discovery of a change that affects its Real Power or Reactive Power capability by more than 10 percent of the last reported verified capability and is expected to last more than 6 months.  ERCOT may require additional testing if it has information indicating that current data is inaccurate.  The Resource Entity is not obligated to place Generation Resources On-Line solely for the purposes of testing.  The reactive capability tests must be conducted at a time agreed to in advance by the Resource Entity, its QSE, the applicable TSP, and ERCOT.

(3)	Leading and lagging reactive operating limits must be demonstrated following the reactive power verification test procedure as more fully described in Nodal Operating Guides Section 3.3.2, Unit Reactive Capability Requirements.  Generation Resources that are classified as Intermittent Renewable Resources (IRRs) shall be tested when generating generating as more fully described in Nodal Operating Guides Section 3.3.2, Unit Reactive Capability Requirements.

(4)	The Resource Entity shall perform the Automatic Voltage Regulator (AVR) tests and shall supply AVR data as specified in the Operating Guides.  The AVR tests must be performed on initial qualification.  The AVR tests must be conducted at a time agreed on in advance by the Resource Entity, its QSE, the applicable TSP and ERCOT.