## Slide 1
FAST CBA AS Quantities

## Slide 2: Current and proposed Future Ancillary Services
Regulation Up
Fast-Responding Regulation Up
Current
Proposed
Fast Frequency Response 1
Primary Frequency Response
Contingency Reserves 1
Synchronous Inertial Response
Supplemental Reserves 1
Mostly unchanged
59.8 Hz, Limited duration
59.7 Hz, Longer duration
Fast Frequency Response 2
Contingency Reserves 2
SCED-dispatched
Manually dispatched
Supplemental Reserves 2
SCED-dispatched
Manually dispatched
Ongoing development
Non-Spin
Responsive
Regulation Down
Fast-Responding Regulation Down
Regulation Up
Fast-Responding Regulation Up
Regulation Down
Fast-Responding Regulation Down

## Slide 3: RRS, PFR/FFR Quantities
Quantities are based on hourly system inertia from 2016 simulation in Plexos, 8760 values
Hourly system inertia is matched to one of 12 cases and corresponding RRS, PFR/FFR quantities and FFR to PFR equivalency ratio are selected for each hour.
Minimum RRS from generation or minimum PFR is based on NERC BAL-003 IFRO
 | Case1 | Case2 | Case3 | Case4 | Case5 | Case6 | Case7 | Case8 | Case9 | Case10 | Case11 | Case12
Inertia, GWs | 120 | 136 | 152 | 177 | 202 | 230 | 256 | 278 | 297 | 316 | 332 | 350
Eq. Ratio | 2.2 | 2 | 1.5 | 1.4 | 1.3 | 1.25 | 1.13 | 1.08 | 1 | 1 | 1 | 1
PFR Requirement (no FFR), MW | 5200 | 4700 | 3750 | 3370 | 3100 | 3040 | 2640 | 2640 | 2240 | 2280 | 2140 | 2140
Min PFR Requirement, MW | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240

## Slide 4: Assumptions RRS Vs PFR/FFR
 | Current -2016 | FAS-2016
Minimum RRS / Minimum PFR | 1240 MW | 1240 MW
RRS quantities w/o Load Resources on UFR / PFR quantities w/o FFR | Same Quantity in Current and FAS | Same Quantity in Current and FAS
FFR1 participation | NA | 0
Load Resources on UFR / FFR participation | Limited to 50%, considering Equivalency Ratio | Beside minimum PFR, the rest can come from FFR
Load Resources participation factor | applied | applied
Limit on Generators | 20% of HSL | 20% of HSL

## Slide 5: Regulation Quantities (FAS/Current)
Regulation quantities are determined for hours 1-24 for every month, as per current AS methodology;
Hourly Load/Wind/Solar outputs in the 2016-basecase were interpolated into minute-by-minute profiles
Regulation requirement is based on 98.8th percentile of 5-min change in net load (load-wind generation-solar generation)
Regulation quantities are identical for Current and Future AS framework

## Slide 6: Contingency Reserve Service – FAS Only
For 12 inertia cases ERCOT identified the lowest settling frequency (point B) based on a single unit trip, with frequency nadir above 59.7 Hz, i.e. no tripping Load Resources on UFR
CRS requirements are calculated as amount of reserves required to restore frequency within normal bounds
For each hour, based on inertia conditions identify CRS requirement as:
CRS Req=(fnormal-fpoint B)*bias*10
 | Case1 | Case2 | Case3 | Case4 | Case5 | Case6 | Case7 | Case8 | Case9 | Case10 | Case11 | Case12
Inertia, GWs | 120 | 136 | 152 | 177 | 202 | 230 | 256 | 278 | 297 | 316 | 332 | 350
Eq. Ratio | 2.2 | 2 | 1.5 | 1.4 | 1.3 | 1.25 | 1.13 | 1.08 | 1 | 1 | 1 | 1
Point B frequency, Hz | 59.8 | 59.79 | 59.79 | 59.79 | 59.77 | 59.78 | 59.77 | 59.78 | 59.76 | 59.75 | 59.75 | 59.76
Notes: Bias is assumed as 1% of system load at the time

## Slide 7: NSRS- Current AS
NSRS is determined for 6 four-hourly blocks for each month as per current AS methodology
NSRS is determined as 95th percentile of net load forecast error (load forecast error- wind forecast error) minus corresponding regulation-up requirement
The maximum of NSRS is set at 2000 MW and with a floor at 1375MW for peak hours.
Notes: Peak hours - H7-H22 in each month

## Slide 8: SRS – FAS Only
SRS is determined based on 95th percentile of net load forecast error minus the other upwards ancillary service capacity.
No concept of floors
Out of 8760 Hours, only 67 hours had non-zero SRS requirements