| NOGRR Number | 144 | NOGRR Title | Incorporation of “Manual Deployment and Recall of Responsive Reserve Service during Scarcity Conditions” into the Nodal Operating Guides |
| --- | --- | --- | --- |

| Date | July 23, 2015 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Sandip Sharma / Jimmy Hartmann |
| E-mail Address | sandip.sharma@ercot.com / jimmy.hartmann@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-4298 / 512-248-6986 |
| Cell Number |  |
| Market Segment | Not applicable. |

Comments

ERCOT submits these comments to align the language in this NOGRR with the Other Binding Document “ERCOT Methodologies for Determining Ancillary Service Requirements.”  ERCOT has changed the amount of Responsive Reserve (RRS) service procured under the 2015 Ancillary Service methodology and therefore is no longer transferring 500 MW of Non-Spinning Reserve (Non-Spin) to RRS.  These comments are intended to better align with the new RRS requirements and address required actions during scarcity conditions identified in paragraph (1) of Section 4.8, Responsive Reserve Service During Scarcity Conditions.

Revised Cover Page Language

None at this time.

Revised Proposed Guide Language

- 4.8	Responsive Reserve Service During Scarcity Conditions

- (1)	This Section details how Responsive Reserve (RRS) service may be manually deployed, also referred to as release of High Ancillary Service Limit (HASL), during scarcity conditions, pursuant to Protocol Section 6.5.7.6.2.2, Deployment of Responsive Reserve Service.  The existing measure of scarcity is Physical Responsive Capability (PRC) and spinning reserves.  If PRC and spinning reserves drop below 3,000 MW, this process may be used.  Scarcity conditions may occur during the Peak Load Season when ERCOT System Load is above 60,000 MW.  For all other months, they could occur when ERCOT System Load is above 50,000 MW.

- 4.8.1	Responsive Reserve Service Manual Deployment

(1)	RRS for capacity may be manually deployed (HASL released) when the system approaches scarcity conditions so that the capacity reserved behind HASL will be released to Security-Constrained Economic Dispatch (SCED). The capacity may be released under any of the following conditions:

(a)	When HASL – (Gen + 5 minute load ramp) <= 200 MW, deploy 500 MW of the available RRS capacity from Generation Resources and Controllable Load Resources after all the available Non-Spinning Reserve (Non-Spin) service has been deployed;

(b)	Additional RRS capacity from Generation Resources and Controllable Load Resources may be deployed in 500 MW increments, as available, when HASL – (Gen + 5 minute load ramp) <= 200 MW and Resources have responded to any earlier deployments; or

(c)	When PRC <= 2,000 MW, release all remaining RRS capacity from Generation Resources and Controllable Load Resources after all the available Non-Spin has been deployed.

- 4.8.2	Responsive Reserve Service Manual Recall

- The manual deployment of RRS for capacity from Generation Resources and Controllable Load Resources may be recalled when HASL – (Gen + 5 minute load ramp) > 1,600 MW and/or PRC >= 3,300 MW.

(2)	The operator will consider system conditions and Ancillary Services in releasing or recalling RRS.  System frequency, load ramp, and factors such as Regulation Up Service (Reg-Up) versus Regulation Down Service (Reg-Down) deployment status will be considered.