## Slide 1: JDOA Update on March 2015 SMT Outage
RMS – August 4, 2015
Bobby Roberts
On Behalf of the SMT Management Committee

## Slide 2: Recap: Outage Dates/Times and Statistics
Outage Start Date/Time:
03/21/2015 07:32 AM Login to SMT Portal unavailable
03/21/2015 01:30 PM All SMT services were impacted
Outage End Date/Time:
03/22/2015 06:00 PM FTPS restored in the new PROD environment
(1 day, 4 hours 30 minutes)
04/07/2015 11:00 AM Systems were back online in the old PROD environment
(15 days, 21 hours 30 minutes)
04/28/2015 12:00 PM Full data restoration completed in the old PROD environment
(37 days, 22 hours 30 minutes)

## Slide 3: Outage Cause
Issue: Hardware Failure
Failure of the 2-node SAN cluster began with an SVC microcode issue that resulted in the corruption of the configuration data used by the entire SAN cluster. The configuration data identified the path and location of each physical/logical disk in the SAN. Despite numerous attempts, the SAN configuration information could not be restored and a full database restoration would be required.
Action Plan:
Hardware Refresh. Includes a 4-node SVC for greater redundancy. [COMPLETE]
Identify and document additional failure scenarios and recovery plans. [COMPLETE]
Quarterly validation of the end-of-life/end-of-service dates for all components of the infrastructure. [ONGOING]

## Slide 4: Factors that Contributed to the Outage Duration
Issue: Database Size
One of the larger databases supported by IBM, any manipulation of the ~20TB takes a significant amount of time.
Action Plan:
Review historical database performance and table indexes. [COMPLETE]
Evaluate and redesign the archival policy. [COMPLETE]
Evaluate database restructuring options. [COMPLETE]
Separate 12-month database history onto a separate SAN. [COMPLETE]
Implement regular health-checks with Oracle SMEs. [ONGOING]

## Slide 5: Factors that Contributed to the Outage Duration (Cont.)
Issue: Incomplete Backups
A key database table had been missing from previous backups due to an inadvertent change made during a routing change window. This caused the full backups to be incomplete and therefore required a large number of archive files to be used for database restoration.
Action Plan:
Review and validate the backup and monitoring processes. [COMPLETE]
Implement a process to ensure the validity of all backups. [COMPLETE]

## Slide 6: Factors that Contributed to the Outage Duration (Cont.)
Issue: Unavailability of DR
DR was not kept current as it was used to finalize development and testing of SMT Release 4.3 (3rd Party). This included the application code as well as maintenance patches for the software and hardware.
Action Plan:
Separate the Stage environment from DR. Built-in to new infrastructure. [COMPLETE]
Ensure that multiple major development efforts are not concurrently underway. [ONGOING]

## Slide 7
Questions?