## Slide 1
Section 5.9 – added export language
    Each ERS Generator site must have an interconnection agreement with its TDSP prior to submitting an ERS offer and must have exported energy to the ERCOT grid prior to the offer due date. An ERS Resource that cannot inject energy to the ERCOT System can only be offered as an ERS Load.
Section 5.12 – remove and the Fuel Type
  For each site in an ERS Load with a backup generator used to provide some or all of the demand response, for each site in an ERS Load with a DRG, and for each site in an ERS Generator, the QSE must specify the nameplate MW of the generator. and the fuel type .
Section 5.26 – remove words “the baseline selection”
    QSEs may not change the price, the MW capacity, the baseline selection, or the declared maximum base Load of an ERS Resource after the offer is submitted.
Edits made by ERCOT after the release for Stakeholder review

## Slide 2
Edits made by ERCOT after the release for Stakeholder review
Section 11.13 – clarified self-test and planned maintenance form submission & modify revision language to be similar to that of ERS Loads
    If the QSE elects to notify ERCOT of self-test schedules and/or planned maintenance, the QSE must submit the required forms to submission forms are required to be received by ERCOT no later than two Business Days prior to the start of an ERS Standard Contract Term, QSEs representing ERS Generators shall submit the following information:
Section 14.4 – clarified split deployment language
  Edited to align more closely with Protocol language is 6.5.9.4.2
Section 19.12 thru 19.17 – reinsert reinstatement language
  A complete import of the reinstatement language from the Feb-May 2014 TRSOW document.

## Slide 3
Significant Items Added or Changed
Sections 8.5, 8.6 Treatment of sites with Distributed Renewable Generation (DRG)
Section 8.11 - Change P.E Affidavits for meter data submission
Section 13 - Supplemental Resources

## Slide 4
Various formatting changes
Section 5.9 - Language regarding ERS Generators having to be energized prior to offer submission; evidence of export
Section 5.22 & 20.2 - Language prohibiting ERS Capacity to be dually committed to provide other services including participating in SCED
Section 11.4 – Notification requirements for revising scheduled periods of unavailability for ERS Loads
Section 18 – Test cycle changed from 365 to 330 days
Section 19.7 – Clarification of two consecutive test failures
Other Lesser Changes

## Slide 5
Comments Received with ERCOT’s Response
Section 5.26 – Under Offer Submission
  QSEs may not change the price, the MW capacity, the baseline selection, or the declared maximum base Load of an ERS Resource after the offer is submitted. absent a request to do so for good cause and agreement by ERCOT to accept the change.
  Why is there no ability to request a change “for good cause”?
    ERCOT Response: All offers are binding when submitted. In no case will ERCOT accept a change in price or capacity after submittal. “the baseline selection,” was removed because there is a circumstance when the baseline can be changed during the course of the SCT.
  If an ERS Resource performance is better under a different baseline, can the baseline be changed after a deployment or test?
    ERCOT Response: If the baseline assignment on the offer is limited to “alternate” because of insufficient interval data history the QSE can request a re-evaluation of the baseline and use of a default baseline if allowed. No other baseline changes are allowed

## Slide 6
Section 11.2, 11.13 & 12 regarding a schedule of planned maintenance and unavailability for ERS Loads or Generators.
  Recommendation that 2 days notice is sufficient. Maintenance activities are more frequently scheduled with 2 days notice than 5.
    ERCOT Response: ERCOT agrees to shorten the notice requirement to 3 days. ERCOT’s judgment is that allowing less than 3 days notice would unduly reduce the effectiveness of ERS by enabling providers to submit unavailability/planned maintenance time in anticipation of periods of scarcity. Self-deployment during those periods would go un-penalized and would override ERCOT Operation’s ability to dispatch that capacity when needed for reliability.
Comments Received with ERCOT’s Response

## Slide 7
Comments Received with ERCOT’s Response
Section 15 – ERS Time Period Availability Calculations
  Proposes that availability be calculated as the ratio of available 15min intervals divided by the total number of 15min intervals in an ERS time period. Measuring by 15min will more accurately reflect our times of unavailability vs. penalizing us for an entire hour.
    ERCOT Response: This would be in conflict with the protocols
  If the above cannot be achieved, then propose the deletion of “containing intervals” in section 15.4(b)(ii). This change will more closely align with how Loads are measured (e.g. Average load over the hour, not 15min interval).
    ERCOT Response: This would be in conflict with the protocols

## Slide 8
Section 15.4, treating self-tests of generators as unannounced tests.
  Can ERS loads also get treatment of self tests as unannounced tests?
    ERCOT Response: Allowing self-tests for ERS Loads would create a significant administrative burden on ERCOT staff and provide little to no benefit to ERS providers.
Section 18 Testing
  What is the reason for lowering the test cycle from 365 to 330 days?
    ERCOT Response: To allow an ERS Resource that was tested one year earlier to be tested in a batch with other ERS Resources that will be tested during the current SCT. This would eliminate the need to do many more tests during a SCT, while allowing once-a-year testing.
Section 18.1 – Testing for Weather Sensitive ERS Resources
  May the frequency of testing be reduced to no more than once a month and maximum duration of test be limited to 30 minutes?
    ERCOT Response: No, these are both protocol requirements for Weather Sensitive Loads (NP 8.1.3.2 (1)(b)).
Comments Received with ERCOT’s Response