| NOGRR Number | 147 | NOGRR Title | Reactive Power Testing Requirements |
| --- | --- | --- | --- |

| Date | August 13, 2015 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Scot Williams |
| E-mail Address | scotwilliams@oncor.com |
| Company | Oncor Electric Delivery |
| Phone Number | 214-743-6674 |
| Cell Number | 214-793-1881 |
| Market Segment | Transmission Owner (TO) |

Comments

Oncor Electric Delivery (Oncor) appreciates the opportunity to work with Luminant and others in modifying ERCOT reactive power testing requirements in the Nodal Operating Guides and reflect the revisions to harmonize the Nodal Protocol requirements with recently approved North American Electric Reliability Corporation (NERC) Reliability Standards. Following are some suggested revisions to the Luminant draft that are reflective of current ERCOT practices and our internal review of NERC MOD-025-2.

Revised Cover Page Language

None at this time.

Proposed Guide Language Revision

- 3.3.2.1	Corrected Unit Reactive Limits (CURL)

A reactive capability curve for each unit on the ERCOT System shall be submitted to ERCOT through the Market Information System (MIS) Certified Area and must contain the most limiting elements for the leading and lagging reactive output.  The limiting factors such as under-excitation limiters, over-excitation limiters, ambient temperature limitations across the MW range of the unit at the unit terminals or any other factor that limits the reactive output of the unit and is verifiable through engineering calculations or testing shall be updated and provided on the corrected reactive capability curve.  The corrected reactive capability curve establishes the Corrected Unit Reactive Limits (CURL) at the unit terminals that ERCOT Planning and ERCOT Operations will use for their studies. For IRR’s the CURL data shall be reported at the low side of the generator step up transformer to the point of interconnection.

Resources will provide updated reactive capability to ERCOT by submitting test information and updated CURLs to the Net Dependable Capability and Reactive Capability (NDCRC) application located on the Market Information System (MIS) Secure Area.  Once approved by ERCOT per Section 3.5, ERCOT Implementation, Resources will provide updated curves for future Network Operations Models by submitting changes to the appropriate ERCOT registration forms in accordance with Planning Guide 6.8.2 (9). ERCOT  and forward these changes to the Steady State Working Group (SSWG) for use in their studies. The CURL should be available in the Resource Entities control room where the tests are conducted and at the QSEs Real Time generation dispatch desk.  During any test, the Generation Resource must maintain its generator cooling system at normal operating conditions, the automatic voltage regulator in service and all auxiliary equipment in service that’s needed for expected normal operation..

- 3.3.2.2	Reactive Testing Requirements

(1)	Reactive testing may be performed as either “Coordinated”, or “Non-Coordinated”, the difference being the amount of notification provided to ERCOT and the TO, and level of their involvement in testing.

(a)	Coordinated Testing

(i)	Coordinated testing is the preferred method for new or larger-capacity units, as it provides a greater amount of coordination with ERCOT and the TO, allowing testing impacts and any potential adjustments to local voltage levels to be studied in advance.

(ii)	The Resource Entity requesting a Coordinated test must submit a test request to ERCOT and the TO via their QSE, by no later than 15:00, one day prior to the proposed test date.  ERCOT and the TO then have until 17:00 of the day prior to the proposed test date, to either approve or disapprove the test request.

(iii)	Both ERCOT and the TO have the right to deny or cancel a test at any time, if they feel that system reliability may be adversely impacted by the test.

(iv)	The test requests should contain the proposed time and date of the test, type of test (leading or lagging), expected unit MW and MVAR output range during the test, and a copy of the reactive capability curve.

(b)	Non-Coordinated Testing

(i)	The Resource Entity representing the resource requesting a Non-Coordinated test must inform ERCOT and the TO via their QSE at least two hours prior to the proposed start of the test.

(ii)	Both ERCOT and the TO have the right to deny or cancel a test at any time, if they feel that system reliability may be adversely impacted by the test.

(2)	Reactive Testing at Maximum MW Output

(a)	It is recommended, but not required, that lagging reactive tests be performed when system voltage is at or below the ERCOT currently scheduled voltage (Voltage Profile)  and when ERCOT System Loads are typically high, such as during the months of May through September, but not necessarily at the time of system peak.

(b)	Laggings tests should meet the following performance criteria:

(i)	Test 1:  Test the unit’s Summer Sustained HSL MW output for at least 1 hour. IRRs should test with at least 90% of wind turbines or photovoltaic inverters on-line. Testing acceptance criteria is met if the unit achieved >90% of the submitted Resource Asset Registration Form (RARF) Summer Sustained HSL value.

(ii)	Test 2:  Test at >95% of the unit’s Summer Sustained HSL for at least 1 hour.  IRRs should test at >60% of Summer Sustained HSL.  Testing acceptance criteria is met if the unit maximum Lagging Gross MVAR minus Auxilliary MVAR achieved >90% of the unit’s CURL.

(iii)	Test 3:  Test at >95% of the unit’s Summer Sustained HSL for at least 1 minute.  IRRs should test at >60% of Summer Sustained HSL.  Record the unit maximum Leading Gross MVAR and Auxilliary MVAR at this real power output level.

(iv)	Test 4:  Test at >95% of the unit’s Summer Sustained HSL for at least 15 minutes.  IRRs should test at >60% of Summer Sustained HSL.  Testing acceptance criteria is met if the unit Lagging Net MVAR at the POI achieved >0.328 times Summer Sustained HSL MW output (0.95 Power Factor requirement).

(v)	Following one successful performance of each of Tests 1, 2, 3 and 4, observed operational data within 2 years of the verification date may be used to fulfill testing requirements, provided that test conditions and acceptance criteria are met.

(3)	Reactive Testing during Low System Load Conditions

(a)	It is recommended, but not required, that leading reactive tests be performed when system voltage is at or above the ERCOT currently scheduled voltage (Voltage Profile) and when ERCOT System Loads are closer to minimum load conditions.

(b)	 Reactive tests should meet the following performance criteria:

(ii)

(i)	Test 1:  Test at the unit’s normally expected real power output typical during system light load conditions for at least 15 minutes.  Testing acceptance criteria is met if the unit maximum Leading Gross MVAR plus Auxiliary MVAR achieved >90% of the units CURL. Nuclear Units are not required to reduce to minimum Real Power output level to perform these tests.

(ii)	Test 2:  Test at the unit’s normally expected real power output typical during system light load conditions for at least 15 minutes.   Record the unit maximum Lagging Gross MVAR and Auxiliary MVAR at this real power output level.

(iii)	Test 3:  Test at the unit’s normally expected real power output typical during system light load conditions for at least 15 minutes. IRRs should test at <60% of Seasonal HSL.  Testing acceptance criteria is met if the unit maximum Leading Net MVAR at the POI achieved <-0.328 times Seasonal HSL MW output (0.95 Power Factor requirement).

(iv)	Following one successful performance of each of Tests 1, 2 and 3, observed operational data within 2 years of the verification date may be used to fulfill testing requirements, provided that test conditions and acceptance criteria are met.

(4)	The Resource Entity shall measure the tested reactive capability on the generator output terminals for non-IRR Generation Resources  The value recorded shall represent the gross MVAr output of the Generation Resource.  Additionally, the net reactive capability shall be measured at the high side of the GSU transformer if metering is available.  This value shall have the Generation Resource’s auxiliary reactive consumption and the GSU losses deducted from the Generation Resource’s gross reactive output.  If metering is not available at the high side, the Resource Entity shall calculate the reactive capability at the high side.  Both high side of the GSU transformer and Generation Resource output terminal values are required and must be submitted through the MIS Certified Area.  Updated CURLs shall be attached to the test results submitted, and shall be clearly defined.  All test data shall be submitted on the form in the NDCRC application.

(5)	The QSE representing a Generation Resource shall be responsible for scheduling reactive verification tests when requested by the Resource Entity in accordance with the conditions outlined above.  If ERCOT does not issue a specific request for a Generation Resource reactive capability verification, the Generation Resource shall complete a reactive verification test at least every five years.

(6)	ERCOT shall have the option to waive the requirement to perform Leading Test 1 for any Generation Resource that seldom runs during such light Load periods.  The granting of such a waiver shall be effective for five years.

(7)

The Resource Entity representing a Generation Resource shall be responsible for the timely and accurate reporting of test results to ERCOT  and to the QSE representing the Generation Resource.  The Resource Entity representing a Generation Resource must properly complete all required data fields in the NDCRC application for a test to be considered valid.

3.5	ERCOT Implementation

(1)	Reactive test results shall be reviewed by ERCOT to determine the accuracy and consistency of the test data provided, and to determine the appropriateness of unit loading and system conditions during the test.  ERCOT shall have the right to order a re-test of the unit, if it determines there are significant discrepancies with the test data.

(2)	Reactive test results shall be reviewed by ERCOT to determine if test results met the acceptance criteria of Section 3.3.2.2, Reactive Testing Requirements.  If the test results fail to meet the acceptance criteria of Section 3.3.2.2, ERCOT shall have the right to either order the Resource Entity to produce a new CURL, or to order a re-test of the unit.

(3)	Reactive test results shall be reviewed by ERCOT against the most recent CURL for the unit.  If unit reactive capability appears to be limited to less than 90% of CURL by unit controls or relays, ERCOT shall contact the Resource Entity and attempt to resolve the limitation.  ERCOT shall have the right to order the Resource Entity to produce a new CURL that reflects current operating limits.

(4)	CURL data validated by test, or any new CURL produced by a Resource Entity in response to new operating limits, shall be implemented by ERCOT in its operational model within four weeks of receipt and resolution of the data.  ERCOT will provide such data to TSPs as Network Models after validation by ERCOT.

(5)	If any test fails to meet the acceptance criteria of 3.3.2.2, then observed operational data may not be used for subsequent testing until actual performance testing has met the acceptance criteria.