| NOGRR Number | 147 | NOGRR Title | Reactive Power Testing Requirements |
| --- | --- | --- | --- |

| Date | August 19, 2015 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Wes Woitt |
| E-mail Address | wesley.woitt@centerpointenergy.com |
| Company | CenterPoint Energy |
| Phone Number | 713-207-2760 |
| Cell Number |  |
| Market Segment | Investor-Owned Utility (IOU) |

Comments

CenterPoint Energy appreciates the opportunity to provide comments on this important topic. The reactive capability provided by Resources is critical for reliable operation of the ERCOT system. In fact, North American Electric Reliability Corporation (NERC) stated in their White Paper on the VAR Standards that “the best and largest source of reactive power or VAR support comes from generators.” As such, the modeled reactive limits for a Resource must reflect the actual capability of the Resource over an extended period of time to ensure that planning and operations studies produce accurate results. In particular, realistic reactive limits are necessary for accurate calculation of expected system behavior in steady-state voltage studies, voltage stability studies, and dynamic studies. Both steady-state voltage studies and voltage stability studies assume that resources are able to supply Reactive Power up to reactive limits for an extended period of time (> 1 hour). Moreover, post-event analyses of major reliability events frequently show that planning models with unrealistic reactive limits contributed to a false sense of security prior to the event. While NERC’s new Reliability Standard MOD-025-2 has introduced additional reactive testing and reporting requirements, CenterPoint Energy is concerned that, on balance, the testing requirements proposed in Nodal Protocol Revision Request (NPRR) 713, Reactive Power Testing Requirements, and Nodal Operating Guide Revision Request (NOGRR) 147 will produce less meaningful results than are achieved through existing testing requirements.

For these reasons, CenterPoint Energy offers comments to NPRR713 and NOGRR147 seeking to ensure that planning and operations models accurately reflect the reactive capability of Resources for the time periods under study. As stated in this revision, the corrected reactive capability curve establishes the Corrected Unit Reactive Limits (CURLs) at the unit terminals that ERCOT planning and operations and Transmission Service Providers (TSPs) will use for their studies. The current reactive capability tests require a minimum of fifteen minutes at the CURL. The proposed testing reduces the duration to one minute at the machine’s CURL.  NERC does call for a one hour lagging test, but that is only at 50% of the CURL. The current 15 minute test is needed to verify that the unit can sustain the reactive capability curve used in modeling reactive capability for extended periods of time. Transmission Planners, ERCOT, and the Resources need to meet to determine the appropriate limits to be included in the Network Operations Model.

Also, CenterPoint Energy reintroduces the language that provides the TSPs the opportunity to review and comment on reactive testing results prior to introducing the changes into the Network Operations Model via Resource Asset Registration Form (RARF).

CenterPoint Energy suggests that the Net Dependable Capability and Reactive Capability (NDCRC) application form be updated to clarify certain requirements, specifically the requirements to provide net injection and power factor data with respect to the Point of Interconnection (POI) with the TSPs and not the generation high side terminals. Additionally, the NDCRC needs to be modified to accept the results of all six tests. ERCOT and the Transmission Planners need to determine which test results are ultimately incorporated into the Network Operations Model. Furthermore, the Planning Guides must be updated accordingly.

Finally, to the extent broad agreement about these issues cannot be reached, CenterPoint Energy recommends further discussion at a joint workshop that includes both planning and operational personnel so that the full impacts of these proposed changes can be identified and understood.

Revised Proposed Guide Language

- 3.3.2.1	Corrected Unit Reactive Limits (CURL)

A reactive capability curve and associated data for each unit on the ERCOT System shall be submitted to ERCOT through the Market Information System (MIS) Certified Area and must contain the most limiting elements for the leading and lagging reactive output.  The limiting factors such as under-excitation limiters, over-excitation limiters, ambient temperature limitations across the MW range of the unit at the unit terminals or any other factor that limits the reactive output of the unit and is verifiable through engineering calculations or testing shall be updated and provided on the corrected reactive capability curve.  The corrected reactive capability curve establishes the Corrected Unit Reactive Limits (CURL) at the unit terminals that ERCOT Planning and ERCOT Operations, and TSPs will use for their studies. For IRR’s the CURL data shall be reported at the low side of the generator step up transformer to the Point of Interconnection (POI).  Resources will provide these updated curves and associated data to ERCOT by submitting test information to the Net Dependable Capability and Reactive Capability (NDCRC) application located on the Market Information System (MIS) Secure Area.  Once approved by ERCOT per Section 3.5, ERCOT Implementation, Resources will provide the updated data by submitting changes to the appropriate ERCOT Resource Asset Registration Forms (RARF) in accordance with paragraph (9) of Planning Guide Section 6.8.2, Resource Registration Process. Prior to including the submitted data into the Network Operations Model, ERCOT will notify the TSP to which the Resource Entity is interconnected that the test data is posted on the MIS Secure Area.  ERCOT and TSPs will review the data and provide any comments within ten Business Days.  ERCOT  will include these changes in the future Network Operations Model and forward the changes to the TSPs and the Steady State Working Group (SSWG) for use in their studies. The CURL should be available in the Resource Entities control room where the tests are conducted and at the QSEs Real Time generation dispatch desk.  During any test, the Generation Resource must maintain its generator cooling system at normal operating conditions.

- 3.3.2.2	Reactive Testing Requirements

(1)	Reactive testing may be performed as either “Coordinated”, or “Non-Coordinated”, the difference being the amount of notification provided to ERCOT and the TO, and level of their involvement in testing.

(a)	Coordinated Testing

(i)	Coordinated testing is the preferred method for new or larger-capacity units, as it provides a greater amount of coordination with ERCOT and the TO, allowing testing impacts and any potential adjustments to local voltage levels to be studied in advance.

(ii)	The Resource Entity requesting a Coordinated test must submit a test request to ERCOT and the TO via their QSE, by no later than 15:00, one day prior to the proposed test date.  ERCOT and the TO then have until 17:00 of the day prior to the proposed test date, to either approve or disapprove the test request.

(iii)	Both ERCOT and the TO have the right to deny or cancel a test at any time, if they feel that system reliability may be adversely impacted by the test.

(iv)	The test requests should contain the proposed time and date of the test, type of test (leading or lagging), expected unit MW and MVAR output range during the test, and a copy of the reactive capability curve.

(b)	Non-Coordinated Testing

(i)	The Resource Entity representing the resource requesting a Non-Coordinated test must inform ERCOT and the TO via their QSE at least two hours prior to the proposed start of the test.

(ii)	Both ERCOT and the TO have the right to deny or cancel a test at any time, if they feel that system reliability may be adversely impacted by the test.

(2)	Lagging Reactive Testing

(a)	It is recommended, but not required, that lagging reactive tests be performed when system voltage is at the lower end of the normal range, such as during high load periods.

(b)	Laggings tests should meet the following performance criteria:

(i)	Lagging Test 1:  Test at or above 95% of the unit’s seasonal High Sustained Limit (HSL) for at least 15 minutes.  Intermittent Renewable Resources (IRRs) should test at or above 60% of their seasonal HSL.  Testing acceptance criteria is met if the unit achieved  no less than 90% of the unit’s original manufacturer reactive curve or most recent CURL.

(ii)	Lagging Test 2:  Test at the unit’s seasonal HSL for at least 1 hour. IRRs should test with at least 90% of inverters on-line. Testing acceptance criteria is met if the unit achieved at least 50% of the units CURL for one hour.

(iii)	Lagging Test 3:  Test at the unit’s normally expected minimum real power output during system light load conditions for at least 1 minute.  IRR and Nuclear units are exempt from this test. Testing acceptance criteria is met if the unit achieved  at least 50% of the unit’s CURL.

(iv)	Following one successful performance of each of  Tests 1, 2 and 3, observed operational data within 2 years of the verification date may be used to fulfill testing requirements, provided that operational data demonstrates 90% of the tests’ thermal capability and test conditions and acceptance criteria are met.

(3)	Leading Reactive Testing

(a)	It is recommended, but not required, that leading reactive tests be performed when system voltage is at the higher end of the normal range, such as during low load periods.

(b)	Leading tests should meet the following performance criteria:

(i)	Leading Test 1:  Test at the unit’s normally expected maximum real power output during system light load conditions for at least 15 minutes.  IRRs should test at or below 60% of their seasonal HSL. Testing acceptance criteria is met if the unit achieved  no less than 90% of the units original manufacturer reactive curve or most recent CURL.

(ii)	Leading Test 2:  Test at the unit’s seasonal HSL for at least 1 minute.  IRR units are exempt from this test.  Testing acceptance criteria is met if the unit achieved  at least 50% of the units CURL.

(ii)	Leading Test 3:  Test at the unit’s normally expected minimum real power output during system light load conditions for at least 1 minute.  IRR and Nuclear units are exempt from this test. Testing acceptance criteria is met if the unit achieved  at least 50% of the units CURL.

(iii)	Following one successful performance of each of Tests 1, 2 and 3, observed operational data within 2 years of the verification date may be used to fulfill testing requirements, provided that operational data demonstrates 90% of the tests’ thermal capability and test conditions and acceptance criteria are met.

(4)	The Resource Entity shall measure the tested reactive capability on the generator output terminals for non-IRR Generation Resources  The value recorded shall represent the gross MVAr output of the Generation Resource.  Additionally, the net reactive capability shall be measured at the high side of the GSU transformer and at the POI, if metering is available.  The high side values shall have the Generation Resource’s auxiliary reactive consumption and the GSU losses deducted from the Generation Resource’s gross reactive output.  The POI values shall have the plant’s auxiliary load and any additional load deducted from the Generation Resource’s gross reactive output. If metering is not available at the high side, the Resource Entity shall calculate the reactive capability at the high side and at the POI.  These values are required and must be submitted through the MIS Certified Area.  CURLs shall be attached to the test results submitted, and shall be clearly defined.  All test data shall be submitted on the form in the NDCRC application.

(5)	The QSE representing a Generation Resource shall be responsible for scheduling reactive verification tests when requested by the Resource Entity in accordance with the conditions outlined above.  If ERCOT does not issue a specific request for a Generation Resource reactive capability verification, the Generation Resource shall complete a reactive verification test at least every five years.

(6)	ERCOT shall have the option to waive the requirement to perform Leading Test 1 for any Generation Resource that seldom runs during such light Load periods.  The granting of such a waiver shall be effective for five years.

(7)

The Resource Entity representing a Generation Resource shall be responsible for the timely and accurate reporting of test results to ERCOT  and to the QSE representing the Generation Resource.  The Resource Entity representing a Generation Resource must properly complete all required data fields in the NDCRC application for a test to be considered valid.

3.5	ERCOT Implementation

(1)	Reactive test results shall be reviewed by ERCOT to validate the accuracy and consistency of the test data provided, and to determine the appropriateness of unit loading and system conditions during the test.  ERCOT shall have the right to order a re-test of the unit, if it determines there are significant discrepancies with the test data.

(2)	Reactive test results shall be reviewed by ERCOT to determine if test results met the acceptance criteria of Section 3.3.2.2, Reactive Testing Requirements.  If the test results fail to meet the acceptance criteria of Section 3.3.2.2, ERCOT shall have the right to either order the Resource Entity to produce a new CURL, or to order a re-test of the unit.

(3)	Reactive test results shall be reviewed by ERCOT against the most recent CURL for the unit.  If unit reactive capability appears to fail the acceptance criteria of Section 3.3.2.2  by unit controls or relays, ERCOT shall contact the Resource Entity and attempt to resolve the limitation.  ERCOT shall have the right to order the Resource Entity to produce a new CURL that reflects current operating limits.  However, a new CURL will not be required if testing limitations are due to temporary system conditions at the time of the test.

(4)	CURL data validated by test, or any new CURL produced by a Resource Entity in response to new operating limits, shall be submitted by the Resource via the Resource Asset Registration Form (RARF)  within four weeks of ERCOT’s approval of the test. ERCOT will notify TSPs after RARF submittal as described in Section 3.3.2.1, Corrected Unit Reactive Limits (CURL).

(5)	If any test fails to meet the acceptance criteria of 3.3.2.2, then observed operational data may not be used for subsequent testing until actual performance testing has met the acceptance criteria.